## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
18 & 19-Sep-2024
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | Challenge Apparels Ltd., 34 Km. Multan Road, Shamkey Bhattian, Lahore, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 18 & 19 -Sep-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | 3 months | We will develop detailed substation room layout drawings in accordance with BS 7671:2018 + A2:2022 (Sections 132.12 and 132.13). Training will also be provided to maintenance staff and emergency responders to ensure proper understanding and use of the drawings. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | During the inspection It was found that the electrical single line diagrams (SLDs) for the factory were available but missing necessary details. | Upgrade comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | 6 months | We will upgrade the facility’s electrical single line diagrams in compliance with Section 514.9.1 of BS 7671:2018 + A2:2022. Training will also be provided to maintenance staff and emergency responders on how to interpret and use the updated diagrams effectively. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory has available electrical layout drawings - including small power layouts, lighting layouts, and containment layouts but the all-layout drawings were missing necessary details. | Upgrade comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | 8 months | The existing electrical layout drawings will be upgraded to meet the requirements of Sections 132.12 and 132.13 of BS 7671:2018 + A2:2022. Training will be provided to maintenance staff and emergency responders on interpreting and using the updated layouts. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | During the survey It was observed that a Single Pole circuit breakers (CB) was mounted inappropriately in kitchen area behind dryer and a circuit breakers are mounted loosely below cutting table in production hall. | Cover all circuit breakers that are openly installed throughout the facility with concealed metallic boxes to ensure safety and compliance with standards. | 3 months | All openly installed circuit breakers throughout the facility will be covered with concealed metallic boxes to improve safety and ensure compliance with relevant standards. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E5 | DBs & Elec Protection Systems | Circuit breakers | During the survey It was observed that there was No phase separator found in production area distribution boards. | Install phase separator on circuit breaker and bus bars within the panel. | 3 months | Phase separators will be installed on the circuit breakers and bus bars within the panels to improve safety. This will ensure compliance with electrical standards and prevent accidental contact. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | During the survey It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes such as: - 10 sq. mm cable found terminated on 100A CB in LT Room | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable ampacity after applying derating factors. | 3 months | We will evaluate and adjust the breaker ratings and cable sizes for all circuits in the facility to ensure compliance with Section 433.1.1 and Appendix 4 of BS 7671:2018 + A2:2022. Breaker ratings will not exceed the cable current-carrying capacity, and adjustable breakers will be set according to the cable ampacity after applying derating factors. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E7 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards at different locations such as capacitor termination at main LT room, IT box located near dispensary and ATM room, warehouse panel at blue phase and embroidery distribution panel on three pole circuit breakers. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. Moreover, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. | 2 weeks | Circuits exceeding 40°C above ambient temperature, operating above 90°C, or showing signs of burning will be immediately isolated and taken out of service. The circuits with temperatures exceeding 20°C above ambient been identified and will be addressed to mitigate risks and ensure safety. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | During the inspection It was also found that the Thermographic report was not available at the site | A thermographic Testing report shall be prepared for every 6 months. | 6 months | We will conduct thermographic test report as required for every 6 months and should be provided promptly to ensure compliance. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E9 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility it was observed that the earth pits were inaccessible and unsuitably located in LT Room near adidas building | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 3 months | The earth pits will be relocated and redesigned to ensure easy access for maintenance and inspection. This will be done in compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility the earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections such as in production area. The earthing cables were not appropriately sized according to the relevant earthing standards in LT room. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. Replace all earthing cables with appropriately sized cables as per the requirements of BS 7671 18th Edition + A2 (2022) Appendix 4, Section 5. Verify that all earthing conductors meet the minimum cross-sectional area specified. | 6 months | We will Install earthing systems where absent and ensure all electrical boards are fitted with the required earthing cables, complying with the required standard. And will also replace all earthing cables with appropriately sized cables as per Appendix 4, Section 5, and verify compliance with the minimum cross-sectional area requirements. |  |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility equipotential bonding for the cable trays, machines body and metallic panel covers was missing in chiller outers near canteen area. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 6 months | We will Implement equipotential bonding for all cable trays to comply with Regulation, and ensure all exposed conductive parts will be bonded to the main earthing terminal. |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility there was no any earth distribution layout drawing and standardize earth testing record present in the facility. | Develop the earth distribution layout drawing, earth testing record and submit them to the Pakistan Accord. | 6 months | We will Develop the earth distribution layout drawing and earth testing record, ensuring compliance with applicable standards. Submit both documents to the Pakistan Accord for approval. |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was observed that a number of external areas, it was observed that electrical components were not suitable for the environmental conditions in which they were installed workshop and boiler distribution panel | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | We will Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed, in accordance with required section. |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was observed that several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements such as IT boxes placed In Front of LT room and near ATM room. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 3 months | We will Replace or refurbish corroded electrical panels to prevent further degradation and safety hazards and Implement protective measures as suggested. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was found that there was improper bus-bar arrangement inside the distribution boards such as in metal free zone in production area | Inspect and repair or replace all damaged panels, cables, and busbars to ensure the integrity of the electrical system in accordance with Section 522 of BS7671 18th Edition + A2 (2022). Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. | 3 months | We will Inspect and repair or replace all damaged panels, cables, and busbars to ensure electrical system integrity, in compliance with Section required. And will Implement a regular maintenance and inspection schedule for panels, cabling, and busbars. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multi-looping was observed in a number of electrical panels across the facility such as in CCTV room, LT room, embroidery panel and cutting machine main panel in production building. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022) | 3 months | We will Modify the electrical installation to ensure that each circuit is protected by a dedicated circuit breaker of the appropriate type and rating for each individual circuit, as required. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E17 | DBs & Elec Protection Systems | Openings | During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements. | Corrective actions are required to seal all openings and replace missing panels covers to restore the integrity and safety of the electrical systems. . | 3 months | Corrective actions have been taken to seal all openings and replaced missing panel covers to restore the integrity and safety of the electrical systems. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E17 | DBs & Elec Protection Systems | Openings | During the visual inspection, unsealed openings were discovered in the panels and distribution boards such as LT room, generator room, production building, and embroidery area. | The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). Install cable glands or bushings to provide strain relief and protect cables at entry points in distribution boards. | 4 months | We will ensure the electrical system complies with the required standard. We will also Install cable glands or bushings at entry points in distribution boards to provide strain relief and protect cables from damage. |  |  |  | In Progress
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Adequate accessibility | During the inspection at numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components such as compressor room, printing room, embroidery, and executive building IT room. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022) | 1 month | We will ensure electrical equipment is arranged in a way to provide sufficient space for both initial installation and later replacement of individual items. |  |  |  | In Progress
[20 empty] | E19 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, embroidery panels, workshop areas, and trunking systems in the stitching section, as well as in the main HT trunk along the side wall of the HT Room. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 1 month | All electrical panels and trunking have been inspected and cleaned from dust or lint. A regular maintenance procedure have been established to ensure routine cleaning, preventing the buildup of debris and ensuring the safety and efficiency of the electrical systems. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection it was noticed that the fire alarm system was non-listed, non-addressable, having inadequate detection coverage issues, non-fire rated cable, faulty sounders, MCP and detectors The following observations were identified with the FADS: - Admin and Adidas Building: The FAP system was conventional, non-listed, lacking with various type of listed detectors in kitchen and office area. | This related to Admin and Adidas Building: (1) Submit design documentation for new replacement FADS system in all buildings to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | We will submit the design documentation for the new FADS system in all buildings to the Pakistan Accord for review, including drawings, technical data sheets, and product certifications. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E20 + 1 month | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E21 + 4 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E22 + 5 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E23 + 3 months | We will submit the required completion documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E24 + 3 months | We will submit the required completion documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection it was noticed that the fire alarm system was non-listed, non-addressable, having inadequate detection coverage issues, non-fire rated cable, faulty sounders, MCP and detectors The following observations were identified with the FADS: - Main Production Building: The Fire alarm panel is conventional and non-listed as delay in detection is noted on the Fire Alarm Panel (FAP) at the time of testing. | This related to Main Production Building: (1) Submit design documentation for new replacement FADS system in all buildings to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | We will Submit the design documentation for the new FADS system to the Pakistan Accord for review before purchasing any equipment. Include drawings, technical data sheets, and product certifications to ensure compliance with NFPA 72 |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E26 + 1 month | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E27 + 4 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E28 + 5 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E29 + 3 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E30 + 3 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection it was noticed that the fire alarm system was non-listed, non-addressable, having inadequate detection coverage issues, non-fire rated cable, faulty sounders, MCP and detectors The following observations were identified with the FADS: - Canteen and Printing Hall Building: The Fire alarm panels is conventional and non-listed, non-compliant in both canteen and printing hall. Also, the type of detector is not relevant to the operations in kitchen area. | This related to Canteen and Printing Hall Building: (1) Submit design documentation for new replacement FADS system in all buildings to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | We will submit the design documentation for the new FADS system in the Canteen and Printing Hall Building to the Pakistan Accord before purchasing equipment. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E32 + 1 month | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E33 + 4 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E34 + 5 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E35 + 3 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS system was installed throughout the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E36 + 3 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Fire Alarm & Detection System (FADS) | Maintenance records | - Routine testing of the Fire Alarm and Detection System (FADS) has not been performed consistently. - The testing and maintenance of the Fire Alarm and Detection System (FADS) have not been conducted in accordance with the requirements specified in Chapter 14 of NFPA 72. | Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | 3 months | We will submit the required documents once finalized. |  |  |  | In Progress
No | 3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Emergency Lighting | No emergency lighting | During the inspection, it was discovered that several areas had no emergency lighting such as: - Production Building: Sample room and production walkways. - Canteen Building: Near kitchen and mess area. | To address the lack of emergency lighting in the facility, listed emergency lighting systems should be designed and installed in accordance with the Building Code of Pakistan Fire Safety Provisions 2016. Maintain comprehensive records of all installations, tests, and maintenance activities. | 3 months | We will address the lack of emergency lighting, listed emergency lighting systems will be designed and installed according to the Building Code of Pakistan Fire Safety Provisions 2016. We will maintain comprehensive records of all installations, tests, and maintenance activities. |  |  |  | In Progress
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Emergency Lighting | Provided but non-functional | During the inspection, the emergency lighting arrangement throughout the facility was assessed. The following observations were made: - Several areas lack sufficient emergency lighting coverage in production and canteen area. - External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations in production walkways. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional listed emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s) | 3 months | We will conduct a comprehensive survey to identify areas with inadequate emergency lighting, and install listed emergency luminaires as per the Building Code of Pakistan Fire Safety Provisions 2016. Ensure external emergency lighting is also installed to facilitate safe evacuation to a secure location outside during hours of darkness. |  |  |  | In Progress
No | 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Emergency Lighting | Provided but non-functional | During the inspection, the emergency lighting arrangement throughout the facility was assessed. The following observations were made: - Multiple emergency luminaires indicate the need for maintenance such as in kitchen, executive building 1st floor and LT room. - In some areas installed emergency lights are too dim to provide adequate illumination such as in printing area. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies. | 3 months | We will maintain all emergency luminaires by cleaning, replacing bulbs, and verifying electrical connections. Replace dim lights with compliant, high-intensity luminaires to ensure safe evacuation per the Building Code of Pakistan Fire Safety Provisions 2016. |  |  |  | In Progress
No | 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Generator, Transformer & Sub-Station Room | Working clearance | During the survey, it was noted that various locations exhibited inadequate work clearance within facility such as - clearance around the HT panel, embroidery and sample room which could hinder maintenance and pose safety risks. | Reorganize the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. | 6 months | We will reorganize the equipment layout to ensure proper clearance, remove obstructions, and implement clear floor markings and signage. Conduct regular audits and train personnel to maintain clearances, and consider adjustable equipment for flexibility. |  |  |  | In Progress
No | 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Generator, Transformer & Sub-Station Room | Battery | During inspection, it was observed that the batteries of generator had some fluid spills as we had seen fluid spread off the batteries. Furthermore, the battery placement for generator was inadequate and their terminal are bare. This is not safe and have a risk of electrocution as well as causing fire if exposed to combustible materials such as at hydrant room, ATM, LT Room and plotter room. | Hazardous substance placed inside the ATM, Plotter room and hydrant room need to be placed in their designated area. Bare terminals of battery need to be covered. Battery placement and cabling will be adjusted to comply with BS-7671 and NFPA standards, alongside performing a thorough periodic maintenance of the generator. | 2 months | We will remove hazardous substances from the ATM, Plotter room, and hydrant room and relocated to their designated areas. Bare battery terminals will be covered, and battery placement and cabling should be adjusted to comply with BS-7671 and NFPA standards, with regular maintenance of the generator. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E44 | Cabling & Wiring | Cables support and protection | During the inspection proper supports were not provided for cables; they were laid directly on the ground. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. - Near admin building aside of officer mess. - Executive building 1st floor. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). | 3 months | We will secure cables with appropriate supports and insulate exposed connections to prevent damage and hazards, as per Regulations required. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E45 | Cabling & Wiring | Cables support and protection | During the inspection numerous cable and wires bunching were identified powering IT boxes In Front of LT room and near dispensary, which can generate sparks and potentially cause a fire. It is essential to avoid cable bunching. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | 3 months | We will Implement a cable management system with regular inspections to ensure cables are properly supported and insulated as advised. |  |  |  | In Progress
No | 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E46 | Cabling & Wiring | Splicing of cables | During the inspection cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. - Embroidery main circuit breaker and distribution MCPs - LT Room distribution circuit breakers. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections | 4 months | We will install cable lugs on all improperly terminated cables to secure connections and prevent issues, in line with required Regulations and implement an SOP for future terminations, along with regular training and audits to ensure compliance. |  |  |  | In Progress
No | 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E47 | Cabling & Wiring | Splicing of cables | During the inspection PVC tape joints were found in several locations - including within distribution boards - where cables terminations were either damaged or burnt. - Kitchen distribution panel in canteen area - Maintenance workshop behind canteen area - Near RO plant office in production building | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | 4 months | We will replace all PVC tape joints with proper terminal blocks or connectors and damaged cables with new wiring, and implement a policy against using PVC tape for jointing and conduct regular inspections, maintenance, and training on proper techniques. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E48 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards in kitchen, stitching and boiler room, deviations from standard cable colour coding practices were identified. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. | 2 months | We will conduct a detailed audit of all distribution boards to identify and correct deviations from standard cable colour coding. Re-label or re-insulate cables with the appropriate colour codes as per BS 7671 standards. |  |  |  | In Progress
No | 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E49 | Cabling & Wiring | Fixtures | During the inspection at many locations loose power receptacles were found. This poses a significant risk of equipment damage or electrical incidents due to the instability of the receptacles in location such as: - Maintenance Workshop behind canteen building - Washing area at side walkways of main production building | Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed. | 3 months | We will implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they are safely and correctly installed. |  |  |  | In Progress
No | 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E50 | Cabling & Wiring | Fixtures | During the inspection it was found that the power receptacles were placed at a very low height having no weather protection as per standard and being operated especially at main gate and printing 1st floor. | Disconnect the power receptacles and relocate their position to an appropriate height and location as per standard. | 3 months | We will disconnect the power receptacles and relocate them to an appropriate height and location, ensuring compliance with safety standards and providing adequate weather protection. |  |  |  | In Progress
No | 3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
18 & 19-Sep-2024
Corrective Action Plan Fire
[8 empty] | Factory Name & Address | [12 empty] | Challenge Apparels Ltd., 34 Km. Multan Road, Shamkey Bhattian, Lahore, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 18 & 19-Sep-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Protection of stairs | Unprotected openings into stairs S 1 & S 2 in Printing Building, S 3 in main production building. Fire load under stair S 2 in Printing Building. Fire load under stair S 3 in Main Production Building. Door self-closer is missing in boiler room (Ground floor). | Remove fire load and any obstructions due to stored items from stairs. | 2 weeks | We have removed all flammable items immediately. We are Maintaining and will completely protect the required S1, S2 & S3 stairs . We will also install self-door closer in boiler room. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Protection of stairs | Unprotected openings into stairs S 1 & S 2 in Printing Building, S 3 in main production building. Fire load under stair S 2 in Printing Building. Fire load under stair S 3 in Main Production Building. Door self-closer is missing in boiler room (Ground floor). | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect the stairs. Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | We have removed all flammable items immediately. We are currently working on drawings and will complete the required fire-rated separating construction and submit the necessary drawings within 2 months. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Protection of stairs | Unprotected openings into stairs S 1 & S 2 in Printing Building, S 3 in main production building. Fire load under stair S 2 in Printing Building. Fire load under stair S 3 in Main Production Building. Door self-closer is missing in boiler room (Ground floor). | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90 minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: All doors into stairs should be fire resisting doors with self-closing mechanisms. Penetrations through doors are not permitted. Doors into stairs should be kept closed (but not locked) at all times. | F3+ 4 months | We will complete the required fire-separating construction for the emergency escape stairs and ensure compliance with all relevant Standard within six months. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits in Main Production Building (Fabric Store & metal free zone) at Ground floor. Alternate travel distance exceeds the permit limit in warehouse area Main Production Building (78m). | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | We will review the travel distances from all areas and propose necessary alternative escape routes or additional exits. The detailed plan will be submitted to Pakistan Accord for approval. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits in Main Production Building (Fabric Store & metal free zone) at Ground floor. Alternate travel distance exceeds the permit limit in warehouse area Main Production Building (78m). | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F4+4 months | We have not received any plan previously reviewed by Pakistan Accord however, We will review the travel distances from all areas and propose necessary alternative escape routes or additional exits. The detailed plan will be submitted to Pakistan Accord for approval. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Number of exits | Single exit from sleeping area Admin Building (1st floor). | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Building Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | Currently, this hall is no longer being used for such purposes as well. We have clear the building and not in use for any purpose. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F7 | Means of Escape | Number of exits | Single exit from sleeping area Admin Building (1st floor). | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Building Standard. | F6+ 4 months | Currently, this hall is no longer being used for such purposes as well. We have clear the building and not in use for any purpose. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F8 | Means of Escape | Escape doors | Escape door is lockable in warehouse Main Production Building (Ground Floor). Escape door is lockable in cutting area Main Production Building (Ground Floor). Escape door is lockable in Chinese mess hall Admin Building (Ground floor). | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | We have removed the lockable devices from doors in the warehouse, cutting area, and Chinese mess which are using for escape. We will ensure everything remains compliant and functional within the next six months. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Escape doors | Escape door is lockable in warehouse Main Production Building (Ground Floor). Escape door is lockable in cutting area Main Production Building (Ground Floor). Escape door is lockable in Chinese mess hall Admin Building (Ground floor). | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Pakistan Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | We will ensure everything remains compliant and functional within the next six months as advised by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Escape doors | Escape door is lockable in warehouse Main Production Building (Ground Floor). Escape door is lockable in cutting area Main Production Building (Ground Floor). Escape door is lockable in Chinese mess hall Admin Building (Ground floor). | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F9+ 3 months | We have removed the lockable devices from escape doors in the warehouse, cutting area, and Chinese mess. We will monitor and ensure everything remains compliant. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Obstructions on escape route in Mian Main Production Building office area (Ground floor). Unprotected stair S3 discharges inside the building at a distance from building exit in Main Production Building. Unprotected stair S1 & S2 discharges inside the Printing Building. Exit doors block the egress path on opening in Main Production Building (Ground floor). Temporary obstructions on escape route at fabric store Main Production Building (Ground floor). | Remove obstructions on escape routes and keep them clear for escape. | 2 weeks | We will remove any obstructions on the escape routes and ensure they remain clear at all times to facilitate safe and smooth evacuation. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit access | Obstructions on escape route in Mian Main Production Building office area (Ground floor). Unprotected stair S3 discharges inside the building at a distance from building exit in Main Production Building. Unprotected stair S1 & S2 discharges inside the Printing Building. Exit doors block the egress path on opening in Main Production Building (Ground floor). Temporary obstructions on escape route at fabric store Main Production Building (Ground floor). | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect stair discharge corridors Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | We will remove any obstructions on the escape routes and ensure they remain clear at all times to facilitate safe and smooth evacuation. We will work on preparation of drawings showing the opposed fire separation construction. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit access | Obstructions on escape route in Mian Main Production Building office area (Ground floor). Unprotected stair S3 discharges inside the building at a distance from building exit in Main Production Building. Unprotected stair S1 & S2 discharges inside the Printing Building. Exit doors block the egress path on opening in Main Production Building (Ground floor). Temporary obstructions on escape route at fabric store Main Production Building (Ground floor). | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. | F12+ 4 months | We will ensure stair discharge routes and corridors are properly fire-separated and as per the revised proposal and Pakistan Accord Building Standard. All doors will meet the specified requirements. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Exit discharge routes in west side of the Main Production Building is not fire separated from Boiler room & compressor room. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect stair discharge routes Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes | 4 months | We will work on this issue and prepare the required drawings. These will be submitted to Accord for review and approval within Three months. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit discharge | Exit discharge routes in west side of the Main Production Building is not fire separated from Boiler room & compressor room. | Ensure external exit discharge routes are adequately fire separated from the rest of the building. | F14 + 4 months | We will work on this issue and prepare the required drawings. These will be submitted to Accord for review and approval within Three months. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit signage | Missing exit signs in production area Main Production Building. Electrically powered exit signs are not a tested and listed system in whole factory. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | We will work on this issue and ensure that the exit signage is rectified and properly installed in compliance with the Pakistan Accord Building Standard within six months. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit signage | Missing exit signs in production area Main Production Building. Electrically powered exit signs are not a tested and listed system in whole factory. | Ensure that all exit signage is checked periodically and in good working condition. | F16+ 3 months | We will ensure that all exit signage is checked periodically and maintained in good working condition to ensure compliance with safety standards. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Separation of high risk areas | Boiler room is not fire separated from exit discharge route on west side of Main Production Building. Compressor room is not fire separated from exit discharge route on west side of Main Production Building. Boiler room is not separated from exit discharge route on North side of Canteen Building. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | We will prepare and submit the required drawings showing the fire separation details for increased fire hazard areas, including locations of fire-rated walls and doors. These will be submitted to Accord for review and approval before work started. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Separation of high risk areas | Boiler room is not fire separated from exit discharge route on west side of Main Production Building. Compressor room is not fire separated from exit discharge route on west side of Main Production Building. Boiler room is not separated from exit discharge route on North side of Canteen Building. | Provide 2 hour fire rated construction including 90 minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F18+ 4 months | We will prepare and submit the required drawings showing the fire separation details for high risk fire hazard areas, including locations of fire-rated walls and doors. These will be submitted to Accord for review and approval before work started. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Separation of occupancies | Large office area is not fire separated from cutting ground floor Main Production Building. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building Proposed fire separation details (including fire rating of walls and doors) | 4 months | We will prepare and submit the required drawings showing the fire separation details for high risk fire hazard areas, including locations of fire-rated walls and doors. These will be submitted to Accord for review and approval before work started. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Separation of occupancies | Large office area is not fire separated from cutting ground floor Main Production Building. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F20+ 4 months | We will prepare and submit the required drawings showing the fire separation details for office area. These will be submitted to Accord for review and approval before work started. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Storage | Storage areas (Accessories store & Fabric Store) are not fire separated from cutting Main Production Building. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | We will identify the storage areas, assess fire separation needs, and submit detailed drawings for fire-separating construction to Pakistan Accord for review before rectification works. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Storage | Storage areas (Accessories store & Fabric Store) are not fire separated from cutting Main Production Building. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F22+ 4 months | We will identify the storage areas, assess fire separation needs, and submit detailed drawings for fire-separating construction to Pakistan Accord for review before rectification works. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Separation of occupancies | Locking devices on doors do not allow free exit from the inside under all circumstances No adequate automatic fire detection and alarm system | The dormitory is not to be used until minimum requirements for sleeping occupancies have been provided. Alternative arrangements must be sought immediately for the dormitory as continuing the use of the building for this purpose is not appropriate. Dormitory not to be re occupied until the minimum requirements have been implemented | 2 weeks | We have no any dormitory. The area is clear not in use. |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Separation of occupancies | Locking devices on doors do not allow free exit from the inside under all circumstances No adequate automatic fire detection and alarm system | Document proposals for design of remedial measures to ensure compliance with all fire safety requirements for sleeping occupancies to comply with Pakistan Accord Building Standard. Submit proposals to Pakistan Accord for review. | 4 months | We have no any dormitory. The area is clear not in use. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Rated Construction | Separation of occupancies | Locking devices on doors do not allow free exit from the inside under all circumstances No adequate automatic fire detection and alarm system | Implement remediation measures to ensure full compliance with dormitory requirements of Pakistan Accord Building Standard and Pakistan Building Code in accordance with previously reviewed design. | F25+ 4 months | We have no any dormitory. The area is clear not in use. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Safety Management | Fire drills | No regular fire drills. No evidence of fire drills | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | We have already conducted fire drill trainings as per the standard and compliance requirements. We have all evidence and documents of fire drill. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Safety Management | Fire drills | No regular fire drills. | Ensure fire drills are performed a minimum 2 times per year. | F27+ 2 months | We have already conducted fire drill trainings as per the standard and compliance requirements twice In a year. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Safety Management | Records of systems maintenance | No evidence of fire drills | Prepare maintenance schedule for all life safety systems. | 3 months | We have already maintained records for the fire extinguishers and fire doors as required. We have already developed a maintenance schedule as well. |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Safety Management | Records of systems maintenance | No records of maintenance of Fire extinguishers. No records of maintenance of Fire Doors. | Prepare a schedule of proposed system maintenance. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | We have already maintained records for the fire extinguishers and fire doors as required. We have already developed a maintenance schedule as well. |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Safety Management | Records of systems maintenance | No records of maintenance of Fire extinguishers. No records of maintenance of Fire Doors. | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep maintenance records. | F30+ 3 months | We have already maintained records for the fire extinguishers and fire doors as required. And these maintenance records are available for review. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Safety Management | Records of system testing | No records of testing of Fire extinguishers. No records of testing of Fire Doors. | Prepare testing schedule for all life safety systems. | 3 months | We have already inspection of fire extinguishers and fire doors on the basis of monthly. |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Safety Management | Records of system testing | No records of testing of Fire extinguishers. No records of testing of Fire Doors. | Prepare a schedule of proposed system testing. Identify how systems will be tested and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | We have already inspection of fire extinguishers and fire doors on monthly basis and have a supervisor who is responsible. |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Safety Management | Records of system testing | No records of testing of Fire extinguishers. No records of testing of Fire Doors. | Ensure all systems are being tested as per the schedule agreed with Accord. Keep testing records. | F33+ 3 months | We have already inspection of fire extinguishers and fire doors on monthly basis and have a supervisor who is responsible. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Safety Management | Emergency Action Plan | EAP document didn’t contain details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | We have already emergency evacuation plan and updating as per the Accord standard. |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Safety Management | Emergency Action Plan | EAP document didn’t contain details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F35+ 2 months | We have already emergency evacuation plan and updating as per the Accord standard. |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
18 & 19-Sep-2024
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [12 empty] | Challenge Apparels Ltd., 34 Km. Multan Road, Shamkey Bhattian, Lahore, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 18 & 19-Sep-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Structural Documentation | Differs from as-built structure | This refers to the main production building where there is one extra bay is drawn on the approved layout. There is one lesser bay in actual. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | Structural engineer will inspect the main production building and the available drawings to prepare accurate as per approved layout. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Structural Documentation | Documentation unavailable | The following drawings are not available and needs to be prepared. • As built structural drawings of main production, adidas, admin and canteen building | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | We already have all drawings so that a Structural engineer will inspect all mentioned area and collect all information and produce accurate and complete as-built documentation. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in the factory. | Building structural engineer to produce loading plans for all floors within the factory considering floor capacity and column capacity. Loading to be actively managed by factory management. | 6 months | Structural engineer to prepare floor-wise load plans considering structural capacity. Factory management to ensure active monitoring and control of floor loading. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S4 | Other Damage/Defects | Corrosion of reinforcement | The water is actively leaking from the pipes of the coolers, the active leakage of water has corroded the reinforcing bars of the column on the outside of the main production building. The seepage has also damaged the masonry wall from inside as well as from the outside. | Building Engineer to inspect the area and stop the source of water leakage. | 1 month | The engineer will inspect and identify the source of water leakage. Currently we are covering the leakage area with an additional tray to contain the water. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Other Damage/Defects | Corrosion of reinforcement | The water is actively leaking from the pipes of the coolers, the active leakage of water has corroded the reinforcing bars of the column on the outside of the main production building. The seepage has also damaged the masonry wall from inside as well as from the outside. | Inspect damage to the Column and propose repairs to structure and Submit report capturing above to Pakistan Accord for approval | 3 months | The Engineer will inspect the leakage area and damage to the Column and propose repairs to structure and will be share the report to Pakistan Accord for approval. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Corrosion of reinforcement | The water is actively leaking from the pipes of the coolers, the active leakage of water has corroded the reinforcing bars of the column on the outside of the main production building. The seepage has also damaged the masonry wall from inside as well as from the outside. | Implement the Remediation | S5 + 3 months | We will implement the remediation as advise and approved by Accord. |  |  |  | In Progress
[20 empty] | S7 | Other Damage/Defects | Corrosion of reinforcement | The water is actively leaking from the pipes of the coolers, the active leakage of water has corroded the reinforcing bars of the column on the outside of the main production building. The seepage has also damaged the masonry wall from inside as well as from the outside. | Continue to monitor for future signs of water ingress/damage | S6 + 3 months | The Engineer will remain monitor & inspect the leakage area and propose repairs to structure. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S8 | Other Damage/Defects | Health and Safety | It concerns with water accumulation on the working floor along with active water leakage which present a risk of potential injury resulting from slip hazard. The water from the pipes of cooler was dripping inside the building and water was accumulated at multiple locations which can be cause slip hazard. | Fix the drain system from where the water is leaking and keep the floor dry. | 1 month | We will fix repaired Immediately all leaked pipes and covering the leakage area with an additional tray to contain the water. Fix the drain system to stop water leakage and ensure proper drainage. Maintain a dry floor by regularly monitoring and managing water accumulation. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Other Damage/Defects | Health and Safety | It concerns with inadequate edge protection which present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of services The edge protection the loading dock area and the roof of the main production building is missing. | Provide appropriate edge protection on the roof of main production building. | 1 month | We are working on this issue and planning design edge protection of the roof and on all sides of the main production building. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Other Damage/Defects | Health and Safety | It concerns with inadequate edge protection which present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of services The edge protection the loading dock area and the roof of the main production building is missing. | Either provide appropriate edge protection on the loading dock area or keep the doors closed. | 1 month | We assure that the door is always kept closed and locked, with access only during loading/unloading time. Door usage controlled to ensure safety. |  |  |  | In Progress

## E Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Cable size
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery | Fixtures
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## F Categories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply | Chemicals handling | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants | Chemicals storage | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## S Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Leaking Pipes
Table 8 | [5 empty] | Damaged structural element
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type