## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
17-Feb-2025
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Fashion & Trends (Pvt.) Ltd. - Millat Industrial Estate, Millat Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 17-Feb-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-05 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2 +3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that, electrical single line diagrams (SLDs) for the factory were not available. This deficiency was noted in all electrical rooms and areas distribution boards where SLDs should be prominently displayed. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that, electrical single line diagrams (SLDs) for the factory were not available. This deficiency was noted in all electrical rooms and areas distribution boards where SLDs should be prominently displayed. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4 +2 months | 2026-01-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacks electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 months | 2025-09-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacks electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6 +3 months | 2026-05-30 | 2026-08-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable including: i. LT room in Building 4 that is 35sqmm cable with 400A breaker ii. Main electrical panel of Building 1 that is 25 sq mm cable with 125A breaker iii. Washing department that is 6 sq mm cable with 100A breaker iv. Breaker at LT room in Building 4 that is 25 sq mm cable with 225A breaker | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable ampacity after applying derating factors. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Hot Spots | The thermographic survey identified numerous hot spots within panels and distribution boards such as: • Abnormal temperature found in LT panel that is 75.9°C • Abnormal temperature found in LT panel that is 71.2°C • Abnormal temperature found in electrical panel at compressor room of Building 5 that is 71.7°C • Abnormal temperature found in distribution board#3 in washing hall at Building 1 that is 84.1°C | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | The thermographic survey identified numerous hot spots within panels and distribution boards such as: • Abnormal temperature found in LT panel that is 75.9°C • Abnormal temperature found in LT panel that is 71.2°C • Abnormal temperature found in electrical panel at compressor room of Building 5 that is 71.7°C • Abnormal temperature found in distribution board#3 in washing hall at Building 1 that is 84.1°C | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | The thermography report for the factory was not available. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections such as earth circuits found missing in electrical panel of dyeing Building 4, electrical panel at generator room, PDB#1 at Building 6, electrical panel at compressor room at building-5 etc. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | Equipotential bonding for the machines, cable trays and metallic panel covers was missing. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | Factory lacks earthing drawings and testing results. | Conduct earth testing and develop earthing drawings. Submit it to Pakistan Accord for information. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified such as missing of earth connection and equipotential bonding. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E14 +6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was observed that loose electrical components with damaged mounting: This poses a significant risk of equipment damage or electrical incidents due to the instability of the receptacles, observations found in electrical panel at washing machine and Reverse Osmosis Plant panel. | Secure the loose electrical components with appropriate fixed supports to prevent movement and ensure stable connections. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was observed that loose electrical components with damaged mounting: This poses a significant risk of equipment damage or electrical incidents due to the instability of the receptacles, observations found in electrical panel at washing machine and Reverse Osmosis Plant panel. | Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Loop Connection | During the inspection found loop connections in several electrical panels such as in power panel of warping department and dyeing area. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed in a number of electrical panels across the facility such as in electrical panel at dyeing Building 4, LDB#1 in Building 6, electrical panel at compressor room in Building 5, electrical panel of embroidery department in Building 2 etc. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Openings | The inspection revealed observation on unsealed openings that were discovered in the panels and distribution boards at several locations such as in main electrical panel of Building 6, distribution board#3 at washing hall of Building 1, in Warehouse main electrical panel, electrical panel of boiler etc. | Corrective actions are required to seal all openings to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Openings | Unsealed openings were discovered in the distribution boards within the facility. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | E20 +3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Adequate accessibility | At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components such as at LT room, distribution board#1 at ground floor of Sewing-2 in Building 1, electrical panel in washing department, electrical panel in compressor room in Building 5 etc. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems such as in changeover panel at generator area, electrical panel at Building 2, electrical panel of Packing department at Building 2, in transformer room etc. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Lint & dust inside panel board | Lint & dust found inside panel boards within the facility. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 1 months | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 1 months | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | If the risk assessment concludes that an LPS is necessary then hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. Establish a routine maintenance schedule to inspect and maintain the LPS, ensuring ongoing protection against corrosion. | E25 +6 months | 2025-10-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | LPS conductors showed signs of corrosion and rust, which can significantly impair the performance and reliability of the lightning protection system. | Perform a thorough inspection of all LPS conductors. Replace any conductors showing signs of corrosion or rust with new components that meet the current standards. Apply protective coatings or use materials resistant to corrosion to prevent future deterioration of LPS components. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | LPS conductors showed signs of corrosion and rust, which can significantly impair the performance and reliability of the lightning protection system. | Establish a routine maintenance schedule to inspect and maintain the LPS, ensuring ongoing protection against corrosion. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. One addressable fire alarm panel was installed for the facility, the system has inadequate detection coverage, insufficient manual call points, low audibility in several areas while some areas has poor audibility and inadequate coverage of visual alarm. | Ensure the functionality and performance of the existing alarm and detection system within the building | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. One addressable fire alarm panel was installed for the facility, the system has inadequate detection coverage, insufficient manual call points, low audibility in several areas while some areas has poor audibility and inadequate coverage of visual alarm. | i. Submit design documentation for new FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non compliant system was installed in the facility. | ii. Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E30 +1 month | 2025-12-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non compliant system was installed in the facility. | iii. Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E31 +4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non compliant system was installed in the facility. | iv. Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E32 +5 months | 2026-05-30 | 2026-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non compliant system was installed in the facility. | v. Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E33 +3 months | 2026-10-30 | 2027-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non compliant system was installed in the facility. | vi. Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E34 +3 months | 2027-01-30 | 2027-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Maintenance records | It was observed that routine testing of the Fire Alarm and Detection System (FADS) has not been performed consistently. | Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | 1 months | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations such as staircase of Building 1, at canteen in Building 4, first floor of Building 2, at finishing department ground floor of Building 1. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations such as staircase of Building 1, at canteen in Building 4, first floor of Building 2, at finishing department ground floor of Building 1. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E37 +6 months | 2025-11-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Emergency Lighting | Provided but insufficient | The following observations were made: i. Several areas lack sufficient emergency lighting coverage such as in LT room, generator room, FACP room and within production floors etc. ii. Installed emergency lights are too dim to provide adequate illumination such as in dyeing department at Building 4. iii. The backup power supply to the emergency luminaires is insufficient. | i. Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation and submit emergency layout to Pakistan Accord. ii. Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies iii. Upgrade the backup power supply to ensure it can adequately support all emergency luminaires during a power failure. This includes installing additional battery packs or generators as necessary to comply with the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Emergency Lighting | Provided but insufficient | It was observed that the emergency lights and directional signs have inadequate coverage pose serious risk of failure during a fire. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E39 +4 months | 2026-03-30 | 2026-07-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | A non compliant system was installed in the facility. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Generator, Transformer & Sub-Station Room | Battery | It was observed that battery terminals were exposed and not properly insulated at generator room, increasing the risk of electrical shock or short circuits. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Generator, Transformer & Sub-Station Room | Battery | It was observed that battery terminals were exposed and not properly insulated at generator room, increasing the risk of electrical shock or short circuits. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust such as at LT room, substation room etc, which poses a serious fire risk. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust such as at LT room, substation room etc, which poses a serious fire risk. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | E45 +6 months | 2025-11-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections, such as distribution board #2 at ground floor Sewing-1 in Building 1. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections, such as distribution board #2 at ground floor Sewing-1 in Building 1. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | E47 +6 months | 2026-01-30 | 2026-07-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together, such as distribution board #1 in packing department at Building 2. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together, such as distribution board #1 in packing department at Building 2. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance and provide continuous training for staff on proper jointing techniques. | E49 +6 months | 2026-01-30 | 2026-07-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Cabling & Wiring | Splicing of cables | Machine power wires were inserted directly into power receptacles without a power plug such as at reverse osmosis plant. | Replace the directly inserted power wires with proper power plugs to ensure safe and secure connections. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Cabling & Wiring | Splicing of cables | Machine power wires were inserted directly into power receptacles without a power plug such as at reverse osmosis plant. | Develop and enforce a facility-wide electrical safety protocol that mandates the use of power plugs for all equipment. Conduct regular safety audits and provide training sessions to staff to reinforce the importance of using proper power plugs and adherence to electrical safety standards. | E51 +6 months | 2026-01-30 | 2026-07-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified such as in main electrical panel of Building 1, electrical panel at cutting in Building 4, distribution board #2 at first floor of Building 1, distribution board #3 at first floor of Building 2. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified such as in main electrical panel of Building 1, electrical panel at cutting in Building 4, distribution board#2 at first floor of Building 1, distribution board #3 at first floor of Building 2. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | E53 +6 months | 2025-11-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Cabling & Wiring | Fixtures | Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance as observed at power switches at printing department second floor of Building 1, power switches at compressor room. | Replace or repair broken and exposed power receptacles immediately to restore safe and secure connections. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Cabling & Wiring | Fixtures | Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance as observed at power switches at printing department second floor of Building 1, power switches at compressor room. | Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. | E55 +6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
17-Feb-2025
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Fashion & Trends (Pvt.) Ltd. - Millat Industrial Estate, Millat Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 17-Feb-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-05 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | Escape doors are lockable/ locked - Throughout facility lockable gates - Locked exit gate knitting hall -Building#6. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | Escape doors are lockable/ locked - Throughout facility lockable gates - Locked exit gate knitting hall -Building#6. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | Escape doors are lockable/ locked - Throughout facility lockable gates - Locked exit gate knitting hall -Building#6. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | Obstructions on exit access escape route - Blocked exit accounts B 2 1st floor stitch area - Manholes along exit access route -Building#7- Ground floor area - Stair discharge inside building - Building#4 -Stairs S #15,S#10,S#8,S-12,S#11,S317,S#1,S#2. | Remove obstructions on escape routes and keep them clear for escape. Cover any holes and uneven areas in escape routes. | 2 weeks' | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | Obstructions on exit access escape route - Blocked exit accounts B 2 1st floor stitch area - Manholes along exit access route -Building#7- Ground floor area - Stair discharge inside building - Building#4 -Stairs S #15,S#10,S#8,S-12,S#11,S317,S#1,S#2. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Exit access | Obstructions on exit access escape route - Blocked exit accounts B 2 1st floor stitch area - Manholes along exit access route -Building#7- Ground floor area - Stair discharge inside building - Building#4 -Stairs S #15,S#10,S#8,S-12,S#11,S317,S#1,S#2. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F6+4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Number of exits | Single exit from some of the occupied floors -Building#4-2nd floor canteen area - 2 exits for 600 people | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Number of exits | Single exit from some of the occupied floors -Building#4-2nd floor canteen area - 2 exits for 600 people | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Standard. | F 8 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Protection of stairs | Unprotected penetrations into stairs- Building#2-Stair #S-9 - Doors are not fire doors - All stairs - Door self-closers are missing - All stairs - Fire load in stairs -Building#2-Stair #S-9 fire load under stairs - Services passing through or within stairs -Building#4-1st floor -Stair #S-16 | Remove fire load and any other obstructions due to stored items from stairs | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Protection of stairs | Unprotected penetrations into stairs- Building#2-Stair #S-9 - Doors are not fire doors - All stairs - Door self-closers are missing - All stairs - Fire load in stairs -Building#2-Stair #S-9 fire load under stairs - Services passing through or within stairs -Building#4-1st floor -Stair #S-17 | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Protection of stairs | Unprotected penetrations into stairs- Building#2-Stair #S-9 - Doors are not fire doors - All stairs - Door self-closers are missing - All stairs - Fire load in stairs -Building#2-Stair #S-9 fire load under stairs - Services passing through or within stairs -Building#4-1st floor -Stair #S-18 | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F11+ 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Escape stair condition | There are no handrails-Building#4-Stair #S-15 | - Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Escape stair condition | There are no handrails-Building#4-Stair #S-15 | Ensure the following are provided: - Stair structure to be fixed so that stairs are safe for escape. | F13+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated from the rest of the building -Building#4-Ground floor exit discharge not protected - External escape routes are through high-risk areas -Building#7 &4 -Ground floor - External escape route passing through boiler - Manholes and obstructions along exit discharge route - Building#4 &7- Exit discharge route -Boiler area | Remove obstructions on external escape routes and keep them clear for escape. Cover any holes and uneven areas in external escape routes." | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated from the rest of the building -Building#4-Ground floor exit discharge not protected - External escape routes are through high-risk areas -Building#7 &4 -Ground floor - External escape route passing through boiler - Manholes and obstructions along exit discharge route - Building#4 &7- Exit discharge route -Boiler area | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes Provide additional exits from site. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated from the rest of the building -Building#4-Ground floor exit discharge not protected - External escape routes are through high-risk areas -Building#7 &4 -Ground floor - External escape route passing through boiler - Manholes and obstructions along exit discharge route - Building#4 &7- Exit discharge route -Boiler area | - Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high-risk areas | F16+ 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Means of Escape | Exit signage | Missing exit signs at entry into stairs -All stairs - Missing exit signs in production areas - All production areas - Missing exit signs in offices and back of house areas - All site - Missing exit signs at roof- Building#2-Roof - Electrically powered exit signs are not a tested and listed system | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Means of Escape | Exit signage | Missing exit signs at entry into stairs -All stairs - Missing exit signs in production areas - All production areas - Missing exit signs in offices and back of house areas - All site - Missing exit signs at roof- Building#2-Roof - Electrically powered exit signs are not a tested and listed system | Ensure that all exit signage is checked periodically and in good working condition. | F 18+ 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building - Electrical rooms are not fire separated - Main Electrical rooms - Generator room is not fire separated - Main Generator area - Boiler area is not fire separated - Building#4&7-Ground floor - Fuel storage areas are not fire separated - Main exit site - Fuel Bund is missing also | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building - Electrical rooms are not fire separated - Main Electrical rooms - Generator room is not fire separated - Main Generator area - Boiler area is not fire separated - Building#4&7-Ground floor - Fuel storage areas are not fire separated - Main exit site - Fuel Bund is missing also | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F20 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Separation of occupancies | Large office areas not fire separated from the production areas - Building#1- Ground floor - Production and storage areas not fire separated -Building#4-Ground floor | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors) | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Separation of occupancies | Large office areas not fire separated from the production areas - Building#1- Ground floor - Production and storage areas not fire separated -Building#4-Ground floor | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F22 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Separation of occupancies | No adequate automatic fire detection and alarm system - Building#2 -Roof floor, Ground floor CEO office - Lack of fire rated separation between the dormitory and other occupancy types-Building#2 -Roof floor, Ground floor CEO office | "The dormitory is not to be used until minimum requirements for sleeping occupancies have been provided. Alternative arrangements must be sought immediately for the dormitory as continuing the use of the building for this purpose is not appropriate. Dormitory not to be re-occupied until the minimum requirements have been implemented." | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of occupancies | No adequate automatic fire detection and alarm system - Building#2 -Roof floor, Ground floor CEO office - Lack of fire rated separation between the dormitory and other occupancy types-Building#2 -Roof floor, Ground floor CEO office | Document proposals for design of remedial measures to ensure compliance with all fire safety requirements for sleeping occupancies to comply with Pakistan Accord Standard. Submit proposals to Pakistan Accord for review. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Separation of occupancies | No adequate automatic fire detection and alarm system - Building#2 -Roof floor, Ground floor CEO office - Lack of fire rated separation between the dormitory and other occupancy types-Building#2 -Roof floor, Ground floor CEO office | Implement remediation measures to ensure full compliance with dormitory requirements of Pakistan Accord Standard and Pakistan Building Code in accordance with previously reviewed design. | F25+ 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building - Building#4-Ground floor -Chemical store and production area - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) - Building#4-Ground floor -Production area - Storage in exit stairs and/or stair discharge routes - Building#2-Ground floor -Stair #S-10. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building - Building#4-Ground floor -Chemical store and production area - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) - Building#4-Ground floor -Production area - Storage in exit stairs and/or stair discharge routes - Building#2-Ground floor -Stair #S-10. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F27 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Suppression | Standpipe system | Per Pakistan Accord Standard a Class-I standpipe systems is required in the building. The system should be designed and installed in accordance with NFPA 14. The following deficiencies have been observed on site, including (list not exhaustive): - Connection points are not compliant - All site - Pressure / flow is not adequate - Missing standpipe outlets in stairs- Building#4 & 2 & 1- Building#1(G+2 stories with area of 2711 sq.m ) , Building#2-(G+1 stories with area of 1822 sq.m) , Building#4 (G+1 with area of 6028 sq.m) | Replace any damaged equipment and ensure current system is fully operational. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Suppression | Standpipe system | Connection points are not compliant - All site - Pressure / flow is not adequate - Missing standpipe outlets in stairs- Building#4 & 2 & 1- Building#1(G+2 stories with area of 2711 sq.m ) , Building#2-(G+1 stories with area of 1822 sq.m) , Building#4 (G+1 with area of 6028 sq.m) | 1--Submit design documentation for a standpipe system (along with required fire water and pump system) and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certification of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Suppression | Standpipe system | Connection points are not compliant - All site - Pressure / flow is not adequate - Missing standpipe outlets in stairs- Building#4 & 2 & 1- Building#1(G+2 stories with area of 2711 sq.m ) , Building#2-(G+1 stories with area of 1822 sq.m) , Building#4 (G+1 with area of 6028 sq.m) | 2--Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F30+ 1 months | 2026-01-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Standpipe system | Connection points are not compliant - All site - Pressure / flow is not adequate - Missing standpipe outlets in stairs- Building#4 & 2 & 1- Building#1(G+2 stories with area of 2711 sq.m ) , Building#2-(G+1 stories with area of 1822 sq.m) , Building#4 (G+1 with area of 6028 sq.m) | 3--Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F31+3 months | 2026-02-28 | 2026-05-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Suppression | Standpipe system | Connection points are not compliant - All site - Pressure / flow is not adequate - Missing standpipe outlets in stairs- Building#4 & 2 & 1- Building#1(G+2 stories with area of 2711 sq.m ) , Building#2-(G+1 stories with area of 1822 sq.m) , Building#4 (G+1 with area of 6028 sq.m) | 4--Once installation of the SUPS system is complete, factory to submit full ""as-built" documentation of the system to Pakistan Accord for review. . | F 32+ 3 months | 2026-05-28 | 2026-08-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Suppression | Standpipe system | Connection points are not compliant - All site - Pressure / flow is not adequate - Missing standpipe outlets in stairs- Building#4 & 2 & 1- Building#1(G+2 stories with area of 2711 sq.m ) , Building#2-(G+1 stories with area of 1822 sq.m) , Building#4 (G+1 with area of 6028 sq.m) | 5--Factory to advise Pakistan Accord when SUPS installation is fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F33+ 3 months | 2026-08-28 | 2026-11-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Suppression | Standpipe system | Connection points are not compliant - All site - Pressure / flow is not adequate - Missing standpipe outlets in stairs- Building#4 & 2 & 1- Building#1(G+2 stories with area of 2711 sq.m ) , Building#2-(G+1 stories with area of 1822 sq.m) , Building#4 (G+1 with area of 6028 sq.m) | 6--Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete. | F34 + 4 months | 2026-11-28 | 2027-03-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Suppression | Fire pumps | There is no diesel pump - There is no main electric pump - There is no jockey pump | Provide electric duty pump, diesel backup fire pumps and jockey pumps, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system. -Ensure above 6 points Standpipe system | 18 months | 2025-09-30 | 2027-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Suppression | Water supply | No separate fire water tank | Develop a rectification plan to provide adequate fire water supplies. The plan should demonstrate compliance with NFPA 22 . Submit the plan to Accord for review and approval prior to implementation on site. Prepare design and drawings for a new dedicated fire water tank (or combined tank with dedicated fire water section). The design shall comply with Building Code of Pakistan and NFPA 22 . These should be submitted Pakistan Accord for review. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Suppression | Water supply | No separate fire water tank | Implement the plan agreed with Pakistan Accord. | F37+ 14 months | 2026-01-30 | 2027-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Suppression | Fire extinguishers | Insufficient coverage of fire extinguishers - Production areas | Ensure that all building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Suppression | Fire extinguishers | Insufficient coverage of fire extinguishers - Production areas | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | F39+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Hazardous Materials | Chemicals handling | Unsafe handling procedures- Building#4-Chemical store / Washing area -SOPs not available - Inadequate ventilation of areas with chemical handling -Building#4-Ground floor -Chemical storeroom | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Hazardous Materials | Chemicals handling | Unsafe handling procedures- Building#4-Chemical store / Washing area -SOPs not available - Inadequate ventilation of areas with chemical handling -Building#4-Ground floor -Chemical storeroom | Implement the chemical handling strategy on site as agreed with Pakistan Accord. | F41+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Hazardous Materials | Chemicals storage | Flammable materials are not stored in a fire separated room-Building#4-Ground floor - Inadequate ventilation of chemical storage areas- Building#4-Ground floor | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | F44 | Hazardous Materials | Chemicals storage | Flammable materials are not stored in a fire separated room-Building#4-Ground floor - Inadequate ventilation of chemical storage areas- Building#4-Ground floor | Implement the above plan on site. All chemical storage areas to be compliant with Pakistan Accord Standard. | F43 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | F45 | Hazardous Materials | Diesel storage | Diesel storage is not fire separated from the rest of the building - 5000 litre Diesel storage near mosque and main exit -Diesel Storage without bunding | Prepare drawings showing the proposed diesel storage arrangements to comply with NFPA 30. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of the proposed diesel storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms - Bunding details | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | F46 | Hazardous Materials | Diesel storage | Diesel storage is not fire separated from the rest of the building - 5000 litre Diesel storage near mosque and main exit -Diesel Storage without bunding | Implement the above plan on site. All diesel storage areas to be compliant with Pakistan Accord Standard. | F45+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | F47 | Fire Safety Management | Fire drills | No regular fire drills - Fire drill documentation is of poor standard - Not all staff are involved in fire drills - Not all staff know what to do in the event of fire | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | F48 | Fire Safety Management | Fire drills | No regular fire drills - Fire drill documentation is of poor standard - Not all staff are involved in fire drills - Not all staff know what to do in the event of fire | Ensure fire drills are performed a minimum 2 times per year. | F47 + 2 months | 2025-11-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | F49 | Fire Safety Management | Records of system testing | No records of testing of Fire Pumps - No records of testing of Standpipes - No records of testing of Fire Extinguishers | Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Pakistan Accord for review and approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | F50 | Fire Safety Management | Records of system testing | No records of testing of Fire Pumps - No records of testing of Standpipes - No records of testing of Fire Extinguishers | - Ensure all systems are being tested as per the schedule agreed with Pakistan Accord. - Keep testing records. | F49 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | F51 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps - Inadequate records of maintenance of Standpipes - No records of maintenance of Fire Extinguishers | - Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Pakistan Accord for review and approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | F52 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps - Inadequate records of maintenance of Standpipes - No records of maintenance of Fire Extinguishers | - Ensure all systems are being maintained as per the schedule agreed with Pakistan Accord . - Keep maintenance records. | F51+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | F53 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels - All site - There is not standard EAP document which details procedures, roles and responsibilities in the event of fire | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | F54 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels - All site - There is not standard EAP document which details procedures, roles and responsibilities in the event of fire | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F53 + 2 months | 2025-11-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
17-Feb-2025
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Fashion & Trends (Pvt.) Ltd. - Millat Industrial Estate, Millat Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2025-02-17
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | No |  | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-05 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns appear to be over stressed for the observed load in Building-1. The size of column and presence of low rebar percentage could be the reason for these highly stressed columns. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns or existing cylinder strength data and submit results to Pakistan Accord. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns appear to be over stressed for the observed load in Building-1. The size of column and presence of low rebar percentage could be the reason for these highly stressed columns. | Factory Engineer to review design, loads and columns stresses in area identified. | S2+1 months | 2025-12-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns appear to be over stressed for the observed load in Building-1. The size of column and presence of low rebar percentage could be the reason for these highly stressed columns. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S3+3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns appear to be over stressed for the observed load in Building-4. The size of column and larger grids could be the reason for these highly stressed columns. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns or existing cylinder strength data and submit results to Pakistan Accord. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns appear to be over stressed for the observed load in Building-4. The size of column and larger grids could be the reason for these highly stressed columns. | Factory Engineer to review design, loads and columns stresses in area identified. | S5+1 months | 2025-12-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns appear to be over stressed for the observed load in Building-4. The size of column and larger grids could be the reason for these highly stressed columns. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S6+3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Cracking | Beams | Beam cracking at the Ground floor in an interior bay has been observed in Building 2, it might occur due to the reduction in capacity as compared to the applied loading on the floor. | Building Engineer to carry out condition survey of the RC beams to investigate cause and impact of these cracks on the capacity of the beams. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Cracking | Beams | Beam cracking at the Ground floor in an interior bay has been observed in Building 2, it might occur due to the reduction in capacity as compared to the applied loading on the floor. | Propose the remedial works to Pakistan Accord in situation if the RC beams are not in line with the design requirements. | S8+1 months | 2025-11-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Cracking | Beams | Beam cracking at the Ground floor in an interior bay has been observed in Building 2, it might occur due to the reduction in capacity as compared to the applied loading on the floor. | Once reviewed, implement the remedial works. Continue monitoring them on an on-going basis. | S9+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Structural System | Lack of local stability | Poor connection details and lack of local stability in supporting mechanism of steel staircase has been observed in Building-3. | Building Engineer to review the design of staircase and propose any strengthening measures as required. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Structural System | Lack of local stability | Poor connection details and lack of local stability in supporting mechanism of steel staircase has been observed in Building-3. | Implement the Remediation as required. | S11+ 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in the column, present at roof level, is exposed to atmospheric corrosion in Building-6. This may affect the structural integrity over the period and for future vertical expansion in the building. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in the column, present at roof level, is exposed to atmospheric corrosion in Building-6. This may affect the structural integrity over the period and for future vertical expansion in the building. | Implement the approved remedial work. | S13+ 1 month | 2025-11-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-2. This may affect the structure integrity over period and for future vertical expansion in the building. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-2. This may affect the structure integrity over period and for future vertical expansion in the building. | Implement the approved remedial work. | S15+ 1 month | 2025-11-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-1. This may affect the structure integrity over period and for future vertical expansion in the building. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-1. This may affect the structure integrity over period and for future vertical expansion in the building. | Implement the approved remedial work. | S17+ 1 month | 2025-11-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-3. This may affect the structure integrity over period and for future vertical expansion in the building. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-3. This may affect the structure integrity over period and for future vertical expansion in the building. | Implement the approved remedial work. | S19+ 1 month | 2025-11-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-4. This may affect the structure integrity over period and for future vertical expansion in the building. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level is exposed to atmospheric corrosion in Building-4. This may affect the structure integrity over period and for future vertical expansion in the building. | Implement the approved remedial work. | S21+ 1 month | 2025-11-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Other Damage/Defects | Moisture ingress | Water ingress and leakage are potentially causing damage to RC columns supporting the steel shed. Improper drainage of the roof slab in Building-1, particularly due to the presence of rainwater during the rainy season, might cause corrosion in reinforcement and concrete spalling, which can result in injuries. Furthermore, water ingress was observed in RC beam and slab elements at first floor level of Building-1. | Identify the source of water ingress and propose measures to prevent further water damage. Inspect damage to the supporting members and propose repairs to the structure. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Other Damage/Defects | Moisture ingress | Water ingress and leakage are potentially causing damage to RC columns supporting the steel shed. Improper drainage of the roof slab in Building-1, particularly due to the presence of rainwater during the rainy season, might cause corrosion in reinforcement and concrete spalling, which can result in injuries. Furthermore, water ingress was observed in RC beam and slab elements at first floor level of Building-1. | Submit the report capturing above to Pakistan Accord for approval. | S23+ 1 month | 2025-10-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Other Damage/Defects | Moisture ingress | Water ingress and leakage are potentially causing damage to RC columns supporting the steel shed. Improper drainage of the roof slab in Building-1, particularly due to the presence of rainwater during the rainy season, might cause corrosion in reinforcement and concrete spalling, which can result in injuries. Furthermore, water ingress was observed in RC beam and slab elements at first floor level of Building-1. | Implement the remedial works. | S24+ 1 month | 2025-11-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S26 | Other Damage/Defects | Moisture ingress | Water ingress and leakage are potentially causing damage to RC columns supporting the steel shed. Improper drainage of the roof slab in Building-1, particularly due to the presence of rainwater during the rainy season, might cause corrosion in reinforcement and concrete spalling, which can result in injuries. Furthermore, water ingress was observed in RC beam and slab elements at first floor level of Building-1. | Continue to monitor for future signs of water ingress. | S25+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S27 | Other Damage/Defects | Health and Safety | No adequate edge protection is provided to the roof of Building-1. This can cause a risk of potential injury resulting from slip, trip, or fall from the roof during the access and maintenance of the roof. | Provide appropriate roof edge protection to all accessible roofs. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S28 | Other Damage/Defects | Health and Safety | No adequate edge protection is provided to the roof of Building-2. This can cause a risk of potential injury resulting from slip, trip, or fall from the roof during the access and maintenance of the roof. | Provide appropriate roof edge protection to all accessible roofs. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S29 | Other Damage/Defects | Health and Safety | No adequate edge protection is provided to the roof of Building-3. This can cause a risk of potential injury resulting from slip, trip, or fall from the roof during the access and maintenance of the roof. | Provide appropriate roof edge protection to all accessible roofs. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S30 | Other Damage/Defects | Health and Safety | No adequate edge protection is provided to the roof of Building-4. This can cause a risk of potential injury resulting from slip, trip, or fall from the roof during the access and maintenance of the roof. | Provide appropriate roof edge protection to all accessible roofs. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S31 | Other Damage/Defects | Health and Safety | No adequate edge protection is provided to the roof of Building-6. This can cause a risk of potential injury resulting from slip, trip, or fall from the roof during the access and maintenance of the roof. | Provide appropriate roof edge protection to all accessible roofs. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S32 | Structural Documentation | Documentation unavailable | As-built detailed architectural drawings including sections and structural drawings were missing for all buildings. | Building Structural Engineer to carry out on-site survey, collect information, and produce accurate and complete as-built documentation. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S33 | Structural Documentation | Non-engineered structure | Non-engineered steel shed structures were observed in Building 1. These structures might be unstable against gravity and wind loads. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S34 | Structural Documentation | Non-engineered structure | Non-engineered steel shed structures were observed in Building 1. These structures might be unstable against gravity and wind loads. | Propose strengthening works as required and submit to Pakistan Accord for approval. | S33+ 2 months | 2025-11-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S35 | Structural Documentation | Non-engineered structure | Non-engineered steel shed structures were observed in Building 1. These structures might be unstable against gravity and wind loads. | Implement strengthening works as required. | S34+ 2 months | 2026-01-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S36 | Structural Documentation | Non-engineered structure | Non-engineered steel shed structures observed in Building-7. These structures might be unstable against gravity and wind loads. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S37 | Structural Documentation | Non-engineered structure | Non-engineered steel shed structures observed in Building-7. These structures might be unstable against gravity and wind loads. | Propose strengthening works as required and submit to Pakistan Accord for approval. | S36+ 2 months | 2025-11-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S38 | Structural Documentation | Non-engineered structure | Non-engineered steel shed structures observed in Building-7. These structures might be unstable against gravity and wind loads. | Implement strengthening works as required. | S37+ 2 months | 2026-01-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S39 | Structural Documentation | Lack of safe load plans | Floor wise safe load plans were missing for buildings (1, 2 and 4). | Building structural engineer to review the design documentation to confirm the load capacity of the structure. Factory to post safe load plans on each floor. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1