## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
2024-10-01
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Al-Hadi Textile (Pvt.) Ltd. - Rohi Nala 3.5 Km Off: 22-Km Ferozepur Road, Lahore, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 01-Oct-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-06-25 | 2025-08-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | Electrical single line diagrams (SLDs) were incomplete limited to LT Room. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Single Line Diagram (SLD) | Electrical single line diagrams (SLDs) were incomplete limited to LT Room. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E2 + 4 months | 2025-11-20 | 2026-03-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Electrical layout drawing | Factory lacked electrical layout drawings for all units including small power layouts, lighting layouts, and containment layouts. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-08-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | DBs & Elec Protection Systems | Circuit breakers | Multiple circuit breakers had ratings that were not appropriate for the connected cable size specifically observed at the Building 2 second floor distribution board,100A MCCB with 6mm cable. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Hot spots were observed particularly at the following locations: 1. LT Room small offices distribution board 2. Yarn dyeing main distribution board Building 1: a. Ground floor dyeing main machine panel b. 1st floor main distribution board c. Office distribution board ground floor Dyeing Hall Building 2: a. Cutting department main distribution board at second floor b. RO plant panel | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted, and appropriate remedial actions have been implemented to resolve the underlying issues. During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-08-20 | 2025-09-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | DBs & Elec Protection Systems | Hot Spots | Thermographic inspection report was not provided. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. Provide thermographic report to Pakistan Accord .Perform thermographic inspection once in 6 months. | 6 months | 2025-08-20 | 2026-02-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Earthing system | i. Several distribution boards lacked earthing cables. It was specifically observed at following locations: a. Distribution board at Building 1 ground floor dyeing halls. b. Distribution board at RO plant room. c. Main distribution board at acro store at Building 2. | i. Design and evaluate the earthing system installation throughout the facility and provided earth in all required distribution board and panels. Provide earthing drawings to Pakistan Accord for review. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Earthing system | ii. Earthing of the electrical equipment were missing specifically at the following locations a. RO Plant b. Fire pump at RO plant room c. Machines at Building 2 ground floor. | ii. Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Earthing system | iii. Equipotential bonding of the cable trays and ladder was not carried throughout the facility. | iii. Implement equipotential bonding for all equipment or cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Panel/cabling/busbar | i. In a number of areas, it was observed that electrical components were improperly installed inside boards further the dressing of the wire inside the boards were unsafe specifically observed at following locations: a. Building 1 ground floor all distribution boards and panels. b. Distribution board at RO plant room. c. Fire pump distribution board. d. Canteen distribution board. | i. Identify and install electrical component as per the manufacturer provided guidelines in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | ii. Several electrical panels exhibited non-compliance to IP rating, signs of corrosion, indicating potential exposure to moisture or other corrosive elements .These observations were made at the following location specifically. a. Distribution board at RO plant room. | ii. Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. Provided compliance to IP rating as per IEC-61349. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Loop Connection | Loop connections were found on the following locations: 1. Distribution board at LV Room. 2. Distribution boards at Building 1 ground floor. 3. Distribution board at RO plant room. 4. Main distribution board at Building 2, second floor. 5. Acro store distribution board at Building 2. 6. Distribution board for printing and cutting at second floor Building 2. 7. Canteen distribution board. | All-electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Multiple Connections | Multiple connection were observed at the following locations: i. Canteen distribution board ii. Acro store distribution boards at Building 2. iii. Main distribution board on second floor Building 2. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Openings | 1. Unsealed openings were discovered within the panels and distribution boards. a. At panel room electrical panels at ground floor. b. RO Plant room panels. c. Building 1, ground floor panels. 2. Back cover of the panels missing in incoming supply panel of LT Room. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Adequate accessibility | The electrical panels do not possess the required space for inspection or easy access to the panels and their components specifically at the following locations 1. HT panel room placed inside a small space lacking safe clearance around, also the HT panels room lacks wall /door to restrict access. 2. Transformer does not possess adequate space around to safely inspect and perform maintenance. 3. LT Room panels does not have adequate space around specifically from the back of the panels to do the inspection and troubleshooting. 4. Electrical room for stentor machines at Building 1 ground floor does not have adequate clearance. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Lint & dust | Significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. These issues were observed in following locations: 1. RO plant distribution boards. 2. Canteen distribution boards. 3. Distribution board at ground floor of Building 1. 4. Cable channels above stitching lines throughout the facility. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 1 month | 2025-08-20 | 2025-09-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | LPS risk assessment was not provided. | i. Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 1 month | 2025-08-20 | 2025-09-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | i. A single early streamer emission arrestor was incorrectly installed at the Building 2 roof top above elevator room. ii. No test results were provided for the lightning protection system, making it difficult to verify its effectiveness and compliance with relevant standards. | i. If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). ii. If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. | E18 + 4 months | 2025-09-20 | 2026-01-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The facility's fire alarm system is conventional and non-listed, with issues including insufficient detection and alarm coverage, improper detector installation, and use of non-fire-rated cables. Additionally, manual call points are missing in key locations, and four out of five panels failed to detect or activate during testing. | i. Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | ii. Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E20 +1 month | 2025-11-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | iii. Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E21+ 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | iv. Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E22 + 5 months | 2026-04-20 | 2026-09-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | v. Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E23 + 3 months | 2026-09-20 | 2026-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | vi. Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E24 + 3 months | 2026-12-20 | 2027-03-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | Emergency Lighting | Provided but non-functional | Non-compliant emergency lights were installed, with many missing from required locations 1. Canteen 2. Chemical store 3. Building 2 ground floor knitting area. 4. Wash store at Building 2. 5. Ground floor dyeing area in Building 1. 6. LT Room at ground floor. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Provided emergency lighting layouts to Pakistan Accord for review. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | Emergency Lighting | Provided but non-functional | Non-compliant emergency lights were installed, with many missing from required locations 1. Canteen 2. Chemical store 3. Building 2 ground floor knitting area. 4. Wash store at Building 2. 5. Ground floor dyeing area in Building 1. 6. LT Room at ground floor. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | Emergency Lighting | Provided but insufficient | i. Emergency lights were provided only at the emergency exit doors. However, no emergency lights were provided at the ingress routes between the floors. | i. Conduct a comprehensive survey to identify areas lacking adequate emergency lighting and exit signages. Install additional emergency luminaires and directional exit signages in these areas to meet the coverage requirements specified in the building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | Emergency Lighting | Provided but insufficient | ii. No emergency lights were provided at Building 2 staircase. | ii. Install emergency lights in all staircases as per the code compliances of building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | Emergency Lighting | Provided but insufficient | iii. Multiple emergency luminaires indicate the need for maintenance. a. Observed throughout the facility specifically at first floor shed area. | iii. Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | Emergency Lighting | Provided but insufficient | iv. External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations. a. Specifically observed at the outdoor assembly area. | iv. Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s) | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Emergency Lighting | Provided but insufficient | v. Directional exit lights were insufficient and does not provide at each diversion to identify the exit further the exit signage were not illuminated. a. Observed throughout the facility. | v. Install directional exit lights at all the required location as per the code compliances of building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Emergency Lighting | Independent power source | The emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. This issue is observed throughout the facility. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Emergency Lighting | Independent power source | Emergency lights were connected to nearby power source. | Provide independent circuit to emergency layout. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Emergency Lighting | General Lighting | The following observations were noted. Several locations were identified as lacking sufficient general lighting. Observed at the following locations: i. Staircase towards roof at Building 1. ii. Staircase towards roof at Building 2. | Conduct a thorough assessment of lighting throughout the facility to find areas with insufficient illumination. Install additional lighting fixtures in these spots to ensure adequate brightness. Ensure the new lighting design meets safety and efficiency guidelines to provide clear visibility for all tasks and emergency situations. | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | The following observations were made: i. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly in following locations a. Transformer Room b. LT Room c. Electrical room for machines at Building 1 ground floor | i. Reorganise the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways | 1 month | 2025-08-20 | 2025-09-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | ii. The HT Room, Transformer Room and the LV Room poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | ii. Add more lights to illuminate the HT Room, Transformer Room and LV Room. Evaluated all the spaces of factory to provide adequate lighting wherever applicable. | 1 month | 2025-08-20 | 2025-09-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Generator, Transformer & Sub-Station Room | Battery | i. Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. ii. The placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. | i. Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. ii. Reposition batteries that are improperly placed to ensure they comply with safety regulations, allowing for safe access and adequate ventilation. Mark and clear pathways around battery installations to ensure easy and safe access for maintenance and emergencies. | 1 month | 2025-08-20 | 2025-09-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Cabling & Wiring | Cables support and protection | i. Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. It was specifically observed at the following locations: a. LT Room b. Building 1 ground floor. c. Building 2 knitting area. d. RO Plant room | i. Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Cabling & Wiring | Cables support and protection | ii. Electrical cables were laid on floor without any appropriate protection and dressing. This arrangement creates a tripping hazard for personnel working in the area, and the cables are susceptible to damage from constant foot traffic, posing a trip hazard specially during an evacuation at following locations: a. Generator room b. HT Room | ii. Elevate the cables/ cable trays off the floor to eliminate tripping hazards and prevent damage from foot traffic in accordance with Regulation 522.6 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Cabling & Wiring | Cable trench and channel cleanliness | it was observed that the cleanliness of the cable trunking system had not been maintained. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Cabling & Wiring | Splicing of cables | i. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. a. RO plants distribution boards. b. Canteen distribution board. c. Distribution boards at Building 1 ground floor. d. Ground floor at Building 1. | i. Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. i. Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance and provide continuous training for staff on proper jointing techniques. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Cabling & Wiring | Colour coding | Several distribution boards, deviations from standard cable colour coding practices were identified. 1. Ground floor distribution boards at Building 1. 2. Distribution boards at RO plant room 3. Canteen distribution board. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Cabling & Wiring | Fixtures | The fixtures and receptacles were found broken at multiple locations. | Replace or repair broken and exposed power receptacles immediately to restore safe and secure connections. Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
2024-10-01
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Al-Hadi Textile (Pvt.) Ltd. - Rohi Nala 3.5 Km Off: 22-Km Ferozepur Road, Lahore, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 01-Oct-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-06-25 | 2025-08-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Protection of stairs | Un-protected stairs in Building 1. - Unprotected openings into stair S4 - Building 1 (roof) & stair S9 – Building 3 (ground floor). - Most of the doors not fire doors installed in stair openings of Building 1(including office area) & Building 2. - Fire load under stair S3- Building 2 (ground floor). - Fire load under stair S4- Building 1 (ground floor) & S2 at roof. - Lift shaft located in Stair 1 of Building 1. | Remove fire load and any obstructions due to stored items from stairs. | 2 weeks | 2025-08-20 | 2025-09-03 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Protection of stairs | Un-protected stairs in Building 1. - Unprotected openings into stair S4 - Building 1 (roof) & stair S9 – Building 3 (ground floor). - Most of the doors not fire doors installed in stair openings of Building 1(including office area) & Building 2. - Fire load under stair S3- Building 2 (ground floor). - Fire load under stair S4- Building 1 (ground floor) & S2 at roof. - Lift shaft located in Stair 1 of Building 1. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Protection of stairs | Un-protected stairs in Building 1. - Unprotected openings into stair S4 - Building 1 (roof) & stair S9 – Building 3 (ground floor). - Most of the doors not fire doors installed in stair openings of Building 1(including office area) & Building 2. - Fire load under stair S3- Building 2 (ground floor). - Fire load under stair S4- Building 1 (ground floor) & S2 at roof. - Lift shaft located in Stair 1 of Building 1. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90 minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F3 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Number of exits | Single exit from thread dying area Building 3 (roof) passing through Building 1. | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Building Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Number of exits | Single exit from thread dying area Building 3 (roof) passing through Building 1. | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Building Standard. | F5 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits in waste store area (found 37m ) - Building 1 (roof). Common path of travel distances exceed permitted limit in finished fabric store (found 39m) - Building 2 (2nd floor). | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits in waste store area (found 37m ) - Building 1 (roof). Common path of travel distances exceed permitted limit in finished fabric store (found 39m) - Building 2 (2nd floor). | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F7 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Escape doors | 1. Escape doors are lockable at stairs (S1 & S3) in Building-1 (Roof) & Building 3 (1st floor). 2. Escape doors are lockable at stairs (S3) in Building-2 (Roof). 3. Sliding doors serve for escape from stitch to pack areas in Building 1 (1st floor) & Building 2 (2nd floor). 4. Door swing against the direction of escape at Building 1(roof). | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-08-20 | 2025-09-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Escape doors | 1. Escape doors are lockable at stairs (S1 & S3) in Building-1 (Roof) & Building 3 (1st floor). 2. Escape doors are lockable at stairs (S3) in Building-2 (Roof). 3. Sliding doors serve for escape from stitch to pack areas in Building 1 (1st floor) & Building 2 (2nd floor). 4. Door swing against the direction of escape at Building 1(roof). | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Escape doors | 1. Escape doors are lockable at stairs (S1 & S3) in Building-1 (Roof) & Building 3 (1st floor). 2. Escape doors are lockable at stairs (S3) in Building-2 (Roof). 3. Sliding doors serve for escape from stitch to pack areas in Building 1 (1st floor) & Building 2 (2nd floor). 4. Door swing against the direction of escape at Building 1(roof). | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F10 + 1 month | 2025-11-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Exit access | Unprotected stair S1 discharges inside office area at Building 1 (ground floor). | Remove obstructions on escape routes and keep them clear for escape. | 2 weeks | 2025-08-20 | 2025-09-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Exit access | Unprotected stair S1 discharges inside office area at Building 1 (ground floor). | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Exit access | Unprotected stair S1 discharges inside office area at Building 1 (ground floor). | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. | F13 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Exit discharge | Exit discharge route not separated from boiler area on west side of Building-1 | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes. - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes. | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Exit discharge | Exit discharge route not separated from boiler area on west side of Building-2. | Ensure external exit discharge routes are adequately fire separated from the rest of the building. | F15 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Means of Escape | Exit signage | Missing exit signs at all the stairs & floors most of the places & entry of Building 1 & Building. 2.(roof). Missing exit signs at Building 3 (ground floor). | Remove misleading directional escape signs. | 2 weeks | 2025-08-20 | 2025-09-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Means of Escape | Exit signage | Missing exit signs at all the stairs & floors most of the places & entry of Building 1 & Building. 2.(roof). Missing exit signs at Building 3 (ground floor). | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Means of Escape | Exit signage | Missing exit signs at all the stairs & floors most of the places & entry of Building 1 & Building. 2.(roof). Missing exit signs at Building 3 (ground floor). | Ensure that all exit signage is checked periodically and in good working condition. | F18 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Separation of high risk areas | 1. Fire pump room is not fire separated from the rest of the building. 2. Electrical room is not separated from lab area at ETP Plant. 3. Boiler area is not fire separated from exit discharge route of Building 1. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). Locations of fire rated walls and doors to protect these rooms. Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Separation of high risk areas | 1. Fire pump room is not fire separated from the rest of the building. 2. Electrical room is not separated from lab area at ETP Plant. 3. Boiler area is not fire separated from exit discharge route of Building 1. | Provide 2 hour fire rated construction including 90 minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F20 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Separation of shafts | 1. Lift shafts are not separated from storage with fire rated construction in Building 1. 2. Lift shafts are not separated from greige fabric storage in Building 2(ground floor). 3. Lift shaft is not separated from chemical store in Building 3 (1st floor). | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Separation of shafts | 1. Lift shafts are not separated from storage with fire rated construction in Building 1. 2. Lift shafts are not separated from greige fabric storage in Building 2(ground floor). 3. Lift shaft is not separated from chemical store in Building 3 (1st floor). | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F22 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Separation of occupancies | Large office area is not fire separated from wet processing area Building 1 (ground floor). | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of occupancies | Large office area is not fire separated from wet processing area Building 1 (ground floor). | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F24 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Floor openings | Vertical openings connecting different levels at storage & cutting area-Building 2 (2nd floor). | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Floor openings | Vertical openings connecting different levels at storage & cutting area-Building 2 (2nd floor). | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F26 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Rated Construction | Storage | Storage areas are not fire separated from stitching & finishing area at Building-1 (2nd floor). - Storage areas are not fire separated from stitching & finishing area at Building-2 (1st floor). - Greigh fabric store not separated from knitting area at Building-2 (ground floor). - Storage in exit stairs and/or stair discharge routes. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Rated Construction | Storage | 1. Storage areas are not fire separated from stitching & finishing area at Building-1 (2nd floor). 2. Storage areas are not fire separated from stitching & finishing area at Building-2 (1st floor). 3. Greigh fabric store not separated from knitting area at Building-2 (ground floor). 4. Storage in exit stairs and/or stair discharge routes. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F28 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Suppression | Standpipe system | Non-compliant standpipe outlets installed in Building 1 & Building 2, while it requires having more than 2 occupied floors & area greater than 2325 m2. | (1) Submit design documentation for a standpipe system, along with supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Suppression | Standpipe system | Non-compliant standpipe outlets installed in Building 1 & Building 2, while it requires having more than 2 occupied floors & area greater than 2325 m2. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F30+ 1 month | 2025-12-20 | 2026-01-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Standpipe system | Non-compliant standpipe outlets installed in Building 1 & Building 2, while it requires having more than 2 occupied floors & area greater than 2325 m2. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F31 + 3 months | 2026-01-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Suppression | Standpipe system | Non-compliant standpipe outlets installed in Building 1 & Building 2, while it requires having more than 2 occupied floors & area greater than 2325 m2. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F32 + 3 months | 2026-04-20 | 2026-07-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Suppression | Standpipe system | Non-compliant standpipe outlets installed in Building 1 & Building 2, while it requires having more than 2 occupied floors & area greater than 2325 m2. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | F33 + 3 months | 2026-07-20 | 2026-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Suppression | Standpipe system | Non-compliant standpipe outlets installed in Building 1 & Building 2, while it requires having more than 2 occupied floors & area greater than 2325 m2. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete. | F34 + 4 months | 2026-10-20 | 2027-02-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Suppression | Fire pumps | Fire pump set is not listed - Fire pumps are not in a fire separated room - Fire pumps installed with negative suction arrangement | Provide electric duty pump, diesel backup fire pumps and jockey pumps, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system. | 18 months | 2025-08-20 | 2027-02-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Suppression | Water supply | No separate fire water tank - No dedicated portion of shared water tank for fire safety purposes - Fire tank is not fire separated from the rest of the building. | Implement the plan agreed with Pakistan Accord. | 18 months | 2025-08-20 | 2027-02-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire extinguishers. Inadequate records of maintenance of Standpipe system. Inadequate records of maintenance of fire pump system. Inadequate records of maintenance of Fire Doors. | Prepare a schedule of proposed system maintenance. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire extinguishers. Inadequate records of maintenance of Standpipe system. Inadequate records of maintenance of fire pump system. Inadequate records of maintenance of Fire Doors. | Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. | F38 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire extinguishers. Inadequate records of testing of Standpipe system. Inadequate records of testing of fire pump system. Inadequate records of testing of Fire Doors. | Prepare a schedule of proposed system testing. Identify how systems will be tested and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire extinguishers. Inadequate records of testing of Standpipe system. Inadequate records of testing of fire pump system. Inadequate records of testing of Fire Doors. | Ensure all systems are being tested as per the schedule agreed with Accord. Keep testing records. | F40 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-08-20 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F42 + 2 months | 2025-10-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | F44 | Hazardous Materials | Diesel Storage | No bunding below diesel storage. | Prepare drawings showing diesel storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of diesel storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. - Bunding details. | 4 months | 2025-08-20 | 2025-12-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | F45 | Hazardous Materials | Diesel Storage | No bunding below diesel storage. | Implement the above plan on site. All diesel storage areas to be compliant with Pakistan Accord Standard. | F44+ 4 month | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
2024-10-01
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Al-Hadi Textile (Pvt.) Ltd. - Rohi Nala 3.5 Km Off: 22-Km Ferozepur Road, Lahore, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 01-Oct-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-06-25 | 2025-08-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | Areas highlighted not to be used for storage on 1st, 2nd floor and under vertical extension on roof of the building beyond 200 kg/sq. meter and submit the pictorial evidence to Pakistan Accord. | 1 month | 2025-08-20 | 2025-09-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Un-managed storage observed on the 1st and 2nd floor level of the Building 1. | Verify in-situ concrete stresses either by 100mm dia. cores or existing cylinder strength data for the identified columns or 100mm dia. cores from 4 columns and submit to Pakistan Accord for review. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | Factory Engineer to review design, loads and columns stresses in area identified and submit the report to Pakistan Accord. | S2+ 3 months | 2025-09-20 | 2025-12-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building ( buildings 1 and 2), in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 2 month | 2025-06-25 | 2025-08-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | S4+3 months | 2025-12-20 | 2026-03-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | S5+4 months | 2025-08-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | (4) Submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review | S6+4 months | 2026-03-20 | 2026-07-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord | S7+ 6 months | 2025-12-25 | 2026-06-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete | S8+ 1 month | 2026-07-20 | 2026-08-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | 6 months | 2025-08-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 1 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 1st and 2nd floor level of the Building 1. | Continue to implement load plan. | S10 + 1 month | 2026-08-20 | 2026-09-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 2 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 2nd floor level of the Building 2. | Verify in-situ concrete stresses either by 100mm dia. cores or existing cylinder strength data for the identified columns or 100mm dia. cores from 4 columns and submit to Pakistan Accord for review. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 2 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 2nd floor level of the Building 2. | Factory Engineer to review design, loads and columns stresses in area identified above. | S12+3 months | 2026-09-20 | 2026-12-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Potential Overstress | Highly stressed columns | Based on an initial assessment considering the observed loads, the internal RC columns of the Building 2 at the ground floor level appear to be highly stressed for the observed load and larger span area. Unmanaged storage observed on the 2nd floor level of the Building 2. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S13+3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Structural Documentation | Differs from as-built structure | This relates to the Buildings 1 and 2, where the provided approved site layouts does not match with the as-built structure at a few instances Building 1: - Section drawings does not represent any extension on roof. Building 2: - Section drawings does not represent any extension on roof. - No vertical extension at roof mentioned in site layout. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built architectural documentation. | 6 months | 2025-08-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Structural Documentation | Documentation unavailable | This relates to the Building 1, 2 and 3. Building 1: - No structural drawings were available. - Vertical extensions are observed with steel structure on roof of building has no documentation. Building 2: - No structural drawings were available. Building 3: - No structural drawings were available. - Vertical extensions observed at roof with steel structure has no documentation. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built structural documentation for all buildings. This should include any extensions / steel sheds. | 6 months | 2025-08-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Structural Documentation | Lack of safe load plans | Loading plans were not available, however the information about the maximum loading capacity of the floor was also not marked on the production floors. | Building structural engineer to review design documentation to produce safe load plans according to the loading capacity of the structure for all buildings. | 6 months | 2025-08-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Structural Documentation | Lack of safe load plans | Loading plans were not available, however the information about the maximum loading capacity of the floor was also not marked on the production floors. | Factory to post safe load plans on each floor. | S18+1 month | 2026-02-20 | 2026-03-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Structural System | Connection details | This relates to the Building 1 roof’s vertically extended asbestos shed, where the connection of vertical steel piped for the shed’s steel frame observed to be welded with the rebar of column which appear to be improper connection. | Building structural engineer to review the as-built design for code compliance and confirm if the connection details is adequate. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Structural System | Connection details | This relates to the Building 1 roof’s vertically extended asbestos shed, where the connection of vertical steel piped for the shed’s steel frame observed to be welded with the rebar of column which appear to be improper connection. | Propose a remedial action plan if the connection details need to be modified and share with Pakistan Accord for review | S20 + 1 month | 2025-11-20 | 2025-12-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Structural System | Connection details | This relates to the Building 1 roof’s vertically extended asbestos shed, where the connection of vertical steel piped for the shed’s steel frame observed to be welded with the rebar of column which appear to be improper connection. | Implement the reviewed remedial actions. | S21+3 months | 2025-12-20 | 2026-03-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Structural System | Lateral stability system | This relates to the Building 1, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Structural System | Lateral stability system | This relates to the Building 1, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Structural System | Lateral stability system | This relates to the Building 1, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Propose strengthening works as required. | S24 + 1 month | 2025-11-20 | 2025-12-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S26 | Structural System | Lateral stability system | This relates to the Building 1, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Carry out remedial works as required. | S25 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S27 | Structural System | Lateral stability system | This relates to the Building 2, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S28 | Structural System | Lateral stability system | This relates to the Building 2, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S29 | Structural System | Lateral stability system | This relates to the Building 2, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Propose strengthening works as required. | S28 + 1 month | 2025-11-20 | 2025-12-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S30 | Structural System | Lateral stability system | This relates to the Building 2, where there is no apparent lateral stability system observed in the direction perpendicular to the RC beams. | Carry out remedial works as required. | S29 + 4 months | 2025-12-20 | 2026-04-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S31 | Other Damage/Defects | Excessive deflection or vibration | In Building 2, signs of deflection have been observed along with minor cracks in ledge beam supporting Double Tee members on all the floors (in one bay), which appear to be due to the longer span length(12.4m rest of bays were 7.9m). Furthermore, in few areas broken flanges of Double Tee also observed along with Double Tee cram section crushing the primary beam as well which appear to be due to openings made for services and for moisture ingress and inadequate beam sizes. | Verify in-situ concrete strengths by 100mm dia. cores from 4 beams and submit to Pakistan Accord. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S32 | Other Damage/Defects | Excessive deflection or vibration | In Building 2, signs of deflection have been observed along with minor cracks in ledge beam supporting Double Tee members on all the floors (in one bay), which appear to be due to the longer span length(12.4m rest of bays were 7.9m). Furthermore, in few areas broken flanges of Double Tee also observed along with Double Tee cram section crushing the primary beam as well which appear to be due to openings made for services and for moisture ingress and inadequate beam sizes. | Building engineer to review design of the 2nd floor accounting for low concrete strengths. | S31 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S33 | Other Damage/Defects | Excessive deflection or vibration | In Building 2, signs of deflection have been observed along with minor cracks in ledge beam supporting Double Tee members on all the floors (in one bay), which appear to be due to the longer span length(12.4m rest of bays were 7.9m). Furthermore, in few areas broken flanges of Double Tee also observed along with Double Tee cram section crushing the primary beam as well which appear to be due to openings made for services and for moisture ingress and inadequate beam sizes. | Permanent strengthening and repair works to be proposed. | S32 + 2 months | 2026-02-20 | 2026-04-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S34 | Other Damage/Defects | Excessive deflection or vibration | In Building 2, signs of deflection have been observed along with minor cracks in ledge beam supporting Double Tee members on all the floors (in one bay), which appear to be due to the longer span length(12.4m rest of bays were 7.9m). Furthermore, in few areas broken flanges of Double Tee also observed along with Double Tee cram section crushing the primary beam as well which appear to be due to openings made for services and for moisture ingress and inadequate beam sizes. | Submit proposals of remedial works to the Pakistan Accord for review. | S33 + 1 month | 2026-04-20 | 2026-05-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S35 | Other Damage/Defects | Excessive deflection or vibration | In Building 2, signs of deflection have been observed along with minor cracks in ledge beam supporting Double Tee members on all the floors (in one bay), which appear to be due to the longer span length(12.4m rest of bays were 7.9m). Furthermore, in few areas broken flanges of Double Tee also observed along with Double Tee cram section crushing the primary beam as well which appear to be due to openings made for services and for moisture ingress and inadequate beam sizes. | Install strengthening works. | S34 +3 months | 2026-05-20 | 2026-08-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S36 | Other Damage/Defects | Moisture ingress | In Building 1, signs of cracks have been observed along with dampness in beams and slab at all floors, which appear to be due to the water ingress over period resulting in concrete to spall after cracking along with the signs of dampness. | Building engineer to inspect the locations (in all the buildings) of water ingress and possible reason of cracks and dampness and propose the remedial solution to repair the structure distress caused by ingress of water. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S37 | Other Damage/Defects | Moisture ingress | In Building 1, signs of cracks have been observed along with dampness in beams and slab at all floors, which appear to be due to the water ingress over period resulting in concrete to spall after cracking along with the signs of dampness. | Provide suitable protection on roof for ingress of water to prevent damage to structure from potential ingress. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S38 | Other Damage/Defects | Moisture ingress | In Building 1, signs of cracks have been observed along with dampness in beams and slab at all floors, which appear to be due to the water ingress over period resulting in concrete to spall after cracking along with the signs of dampness. | Implement the remedial works. | S36 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S39 | Other Damage/Defects | Corrosion of reinforcement | This relates the exposed rebars at roof of Building 1, which pose a high risk of corrosion because of rebar being exposed to weather. | Building Engineer to inspect areas with protect the exposed rebars from the weather and to propose the remedial solution to further stop reduce the effect of corrosion. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S40 | Other Damage/Defects | Corrosion of reinforcement | This relates the exposed rebars at roof of Building 1, which pose a high risk of corrosion because of rebar being exposed to weather. | Implement the remedial works. | S39 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S41 | Other Damage/Defects | Column impact damage | This relates to all the floors of Building 1, where impact damages observed in column which appear to be due to hit by trolleys which pose a risk of reduction in column strength. These columns did not have any plaster or any other protection. | Building Engineer to inspect areas with damaged column and to propose the remedial solution to further prevention of damages in future. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S42 | Other Damage/Defects | Column impact damage | This relates to all the floors of Building 1, where impact damages observed in column which appear to be due to hit by trolleys which pose a risk of reduction in column strength. These columns did not have any plaster or any other protection. | Implement the remedial works. | S41 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S43 | Other Damage/Defects | Column impact damage | This relates to all the floors of Building 2, where impact damages observed in column which appear to be due to hit by trolleys which pose a risk of reduction in column strength. These columns did not have any plaster or any other protection. | Building Engineer to inspect areas with damaged column and to propose the remedial solution to further prevention of damages in future. | 3 months | 2025-08-20 | 2025-11-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S44 | Other Damage/Defects | Column impact damage | This relates to all the floors of Building 2, where impact damages observed in column which appear to be due to hit by trolleys which pose a risk of reduction in column strength. These columns did not have any plaster or any other protection. | Implement the remedial works. | S43 + 3 months | 2025-11-20 | 2026-02-20 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1