## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
26-Feb-2025
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Bismillah Textiles Ltd. - 1 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 26-Feb-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-05 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2+6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were provided but missing with necessary details. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Update the existing electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022) Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were provided but missing with necessary details. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4+6 months | 2026-03-30 | 2026-09-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 months | 2025-09-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6+6 months | 2026-05-30 | 2026-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | Obsolete oil-type circuit breaker in the HT panel poses safety risks, reduced reliability, and maintenance challenges due to aging components and outdated technology. | Replace the obsolete oil-type circuit breaker with a modern vacuum or SF6 circuit breaker to ensure safety, reliability, and maintainability. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Circuit breakers | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. This issue was specifically observed at classic building 1st floor, trends LT Room and warehouse Building 6. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable ampacity after applying derating factors. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | During the inspection, Thermographic surveys were conducted on the electrical boards. The survey identified numerous hot spots within panels and distribution boards in location such as Stenter 4 and 5 circuit breaker in processing, boiler contactor and ETP control panel. | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | It was also found that the Thermographic report was not available at the site. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | The earth pits were inaccessible and unsuitably located at energy building. | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. This issue was specifically observed at energy building and trend building 1st floor. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. This issue was specifically observed at energy building and trend building 1st floor. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | It was noted that the earth bar was incorrectly connected to the neutral bar, indicating improper grounding practices. This issue was specifically observed at head office and processing building. | Disconnect the earth bars from the neutral bars with the distribution boards and ensure proper separation and connection. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | Equipotential bonding for the cable trays and metallic panel covers was missing. This issue was observed at batch rotating machine and energy building panels. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | Polythene sheet over live transformer contacts, found in Building 8, poses a fire and electrical hazard due to its flammability and potential for insulation failure. | Remove the polythene sheet from live transformer contacts to eliminate fire and electrical hazards and ensure proper insulation. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed at Head Office Building. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. This issue was specifically observed at Admin Building. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | There were visible signs of damage to panels . This issue was specifically observed at ETP Control Room. | Inspect and repair or replace all damaged panels, cables, and busbars to ensure the integrity of the electrical system in accordance with Section 522 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed at Head Office Building. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E20 + 6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Loop Connection | During the inspection loop connections were identified within the electrical panels specifically at Building 3 processing LT panel. In these loop connections, one circuit breaker is energised by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 3 Months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Multiple connections | During our inspection, multilooping was observed in a number of electrical panels across the facility. This issue was specifically observed at trends building, head office processing and finishing areas in Building 2, Building 3 and Building 5. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Openings | During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements. Unsealed openings were discovered in the panels and distribution boards at Buildings 2, 5 and 6. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Adequate Accessibility | At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. This issue was specifically observed at Building 3 (processing) and Building 9 (ETP). | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at trends building 1st floor, Canteen Building and RO Building. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at trends building 1st floor, Canteen Building and RO Building. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | There were four fire alarm panels installed in the facility. However, the fire alarm system has major issues, including non-compliant panels, cables, and hooters, inadequate visual and sound coverage, and non-fire rated cable. Additionally, no documentation or certification was available in the facility to verify product listings. | (1) Submit design documentation for new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E30 + 1 month | 2025-12-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E31 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E32 +5 months | 2026-05-30 | 2026-10-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E33 +3 months | 2026-10-30 | 2027-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E34 + 3 months | 2027-01-30 | 2027-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | General & Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations such as at Building 3 and Building 8. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | General & Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations such as at Building 3 and Building 8. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | General & Emergency Lighting | Provided but insufficient | Several areas lack sufficient emergency lighting coverage such as Building 2 (admin) and Building 3 (processing). | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 6 Months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | General & Emergency Lighting | Provided but insufficient | Multiple emergency luminaires indicate the need for maintenance such as at Building 9 canteen. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | 2 Months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | General & Emergency Lighting | Independent power source | Installed emergency lights are too dim to provide adequate illumination in Building 5. | Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | General & Emergency Lighting | Independent power source | The backup power supply to the emergency luminaires is insufficient. | Upgrade the backup power supply to ensure it can adequately support all emergency luminaires during a power failure. This includes installing additional battery packs or generators as necessary to comply with the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | General & Emergency Lighting | Ventilation and illumination | An assessment of the existing ventilation system was conducted, alongside an evaluation of the lighting setup in various parts of the room, to determine their compliance with recommended standards. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer area. | Redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the generator and transformer receive adequate ventilation. This might involve repositioning vents or adding ductwork. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | General & Emergency Lighting | Ventilation and illumination | An assessment of the existing ventilation system was conducted, alongside an evaluation of the lighting setup in various parts of the room, to determine their compliance with recommended standards. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer area. | Establish regular maintenance and testing of the ventilation system and luminaires within the spaces to ensure adequate performance. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Generator, Transformer & Sub-Station Room | Working clearance | During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. | Reorganise the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | Generator, Transformer & Sub-Station Room | Working clearance | During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. | Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Generator, Transformer & Sub-Station Room | Breathing system | During the inspection of the transformer's breathing system, an assessment was conducted on its components, including the conservator tank, breather, and associated valves and piping. The condition of the silica gel or other desiccants within the breather was examined to ensure proper functionality. | Replace the silica gel in the breather and repair any leaks around the breather housing to prevent moisture ingress into the transformer insulation oil. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Generator, Transformer & Sub-Station Room | Breathing system | During the inspection of the transformer's breathing system, an assessment was conducted on its components, including the conservator tank, breather, and associated valves and piping. The condition of the silica gel or other desiccants within the breather was examined to ensure proper functionality. | Implement a regular maintenance schedule to periodically inspect and service the breathing system components, ensuring the silica gel is replaced as needed and that all seals and connections are intact to maintain system integrity. | E46 + 6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Generator, Transformer & Sub-Station Room | Room separation | During the inspection of the generator, transformer, and substation rooms, the physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. This was observed at HT and transformer room in the Energy Building. | Install temporary fire-resistant barriers and seal any gaps and openings between the generator, transformer, and substation areas to immediately reduce the risk of fire and electrical fault propagation. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Generator, Transformer & Sub-Station Room | Room separation | During the inspection of the generator, transformer, and substation rooms, the physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. This was observed at HT and transformer room in the Energy Building. | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Generator, Transformer & Sub-Station Room | Battery | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Generator, Transformer & Sub-Station Room | Battery | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Generator, Transformer & Sub-Station Room | Battery | The placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. | Reposition batteries that are improperly placed to ensure they comply with safety regulations, allowing for safe access and adequate ventilation. Mark and clear pathways around battery installations to ensure easy and safe access for maintenance and emergencies. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Generator, Transformer & Sub-Station Room | Battery | The placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. | Conduct regular audits of battery placements to ensure ongoing compliance with safety standards and regulations. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Cabling & Wiring | Cable support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Cabling & Wiring | Cable support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at trends building, engraving area near ETP and Energy Building. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at Trends Building, engraving area near ETP and Energy Building. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was observed at trends Building 2nd floor. | install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was observed at trends Building 2nd floor. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 370 | 421 | 6 | 5 |  | Initial | [11 empty] | E60 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed at ETP area, storage area, Classic Building and behind the engraving processing area. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 371 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed at ETP area, storage area, Classic Building and behind the engraving processing area. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E62 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was specifically observed at classic building ground floor and rolling area processing Building 3. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E63 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was specifically observed at classic building ground floor and rolling area processing Building 3. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 374 | 421 | 6 | 5 |  | Initial | [11 empty] | E64 | Cabling & Wiring | Fixtures | Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was specifically observed at maintenance workshop, energy building, classic building and old processing production area. | Replace combustible wooden ply backings with non-combustible materials to reduce fire risk. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 375 | 421 | 6 | 5 |  | Initial | [11 empty] | E65 | Cabling & Wiring | Fixtures | Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was specifically observed at maintenance workshop, energy building, classic building and old processing production area. | Establish a facility-wide standard to use only non-combustible materials for mounting electrical components, and conduct regular audits for compliance. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 376 | 421 | 6 | 5
| 3 | 8 |  | 377 | 421 | 6 | 5
| 3 | 8 |  | 378 | 421 | 6 | 5
| 3 | 8 |  | 379 | 421 | 6 | 5
| 3 | 8 |  | 380 | 421 | 6 | 5
| 3 | 8 |  | 381 | 421 | 6 | 5
| 3 | 8 |  | 382 | 421 | 6 | 5
| 3 | 8 |  | 383 | 421 | 6 | 5
| 3 | 8 |  | 384 | 421 | 6 | 5
| 3 | 8 |  | 385 | 421 | 6 | 5
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
26-Feb-2025
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Bismillah Textiles Ltd. - 1 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 26-Feb-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-05 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | 1. Escape doors are lockable throughout the factory. 2. Doors serving areas with over 50 occupants swing against the direction of escape i.e. in the Mosque. 3. Sliding doors serve for escape from areas with more than 10 occupants, i.e. Building 3, Building 9. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | 1. Escape doors are lockable throughout the factory. 2. Doors serving areas with over 50 occupants swing against the direction of escape i.e. in the Mosque. 3. Sliding doors serve for escape from areas with more than 10 occupants, i.e. Building 3, Building 9. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | 1. Escape doors are lockable throughout the factory. 2. Doors serving areas with over 50 occupants swing against the direction of escape i.e. in the Mosque. 3. Sliding doors serve for escape from areas with more than 10 occupants, i.e. Building 3, Building 9. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | - Escape passing through increased risk area on way to exit i.e. evacuation into another building from Building 3 into Building 9, passing through an area with possible hazardous fumes in Building 4. - Obstructions on escape route i.e. clutter in the path of escape throughout the factory - Trip hazards on escape route throughout the factory. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) in S-18 Building 10. - Protected stair discharges inside the building at a distance from building exit i.e. S-17 in Building 10, S-2 and S-3 in Building 2 and S15 in Building 9. - Obstruction of means of escape i.e. Level 1 S-8 Building 4. | Remove obstructions on escape routes and keep them clear for escape. Cover any holes and uneven areas in escape routes. Provide warning signs where headroom height is less than 2.05 m on escape routes. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | - Escape passing through increased risk area on way to exit i.e. evacuation into another building from Building 3 into Building 9, passing through an area with possible hazardous fumes in Building 4. - Obstructions on escape route i.e. clutter in the path of escape throughout the factory - Trip hazards on escape route throughout the factory. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) in S-18 Building 10. - Protected stair discharges inside the building at a distance from building exit i.e. S-17 in Building 10, S-2 and S-3 in Building 2 and S15 in Building 9. - Obstruction of means of escape i.e. Level 1 S-8 Building 4. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) - Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Exit access | - Escape passing through increased risk area on way to exit i.e. evacuation into another building from Building 3 into Building 9, passing through an area with possible hazardous fumes in Building 4. - Obstructions on escape route i.e. clutter in the path of escape throughout the factory - Trip hazards on escape route throughout the factory. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) in S-18 Building 10. - Protected stair discharges inside the building at a distance from building exit i.e. S-17 in Building 10, S-2 and S-3 in Building 2 and S15 in Building 9. - Obstruction of means of escape i.e. Level 1 S-8 Building 4. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. - Implement measures to ensure adequate clear head height is achieved along all escape routes. | F6+ 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Travel distance | - Common path of travel distances exceed permitted limits i.e. Level 2 and 3 of Building 5 (25m), Ground floor storage area in Building 9 (50m) and Level 1 of Building 9 (33m). - Travel distance to the nearest of alternative exits exceeds distance limits i.e. Ground floor storage area in Building 9 (115m) and machine area in Building 3 (74m). | Any area over 46m common path of travel needs to be vacated or the egress routes need to be rearranged. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Travel distance | - Common path of travel distances exceed permitted limits i.e. Level 2 and 3 of Building 5 (25m), Ground floor storage area in Building 9 (50m) and Level 1 of Building 9 (33m). - Travel distance to the nearest of alternative exits exceeds distance limits i.e. Ground floor storage area in Building 9 (115m) and machine area in Building 3 (74m). | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Travel distance | - Common path of travel distances exceed permitted limits i.e. Level 2 and 3 of Building 5 (25m), Ground floor storage area in Building 9 (50m) and Level 1 of Building 9 (33m). - Travel distance to the nearest of alternative exits exceeds distance limits i.e. Ground floor storage area in Building 9 (115m) and machine area in Building 3 (74m). | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | F9 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Number of exits | - Single exit from some of the occupied floors i.e. the roof levels that are provided with solar panels Building 5 and Building 2, the Mosque and Level 1 of Building 2. | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Number of exits | - Single exit from some of the occupied floors i.e. the roof levels that are provided with solar panels Building 5 and Building 2, the Mosque and Level 1 of Building 2. | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Standard. | F11 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Protection of stairs | - Unprotected openings into stairs i.e. Building 5. - Unprotected penetrations into stairs i.e. Building 4. - Fire doors propped open throughout the factory. - Doors not fire doors throughout the factory. - Door self-closers are missing throughout the factory. - Fire load in stairs i.e. S-9 Building 5 and S-14 Building 7. - Storage in exit stairs and/or stair discharge routes i.e. Building 5 in S-9. | Remove fire load and any other obstructions due to stored items from stairs. Remove devices that leave the doors propped open. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Protection of stairs | - Unprotected openings into stairs i.e. Building 5. - Unprotected penetrations into stairs i.e. Building 4. - Fire doors propped open throughout the factory. - Doors not fire doors throughout the factory. - Door self-closers are missing throughout the factory. - Fire load in stairs i.e. S-9 Building 5 and S-14 Building 7. - Storage in exit stairs and/or stair discharge routes i.e. Building 5 in S-9. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Protection of stairs | - Unprotected openings into stairs i.e. Building 5. - Unprotected penetrations into stairs i.e. Building 4. - Fire doors propped open throughout the factory. - Doors not fire doors throughout the factory. - Door self-closers are missing throughout the factory. - Fire load in stairs i.e. S-9 Building 5 and S-14 Building 7. - Storage in exit stairs and/or stair discharge routes i.e. Building 5 in S-9. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F14 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Escape stair condition | ,- Stair are not structurally safe i.e. external stair from Level 1 in Building 9. - Stair balustrades are not safe i.e. external stair from Level 1 in Building 9. - Handrails are too low i.e. external stair from Level 1 in Building 9. - Trip hazards in stairs i.e. clutter accumulated in stairs of Building 2. | Remove all obstructions from stairs. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Means of Escape | Escape stair condition | - Stair are not structurally safe i.e. external stair from Level 1 in Building 9. - Stair balustrades are not safe i.e. external stair from Level 1 in Building 9. - Handrails are too low i.e. external stair from Level 1 in Building 9. - Trip hazards in stairs i.e. clutter accumulated in stairs of Building 2. | Remove all trip hazards from stairs. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Means of Escape | Escape stair condition | ,- Stair are not structurally safe i.e. external stair from Level 1 in Building 9. - Stair balustrades are not safe i.e. external stair from Level 1 in Building 9. - Handrails are too low i.e. external stair from Level 1 in Building 9. - Trip hazards in stairs i.e. clutter accumulated in stairs of Building 2. | Ensure the following are provided: - Stair structure to be fixed so that stairs are safe for escape. - Ensure all stairs have balustrades. - Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Means of Escape | Exit discharge | - Stair discharge routes are not fire separated from the rest of the building i.e. Building 5 and Building 4. - External escape routes are through high risk areas i.e. Building 3 and Building 5. - External escape blocked due to gates locked i.e. from Building 8 and Building 9. - Turnstiles/Gate obstructing the path of travel to outside i.e. Building 5 and Building 10. | Remove obstructions and lockable gates on external escape routes and keep them clear for escape. Turnstiles are not appropriate on an escape route and a pass door should be provided. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Means of Escape | Exit discharge | - Stair discharge routes are not fire separated from the rest of the building i.e. Building 5 and Building 4. - External escape routes are through high risk areas i.e. Building 3 and Building 5. - External escape blocked due to gates locked i.e. from Building 8 and Building 9. - Turnstiles/Gate obstructing the path of travel to outside i.e. Building 5 and Building 10. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes. - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes. - Provide additional exits from site. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Means of Escape | Exit discharge | - Stair discharge routes are not fire separated from the rest of the building i.e. Building 5 and Building 4. - External escape routes are through high risk areas i.e. Building 3 and Building 5. - External escape blocked due to gates locked i.e. from Building 8 and Building 9. - Turnstiles/Gate obstructing the path of travel to outside i.e. Building 5 and Building 10. | - Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high risk areas. | F20 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs. - Missing exit signs at stair discharge routes throughout the factory. - Missing exit signs in corridors and circulation areas throughout the factory. - Missing exit signs in production areas throughout the factory. - Missing exit signs in offices and back of house areas. - Missing exit signs at exits from site. - Missing exit signs at roof. - Exit signs are not clear / misleading throughout the factory. - Electrically powered exit signs are not a tested and listed system. - Electrically powered exit signs indicate battery problems. | Remove misleading directional escape signs. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs. - Missing exit signs at stair discharge routes throughout the factory. - Missing exit signs in corridors and circulation areas throughout the factory. - Missing exit signs in production areas throughout the factory. - Missing exit signs in offices and back of house areas. - Missing exit signs at exits from site. - Missing exit signs at roof. - Exit signs are not clear / misleading throughout the factory. - Electrically powered exit signs are not a tested and listed system. - Electrically powered exit signs indicate battery problems. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs. - Missing exit signs at stair discharge routes throughout the factory. - Missing exit signs in corridors and circulation areas throughout the factory. - Missing exit signs in production areas throughout the factory. - Missing exit signs in offices and back of house areas. - Missing exit signs at exits from site. - Missing exit signs at roof. - Exit signs are not clear / misleading throughout the factory. - Electrically powered exit signs are not a tested and listed system. - Electrically powered exit signs indicate battery problems. | Ensure that all exit signage is checked periodically and in good working condition. | F23+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of high-risk areas | - Fire pump room is not fire separated from the rest of the building. - Electrical rooms are not fire separated i.e. Level 2 of Building 5 and Building 9. - Server room not fire separated on L1 of Building 10. - Compressor room not fire separated from the production area on Ground Level of Building 5. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction.) | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Separation of high-risk areas | - Fire pump room is not fire separated from the rest of the building. - Electrical rooms are not fire separated i.e. Level 2 of Building 5 and Building 9. - Server room not fire separated on L1 of Building 10. - Compressor room not fire separated from the production area on Ground Level of Building 5. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F25 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Separation of shafts | - Lift shafts are not separated with fire rated construction i.e. lifts in Building 4, Building 5 and Building 10. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Rated Construction | Separation of shafts | - Lift shafts are not separated with fire rated construction i.e. lifts in Building 4, Building 5 and Building 10. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F27+ 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Rated Construction | Floor openings | - Chutes and/or conveyor belts are not fire separated i.e. Building 10. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Rated Construction | Floor openings | - Chutes and/or conveyor belts are not fire separated i.e. Building 10. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F29 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Rated Construction | Separation of occupancies | - Car park areas are not fire separated from the rest of the building. - Kitchen not fire separated form S-9 in Level 2 of Building 5. - Day care is not on ground floor provided with direct access to street or fire separated from the rest of the building with suitable egress routes, i.e. Level 1 of Building 10. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building. - Proposed fire separation details (including fire rating of walls and doors). - Relocate Day Care to Ground floor with exits directly to outside the building. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Rated Construction | Separation of occupancies | - Car park areas are not fire separated from the rest of the building. - Kitchen not fire separated form S-9 in Level 2 of Building 5. - Day care is not on ground floor provided with direct access to street or fire separated from the rest of the building with suitable egress routes, i.e. Level 1 of Building 10. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F31 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Rated Construction | Separation of occupancies | There was presence of informal sleeping areas. | Remove all informal sleeping areas from all buildings. | 2 weeks | 2025-09-30 | 2025-10-14 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Rated Construction | Separation of occupancies | There was presence of informal sleeping areas. | Document proposals for design of remedial measures to ensure compliance with all fire safety requirements for sleeping occupancies to comply with Pakistan Accord Standard. Submit proposals to Pakistan Accord for review. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Rated Construction | Separation of occupancies | There was presence of informal sleeping areas. | Implement remediation measures to ensure full compliance with dormitory requirements of Pakistan Accord Standard and Pakistan Building Code in accordance with previously reviewed design. | F34 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Rated Construction | Storage | - Storage areas are not fire separated from the rest of the building throughout the factory. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) i.e. Building 4, Building 5 and Building 10. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Rated Construction | Storage | - Storage areas are not fire separated from the rest of the building throughout the factory. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) i.e. Building 4, Building 5 and Building 10. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F36 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Suppression | Standpipe system | - There are no standpipes in the building. | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with, NFPA 14, 20, 22, and 24. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Suppression | Standpipe system | - There are no standpipes in the building. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F38 + 1 month | 2026-01-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Suppression | Standpipe system | - There are no standpipes in the building. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F39 + 3 months | 2026-02-28 | 2026-05-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Fire Suppression | Standpipe system | - There are no standpipes in the building. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F40 + 3 months | 2026-05-28 | 2026-08-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Fire Suppression | Standpipe system | - There are no standpipes in the building. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F41 + 3 months | 2026-08-28 | 2026-11-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Fire Suppression | Standpipe system | - There are no standpipes in the building. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F42 + 4 months = 18 months | 2026-11-28 | Invalid | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | F44 | Fire Suppression | Fire pumps | - Fire pump set is not listed. - There is no diesel pump. - Fire pumps are not in a fire separated room. | Provide electric duty pump, diesel backup fire pumps and jockey pumps, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 18 months | 2025-09-30 | 2027-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | F45 | Fire Suppression | Water supply | - No separate fire water tank. - Unclear source of water for the fire pumps. | Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 18 months | 2025-09-30 | 2027-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | F46 | Fire Suppression | Fire extinguishers | - Poor condition of fire extinguishers i.e. some extinguishers empty with seals missing in Building 5. | Ensure that all building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | F47 | Fire Suppression | Fire extinguishers | - Poor condition of fire extinguishers i.e. some extinguishers empty with seals missing in Building 5. | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | F46 + 2 months | 2025-11-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | F48 | Hazardous Materials | Chemicals handling | - Large amounts of chemicals in production areas i.e. Building 3. - Large amounts of chemicals on egress routes i.e. outside of Building 5. - Presence of exposed asbestos potentially presenting a risk to building occupants i.e. Building 9. | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. Review the risk of asbestos and decide on suitable risk mitigation measures. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | F49 | Hazardous Materials | Chemicals handling | - Large amounts of chemicals in production areas i.e. Building 3. - Large amounts of chemicals on egress routes i.e. outside of Building 5. - Presence of exposed asbestos potentially presenting a risk to building occupants i.e. Building 9. | Implement the chemical handling strategy on site as agreed with Accord. | F48 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | F50 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room i.e. Chemical storage rooms in Building 3. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. | 4 months | 2025-09-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | F51 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room i.e. Chemical storage rooms in Building 3. | Implement the above plan on site. All chemical storage areas to be compliant with Pakistan Accord Standard. | F50 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | F52 | Fire Safety Management | Fire drills | - Fire drill documentation is of poor standard. | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | F53 | Fire Safety Management | Fire drills | - Fire drill documentation is of poor standard. | Ensure fire drills are performed a minimum 2 times per year. | F52+ 2 months | 2025-11-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | F54 | Fire Safety Management | Records of system testing | - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Pumps. - Inadequate records of testing of Emergency lighting. - Inadequate records of testing of Fire Extinguishers. - Inadequate records of testing of Fire Doors. | -Prepare testing schedule for all life safety systems. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | F55 | Fire Safety Management | Records of system testing | - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Pumps. - Inadequate records of testing of Emergency lighting. - Inadequate records of testing of Fire Extinguishers. - Inadequate records of testing of Fire Doors. | -Ensure all systems are being tested as per the schedule agreed with Accord . - Keep testing records. | F54+ 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | F56 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Extinguishers. - Inadequate records of maintenance of Emergency Lighting. - Inadequate records of maintenance of Fire Pumps. - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Doors. | - Set up a maintenance schedule for all life safety systems. - Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. -The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | F57 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Extinguishers. - Inadequate records of maintenance of Emergency Lighting. - Inadequate records of maintenance of Fire Pumps. - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Doors. | - Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. | F56 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | F58 | Fire Safety Management | Emergency Action Plan | - Evacuation diagrams are missing on some levels and final exits. - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-09-30 | 2025-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | F59 | Fire Safety Management | Emergency Action Plan | - Evacuation diagrams are missing on some levels and final exits. - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F58 + 2 months | 2025-11-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
2025-02-26
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Bismillah Textiles Ltd. - 1 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2025-02-26
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-05 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns or existing cylinder strength data and submit results to Pakistan Accord. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Verify insitu reinforcement by removing cover and confirming no. and diameter of bars and submit results to Accord. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Factory Engineer to review design, loads and columns stresses in area identified and submit to Pakistan Accord for review. | S3+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building , in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 8 weeks | 2025-08-05 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | S5+3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths along with safe load plans reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan. | S6+4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (4) Submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review. | S7+4 months | 2026-04-30 | 2026-08-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord. | S8+6 months | 2026-08-30 | 2027-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete. | S9+1 month | 2027-02-28 | 2027-03-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Potential Overstress | Highly stressed columns | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Continue to implement load plan. | S10+1 month | 2027-03-28 | 2027-04-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Potential Overstress | Highly stressed columns | The Building 10 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be smaller column size. | Verify insitu concrete stresses either by 100mm dia. cores or existing cylinder strength data for the from 4 columns and submit the results to Pakistan Accord to recheck the column stresses. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Potential Overstress | Highly stressed columns | The Building 10 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be smaller column size. | Factory Engineer to review design, loads and columns stresses in area identified above and submit to Pakistan Accord for review. | S12+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Potential Overstress | Highly stressed columns | The Building 10 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be smaller column size. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S13+3 months | 2026-03-30 | 2026-06-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Cracking | Column | This observation refers to the ground floor of Building 7, cracking was observed in columns. The potential cause of cracking can be due to moisture present in the atmosphere from wet process activity or corrosion of the reinforcement. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Cracking | Column | This observation refers to the ground floor of Building 7, cracking was observed in columns. The potential cause of cracking can be due to moisture present in the atmosphere from wet process activity or corrosion of the reinforcement. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Cracking | Column | This observation refers to the ground floor of Building 7, cracking was observed in columns. The potential cause of cracking can be due to moisture present in the atmosphere from wet process activity or corrosion of the reinforcement. | Carry out the remedial work. | S16+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Cracking | Column | This observation refers to the workshop area on the ground floor of Building 9, where cracking was observed in columns. The potential cause of cracking can be due to water ingress or corrosion of reinforcement. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Cracking | Column | This observation refers to the workshop area on the ground floor of Building 9, where cracking was observed in columns. The potential cause of cracking can be due to water ingress or corrosion of reinforcement. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Cracking | Column | This observation refers to the workshop area on the ground floor of Building 9, where cracking was observed in columns. The potential cause of cracking can be due to water ingress or corrosion of reinforcement. | Carry out the remedial work. | S19+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Structural System | Lateral stability system | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate and submit to Pakistan Accord for review. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Structural System | Lateral stability system | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Structural System | Lateral stability system | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Propose strengthening works as required and submit to Pakistan Accord for review. | S22 + 1 month | 2025-12-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Structural System | Lateral stability system | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Carry out remedial works as required. | S23 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level of the Building 4 significantly affected from atmospheric corrosion. This may affect the structure’s integrity over the period. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S26 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in column presents at roof level of the Building 4 significantly affected from atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement the approved remedial work. | S25 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S27 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in the column at the roof level of Building 2 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S28 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in the column at the roof level of Building 2 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement the approved remedial work. | S27 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S29 | Other Damage/Defects | Corrosion of reinforcement | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Identify the cause of the damage and propose measures to prevent further water damage. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S30 | Other Damage/Defects | Corrosion of reinforcement | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Inspect damage to the column and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S31 | Other Damage/Defects | Corrosion of reinforcement | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement remedial work. | S30+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S32 | Other Damage/Defects | Corrosion of reinforcement | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Continue to monitor for future damage. | S31+3 months | 2026-03-30 | 2026-06-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S33 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in the column at the roof level of Building 7 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S34 | Other Damage/Defects | Corrosion of reinforcement | The dowel reinforcement in the column at the roof level of Building 7 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement the approved remedial work. | S33 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S35 | Other Damage/Defects | Column impact damage | This observation refers to Building 9 – mechanical workshop, specifically a ground floor column that has sustained damage due to vehicle movement. The impact has resulted in exposed rebar. Furthermore, the factory has plans to demolish the building. | Repair damage to column corners and external faces. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S36 | Other Damage/Defects | Column impact damage | This observation refers to Building 9 – mechanical workshop, specifically a ground floor column that has sustained damage due to vehicle movement. The impact has resulted in exposed rebar. Furthermore, the factory has plans to demolish the building. | Install protective measures to prevent recurring damage. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S37 | Other Damage/Defects | Column impact damage | This observation refers to Building 9 – mechanical workshop, specifically a ground floor column that has sustained damage due to vehicle movement. The impact has resulted in exposed rebar. Furthermore, the factory has plans to demolish the building. | Continue to monitor condition of columns in highly trafficked areas. | S36 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S38 | Other Damage/Defects | Column impact damage | This observation refers to Building 10, second floor column, where we observed that the column was damaged due to the movement of vehicles. | Repair damage to column corners and external faces. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S39 | Other Damage/Defects | Column impact damage | This observation refers to Building 10, second floor column, where we observed that the column was damaged due to the movement of vehicles. | Install protective measures to prevent recurring damage. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S40 | Other Damage/Defects | Column impact damage | This observation refers to Building 10, second floor column, where we observed that the column was damaged due to the movement of vehicles. | Continue to monitor condition of columns in highly trafficked areas. | S39 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S41 | Other Damage/Defects | Moisture ingress | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Identify the source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S42 | Other Damage/Defects | Moisture ingress | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Inspect damage to the column and wall and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S43 | Other Damage/Defects | Moisture ingress | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Implement works as required and in accordance with documentation reviewed by Pakistan Accord. | S42+3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S44 | Other Damage/Defects | Moisture ingress | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Continue to monitor for future signs of water ingress/damage. | S43+3 months | 2026-03-30 | 2026-06-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S45 | Other Damage/Defects | Health and Safety | This concerns inadequate edge protection in Building 4 on roof where solar panels have been installed but no edge protection. This creates a risk of injury resulting from trip or fall. | Provide adequate edge protection on roof. Ensure similar measures are implemented in any other factory areas where these safety concerns exist. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S46 | Other Damage/Defects | Health and Safety | This concerns inadequate edge protection in Building 7 on the roof, where the roof is accessible and edge protection is not provided. This creates a risk of injury resulting from a trip or fall. | Provide adequate edge protection on roof. Ensure similar measures are implemented in any other factory areas where these safety concerns exist. | 1 month | 2025-09-30 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S47 | Structural Documentation | Documentation unavailable | This observation relates to structural drawings and sections of all the buildings and architectural drawings of all the buildings except buildings 4, 5 & 6 that were unavailable. We were presented with as-built architectural plans of buildings 4, 5 and 6. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built drawings. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S48 | Structural Documentation | Non-engineered structure | The structure of the steel fire escape staircase in Building 5 appears undersized. The structure might not be strong enough to bear the load of more people in case of an emergency. The member sizes of structure seem undersized from visual inspection. In case of emergency, quick evacuation of people from the building can result in higher loading on the stairs, which may then overload it and potentially cause serious injuries. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S49 | Structural Documentation | Non-engineered structure | The structure of the steel fire escape staircase in Building 5 appears undersized. The structure might not be strong enough to bear the load of more people in case of an emergency. The member sizes of structure seem undersized from visual inspection. In case of emergency, quick evacuation of people from the building can result in higher loading on the stairs, which may then overload it and potentially cause serious injuries. | Propose strengthening works as required and submit to Pakistan Accord for approval. | S48 + 1 month | 2025-12-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S50 | Structural Documentation | Non-engineered structure | The structure of the steel fire escape staircase in Building 5 appears undersized. The structure might not be strong enough to bear the load of more people in case of an emergency. The member sizes of structure seem undersized from visual inspection. In case of emergency, quick evacuation of people from the building can result in higher loading on the stairs, which may then overload it and potentially cause serious injuries. | Implement strengthening works as required. | S49 + 4 months | 2026-01-30 | 2026-05-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S51 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in Buildings 2, 4, 5, 7 and 10. | Building structural engineer to review design documentation to confirm load capacity of the structure. Develop safe load plans and submit to Pakistan Accord for review. | 6 months | 2025-09-30 | 2026-03-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S52 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in Buildings 2, 4, 5, 7 and 10. | Factory to post safe load plans on each floor. | S51 + 1 month | 2026-03-30 | 2026-04-30 | AGREE |  |  |  | In Progress

## Remediation Schedule
Remediation Schedule
| Bismillah Textiles Ltd. - 1 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan | [8 empty] | Aug 25 | Sep 25 | Oct 25 | Nov 25 | Dec 25 | Jan 26 | Feb 26 | Mar 26 | Apr 26 | May 26 | Jun 26 | Jul 26 | Aug 26 | Sep 26 | Oct 26 | Nov 26 | Dec 26 | Jan 27 | Feb 27 | Mar 27 | Apr 27 | May 27 | Jun 27 | Jul 27 | Aug 27 | Sep 27 | Oct 27 | Nov 27 | Dec 27 | Jan 28 | Feb 28 | Mar 28 | Apr 28 | May 28 | Jun 28 | Jul 28 | Aug 28 | Sep 28 | Oct 28 | Nov 28 | Dec 28 | Jan 29 | Feb 29 | Mar 29 | Apr 29 | May 29 | Jun 29 | Jul 29 | Aug 29 | Sep 29 | Oct 29 | Nov 29 | Dec 29 | Jan 30 | Feb 30 | Mar 30 | Apr 30 | May 30 | Jun 30 | Jul 30 | Aug 30 | Sep 30 | Oct 30 | Nov 30 | Dec 30 | Jan 31 | Feb 31 | Mar 31 | Apr 31 | May 31 | Jun 31 | Jul 31 | Aug 31 | Sep 31 | Oct 31 | Nov 31 | Dec 31 | Jan 32
 | time axis 2025-08-05 to 2032-01-05
Do not delete this row. This row is hidden to preserve a formula that is used to highlight the current day within the project schedule. | time axis 2025-08-05 to 2032-01-05
TIMELINE
ITEM NO | #ERROR! | REMEDIATION PLAN | FACTORY UPDATE | TIMING (MONTHS) | PROGRESS STATUS | REMEDIATION START DATE | REMEDIATION FINISH DATE | DURATION (MONTHS)
S1 |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. |  | 8 weeks | In Progress | 2025-08-05 | 2025-09-30 | 2 | 14 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S2 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns or existing cylinder strength data and submit results to Pakistan Accord. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S3 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Verify insitu reinforcement by removing cover and confirming no. and diameter of bars and submit results to Accord. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S4 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Factory Engineer to review design, loads and columns stresses in area identified and submit to Pakistan Accord for review. |  | S3+3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S5 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building , in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. |  | 8 weeks | In Progress | 2025-08-05 | 2025-09-30 | 2 | 14 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S6 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review |  | S5+3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S7 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths along with safe load plans reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan. |  | S6+4 months | In Progress | 2025-12-30 | 2026-04-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S8 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (4) Submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review. |  | S7+4 months | In Progress | 2026-04-30 | 2026-08-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S9 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord. |  | S8+6 months | In Progress | 2026-08-30 | 2027-02-28 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S10 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete. |  | S9+1 month | In Progress | 2027-02-28 | 2027-03-28 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S11 | The Building 5 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be larger grid sizes (8.39 x 7.32). | Continue to implement load plan. |  | S10+1 month | In Progress | 2027-03-28 | 2027-04-28 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S12 | The Building 10 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be smaller column size. | Verify insitu concrete stresses either by 100mm dia. cores or existing cylinder strength data for the from 4 columns and submit the results to Pakistan Accord to recheck the column stresses. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S13 | The Building 10 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be smaller column size. | Factory Engineer to review design, loads and columns stresses in area identified above and submit to Pakistan Accord for review. |  | S12+3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S14 | The Building 10 columns appear to be overstressed against the observed load at the ground floor level. The potential cause of overstressing can be smaller column size. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. |  | S13+3 months | In Progress | 2026-03-30 | 2026-06-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S15 | This observation refers to the ground floor of Building 7, cracking was observed in columns. The potential cause of cracking can be due to moisture present in the atmosphere from wet process activity or corrosion of the reinforcement. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S16 | This observation refers to the ground floor of Building 7, cracking was observed in columns. The potential cause of cracking can be due to moisture present in the atmosphere from wet process activity or corrosion of the reinforcement. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S17 | This observation refers to the ground floor of Building 7, cracking was observed in columns. The potential cause of cracking can be due to moisture present in the atmosphere from wet process activity or corrosion of the reinforcement. | Carry out the remedial work. |  | S16+3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S18 | This observation refers to the workshop area on the ground floor of Building 9, where cracking was observed in columns. The potential cause of cracking can be due to water ingress or corrosion of reinforcement. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S19 | This observation refers to the workshop area on the ground floor of Building 9, where cracking was observed in columns. The potential cause of cracking can be due to water ingress or corrosion of reinforcement. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S20 | This observation refers to the workshop area on the ground floor of Building 9, where cracking was observed in columns. The potential cause of cracking can be due to water ingress or corrosion of reinforcement. | Carry out the remedial work. |  | S19+3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S21 | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate and submit to Pakistan Accord for review. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S22 | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary and submit to Pakistan Accord for review. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S23 | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Propose strengthening works as required and submit to Pakistan Accord for review. |  | S22 + 1 month | In Progress | 2025-12-30 | 2026-01-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S24 | This issue refers to Building 5, a four-story RC MRF structure. The lateral stability system is active only in one direction across all floors, as there are no beams provided in the perpendicular direction. Additionally, in some bays, the columns are braced in only one direction. This unidirectional lateral resistance may compromise the building's stability under wind or seismic loads acting in the unbraced direction. The absence of beams and bracing in that direction can cause excessive lateral displacement or even structural instability. | Carry out remedial works as required. |  | S23 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S25 | The dowel reinforcement in column presents at roof level of the Building 4 significantly affected from atmospheric corrosion. This may affect the structure’s integrity over the period. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S26 | The dowel reinforcement in column presents at roof level of the Building 4 significantly affected from atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement the approved remedial work. |  | S25 + 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S27 | The dowel reinforcement in the column at the roof level of Building 2 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S28 | The dowel reinforcement in the column at the roof level of Building 2 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement the approved remedial work. |  | S27 + 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S29 | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Identify the cause of the damage and propose measures to prevent further water damage. |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S30 | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Inspect damage to the column and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S31 | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement remedial work. |  | S30+3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S32 | The reinforcement in the column at the roof level of Building 5 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Continue to monitor for future damage. |  | S31+3 months | In Progress | 2026-03-30 | 2026-06-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S33 | The dowel reinforcement in the column at the roof level of Building 7 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S34 | The dowel reinforcement in the column at the roof level of Building 7 was significantly affected by atmospheric corrosion. This may affect the structure’s integrity over the period. | Implement the approved remedial work. |  | S33 + 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S35 | This observation refers to Building 9 – mechanical workshop, specifically a ground floor column that has sustained damage due to vehicle movement. The impact has resulted in exposed rebar. Furthermore, the factory has plans to demolish the building. | Repair damage to column corners and external faces. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S36 | This observation refers to Building 9 – mechanical workshop, specifically a ground floor column that has sustained damage due to vehicle movement. The impact has resulted in exposed rebar. Furthermore, the factory has plans to demolish the building. | Install protective measures to prevent recurring damage. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S37 | This observation refers to Building 9 – mechanical workshop, specifically a ground floor column that has sustained damage due to vehicle movement. The impact has resulted in exposed rebar. Furthermore, the factory has plans to demolish the building. | Continue to monitor condition of columns in highly trafficked areas. |  | S36 + 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S38 | This observation refers to Building 10, second floor column, where we observed that the column was damaged due to the movement of vehicles. | Repair damage to column corners and external faces. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S39 | This observation refers to Building 10, second floor column, where we observed that the column was damaged due to the movement of vehicles. | Install protective measures to prevent recurring damage. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S40 | This observation refers to Building 10, second floor column, where we observed that the column was damaged due to the movement of vehicles. | Continue to monitor condition of columns in highly trafficked areas. |  | S39 + 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S41 | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Identify the source of water ingress and propose measures to prevent further water damage. |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S42 | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Inspect damage to the column and wall and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S43 | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Implement works as required and in accordance with documentation reviewed by Pakistan Accord. |  | S42+3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S44 | This observation refers to Building 7, ground floor columns and wall, where some signs of moisture ingress were observed at the time of inspection, due to water ingress columns have been cracked at the ground floor. Likely due to moisture present in the atmosphere from wet process activity or water accumulation from the overflow of the Boiler’s tank. | Continue to monitor for future signs of water ingress/damage. |  | S43+3 months | In Progress | 2026-03-30 | 2026-06-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S45 | This concerns inadequate edge protection in Building 4 on roof where solar panels have been installed but no edge protection. This creates a risk of injury resulting from trip or fall. | Provide adequate edge protection on roof. Ensure similar measures are implemented in any other factory areas where these safety concerns exist. |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S46 | This concerns inadequate edge protection in Building 7 on the roof, where the roof is accessible and edge protection is not provided. This creates a risk of injury resulting from a trip or fall. | Provide adequate edge protection on roof. Ensure similar measures are implemented in any other factory areas where these safety concerns exist. |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S47 | This observation relates to structural drawings and sections of all the buildings and architectural drawings of all the buildings except buildings 4, 5 & 6 that were unavailable. We were presented with as-built architectural plans of buildings 4, 5 and 6. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built drawings. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S48 | The structure of the steel fire escape staircase in Building 5 appears undersized. The structure might not be strong enough to bear the load of more people in case of an emergency. The member sizes of structure seem undersized from visual inspection. In case of emergency, quick evacuation of people from the building can result in higher loading on the stairs, which may then overload it and potentially cause serious injuries. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S49 | The structure of the steel fire escape staircase in Building 5 appears undersized. The structure might not be strong enough to bear the load of more people in case of an emergency. The member sizes of structure seem undersized from visual inspection. In case of emergency, quick evacuation of people from the building can result in higher loading on the stairs, which may then overload it and potentially cause serious injuries. | Propose strengthening works as required and submit to Pakistan Accord for approval. |  | S48 + 1 month | In Progress | 2025-12-30 | 2026-01-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S50 | The structure of the steel fire escape staircase in Building 5 appears undersized. The structure might not be strong enough to bear the load of more people in case of an emergency. The member sizes of structure seem undersized from visual inspection. In case of emergency, quick evacuation of people from the building can result in higher loading on the stairs, which may then overload it and potentially cause serious injuries. | Implement strengthening works as required. |  | S49 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S51 | No safe load plans were posted in Buildings 2, 4, 5, 7 and 10. | Building structural engineer to review design documentation to confirm load capacity of the structure. Develop safe load plans and submit to Pakistan Accord for review. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
S52 | No safe load plans were posted in Buildings 2, 4, 5, 7 and 10. | Factory to post safe load plans on each floor. |  | S51 + 1 month | In Progress | 2026-03-30 | 2026-04-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F1 |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. |  | 8 weeks | In Progress | 2025-08-05 | 2025-09-30 | 2 | 14 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F2 | 1. Escape doors are lockable throughout the factory. 2. Doors serving areas with over 50 occupants swing against the direction of escape i.e. in the Mosque. 3. Sliding doors serve for escape from areas with more than 10 occupants, i.e. Building 3, Building 9. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F3 | 1. Escape doors are lockable throughout the factory. 2. Doors serving areas with over 50 occupants swing against the direction of escape i.e. in the Mosque. 3. Sliding doors serve for escape from areas with more than 10 occupants, i.e. Building 3, Building 9. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F4 | 1. Escape doors are lockable throughout the factory. 2. Doors serving areas with over 50 occupants swing against the direction of escape i.e. in the Mosque. 3. Sliding doors serve for escape from areas with more than 10 occupants, i.e. Building 3, Building 9. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. |  | F3+ 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F5 | - Escape passing through increased risk area on way to exit i.e. evacuation into another building from Building 3 into Building 9, passing through an area with possible hazardous fumes in Building 4. - Obstructions on escape route i.e. clutter in the path of escape throughout the factory - Trip hazards on escape route throughout the factory. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) in S-18 Building 10. - Protected stair discharges inside the building at a distance from building exit i.e. S-17 in Building 10, S-2 and S-3 in Building 2 and S15 in Building 9. - Obstruction of means of escape i.e. Level 1 S-8 Building 4. | Remove obstructions on escape routes and keep them clear for escape. Cover any holes and uneven areas in escape routes. Provide warning signs where headroom height is less than 2.05 m on escape routes. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F6 | - Escape passing through increased risk area on way to exit i.e. evacuation into another building from Building 3 into Building 9, passing through an area with possible hazardous fumes in Building 4. - Obstructions on escape route i.e. clutter in the path of escape throughout the factory - Trip hazards on escape route throughout the factory. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) in S-18 Building 10. - Protected stair discharges inside the building at a distance from building exit i.e. S-17 in Building 10, S-2 and S-3 in Building 2 and S15 in Building 9. - Obstruction of means of escape i.e. Level 1 S-8 Building 4. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) - Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F7 | - Escape passing through increased risk area on way to exit i.e. evacuation into another building from Building 3 into Building 9, passing through an area with possible hazardous fumes in Building 4. - Obstructions on escape route i.e. clutter in the path of escape throughout the factory - Trip hazards on escape route throughout the factory. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) in S-18 Building 10. - Protected stair discharges inside the building at a distance from building exit i.e. S-17 in Building 10, S-2 and S-3 in Building 2 and S15 in Building 9. - Obstruction of means of escape i.e. Level 1 S-8 Building 4. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. - Implement measures to ensure adequate clear head height is achieved along all escape routes. |  | F6+ 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F8 | - Common path of travel distances exceed permitted limits i.e. Level 2 and 3 of Building 5 (25m), Ground floor storage area in Building 9 (50m) and Level 1 of Building 9 (33m). - Travel distance to the nearest of alternative exits exceeds distance limits i.e. Ground floor storage area in Building 9 (115m) and machine area in Building 3 (74m). | Any area over 46m common path of travel needs to be vacated or the egress routes need to be rearranged. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F9 | - Common path of travel distances exceed permitted limits i.e. Level 2 and 3 of Building 5 (25m), Ground floor storage area in Building 9 (50m) and Level 1 of Building 9 (33m). - Travel distance to the nearest of alternative exits exceeds distance limits i.e. Ground floor storage area in Building 9 (115m) and machine area in Building 3 (74m). | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F10 | - Common path of travel distances exceed permitted limits i.e. Level 2 and 3 of Building 5 (25m), Ground floor storage area in Building 9 (50m) and Level 1 of Building 9 (33m). - Travel distance to the nearest of alternative exits exceeds distance limits i.e. Ground floor storage area in Building 9 (115m) and machine area in Building 3 (74m). | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. |  | F9 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F11 | - Single exit from some of the occupied floors i.e. the roof levels that are provided with solar panels Building 5 and Building 2, the Mosque and Level 1 of Building 2. | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F12 | - Single exit from some of the occupied floors i.e. the roof levels that are provided with solar panels Building 5 and Building 2, the Mosque and Level 1 of Building 2. | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Standard. |  | F11 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F13 | - Unprotected openings into stairs i.e. Building 5. - Unprotected penetrations into stairs i.e. Building 4. - Fire doors propped open throughout the factory. - Doors not fire doors throughout the factory. - Door self-closers are missing throughout the factory. - Fire load in stairs i.e. S-9 Building 5 and S-14 Building 7. - Storage in exit stairs and/or stair discharge routes i.e. Building 5 in S-9. | Remove fire load and any other obstructions due to stored items from stairs. Remove devices that leave the doors propped open. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F14 | - Unprotected openings into stairs i.e. Building 5. - Unprotected penetrations into stairs i.e. Building 4. - Fire doors propped open throughout the factory. - Doors not fire doors throughout the factory. - Door self-closers are missing throughout the factory. - Fire load in stairs i.e. S-9 Building 5 and S-14 Building 7. - Storage in exit stairs and/or stair discharge routes i.e. Building 5 in S-9. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F15 | - Unprotected openings into stairs i.e. Building 5. - Unprotected penetrations into stairs i.e. Building 4. - Fire doors propped open throughout the factory. - Doors not fire doors throughout the factory. - Door self-closers are missing throughout the factory. - Fire load in stairs i.e. S-9 Building 5 and S-14 Building 7. - Storage in exit stairs and/or stair discharge routes i.e. Building 5 in S-9. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. |  | F14 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F16 | ,- Stair are not structurally safe i.e. external stair from Level 1 in Building 9. - Stair balustrades are not safe i.e. external stair from Level 1 in Building 9. - Handrails are too low i.e. external stair from Level 1 in Building 9. - Trip hazards in stairs i.e. clutter accumulated in stairs of Building 2. | Remove all obstructions from stairs. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F17 | - Stair are not structurally safe i.e. external stair from Level 1 in Building 9. - Stair balustrades are not safe i.e. external stair from Level 1 in Building 9. - Handrails are too low i.e. external stair from Level 1 in Building 9. - Trip hazards in stairs i.e. clutter accumulated in stairs of Building 2. | Remove all trip hazards from stairs. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F18 | ,- Stair are not structurally safe i.e. external stair from Level 1 in Building 9. - Stair balustrades are not safe i.e. external stair from Level 1 in Building 9. - Handrails are too low i.e. external stair from Level 1 in Building 9. - Trip hazards in stairs i.e. clutter accumulated in stairs of Building 2. | Ensure the following are provided: - Stair structure to be fixed so that stairs are safe for escape. - Ensure all stairs have balustrades. - Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F19 | - Stair discharge routes are not fire separated from the rest of the building i.e. Building 5 and Building 4. - External escape routes are through high risk areas i.e. Building 3 and Building 5. - External escape blocked due to gates locked i.e. from Building 8 and Building 9. - Turnstiles/Gate obstructing the path of travel to outside i.e. Building 5 and Building 10. | Remove obstructions and lockable gates on external escape routes and keep them clear for escape. Turnstiles are not appropriate on an escape route and a pass door should be provided. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F20 | - Stair discharge routes are not fire separated from the rest of the building i.e. Building 5 and Building 4. - External escape routes are through high risk areas i.e. Building 3 and Building 5. - External escape blocked due to gates locked i.e. from Building 8 and Building 9. - Turnstiles/Gate obstructing the path of travel to outside i.e. Building 5 and Building 10. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes. - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes. - Provide additional exits from site. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F21 | - Stair discharge routes are not fire separated from the rest of the building i.e. Building 5 and Building 4. - External escape routes are through high risk areas i.e. Building 3 and Building 5. - External escape blocked due to gates locked i.e. from Building 8 and Building 9. - Turnstiles/Gate obstructing the path of travel to outside i.e. Building 5 and Building 10. | - Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high risk areas. |  | F20 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F22 | - Missing exit signs at entry into stairs. - Missing exit signs at stair discharge routes throughout the factory. - Missing exit signs in corridors and circulation areas throughout the factory. - Missing exit signs in production areas throughout the factory. - Missing exit signs in offices and back of house areas. - Missing exit signs at exits from site. - Missing exit signs at roof. - Exit signs are not clear / misleading throughout the factory. - Electrically powered exit signs are not a tested and listed system. - Electrically powered exit signs indicate battery problems. | Remove misleading directional escape signs. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F23 | - Missing exit signs at entry into stairs. - Missing exit signs at stair discharge routes throughout the factory. - Missing exit signs in corridors and circulation areas throughout the factory. - Missing exit signs in production areas throughout the factory. - Missing exit signs in offices and back of house areas. - Missing exit signs at exits from site. - Missing exit signs at roof. - Exit signs are not clear / misleading throughout the factory. - Electrically powered exit signs are not a tested and listed system. - Electrically powered exit signs indicate battery problems. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3 |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F24 | - Missing exit signs at entry into stairs. - Missing exit signs at stair discharge routes throughout the factory. - Missing exit signs in corridors and circulation areas throughout the factory. - Missing exit signs in production areas throughout the factory. - Missing exit signs in offices and back of house areas. - Missing exit signs at exits from site. - Missing exit signs at roof. - Exit signs are not clear / misleading throughout the factory. - Electrically powered exit signs are not a tested and listed system. - Electrically powered exit signs indicate battery problems. | Ensure that all exit signage is checked periodically and in good working condition. |  | F23+ 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F25 | - Fire pump room is not fire separated from the rest of the building. - Electrical rooms are not fire separated i.e. Level 2 of Building 5 and Building 9. - Server room not fire separated on L1 of Building 10. - Compressor room not fire separated from the production area on Ground Level of Building 5. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction.) |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F26 | - Fire pump room is not fire separated from the rest of the building. - Electrical rooms are not fire separated i.e. Level 2 of Building 5 and Building 9. - Server room not fire separated on L1 of Building 10. - Compressor room not fire separated from the production area on Ground Level of Building 5. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. |  | F25 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F27 | - Lift shafts are not separated with fire rated construction i.e. lifts in Building 4, Building 5 and Building 10. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F28 | - Lift shafts are not separated with fire rated construction i.e. lifts in Building 4, Building 5 and Building 10. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. |  | F27+ 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F29 | - Chutes and/or conveyor belts are not fire separated i.e. Building 10. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F30 | - Chutes and/or conveyor belts are not fire separated i.e. Building 10. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. |  | F29 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F31 | - Car park areas are not fire separated from the rest of the building. - Kitchen not fire separated form S-9 in Level 2 of Building 5. - Day care is not on ground floor provided with direct access to street or fire separated from the rest of the building with suitable egress routes, i.e. Level 1 of Building 10. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building. - Proposed fire separation details (including fire rating of walls and doors). - Relocate Day Care to Ground floor with exits directly to outside the building. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F32 | - Car park areas are not fire separated from the rest of the building. - Kitchen not fire separated form S-9 in Level 2 of Building 5. - Day care is not on ground floor provided with direct access to street or fire separated from the rest of the building with suitable egress routes, i.e. Level 1 of Building 10. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. |  | F31 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F33 | There was presence of informal sleeping areas. | Remove all informal sleeping areas from all buildings. |  | 2 weeks | In Progress | 2025-09-30 | 2025-10-14 | 0.5 | 3.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F34 | There was presence of informal sleeping areas. | Document proposals for design of remedial measures to ensure compliance with all fire safety requirements for sleeping occupancies to comply with Pakistan Accord Standard. Submit proposals to Pakistan Accord for review. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F35 | There was presence of informal sleeping areas. | Implement remediation measures to ensure full compliance with dormitory requirements of Pakistan Accord Standard and Pakistan Building Code in accordance with previously reviewed design. |  | F34 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F36 | - Storage areas are not fire separated from the rest of the building throughout the factory. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) i.e. Building 4, Building 5 and Building 10. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F37 | - Storage areas are not fire separated from the rest of the building throughout the factory. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) i.e. Building 4, Building 5 and Building 10. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. |  | F36 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F38 | - There are no standpipes in the building. | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with, NFPA 14, 20, 22, and 24. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F39 | - There are no standpipes in the building. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. |  | F38 + 1 month | In Progress | 2026-01-30 | 2026-02-28 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F40 | - There are no standpipes in the building. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. |  | F39 + 3 months | In Progress | 2026-02-28 | 2026-05-28 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F41 | - There are no standpipes in the building. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. |  | F40 + 3 months | In Progress | 2026-05-28 | 2026-08-28 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F42 | - There are no standpipes in the building. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  | F41 + 3 months | In Progress | 2026-08-28 | 2026-11-28 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F43 | - There are no standpipes in the building. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete |  | F42 + 4 months = 18 months | In Progress | 2026-11-28 | Invalid | #VALUE! | #VALUE! | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F44 | - Fire pump set is not listed. - There is no diesel pump. - Fire pumps are not in a fire separated room. | Provide electric duty pump, diesel backup fire pumps and jockey pumps, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. |  | 18 months | In Progress | 2025-09-30 | 2027-03-30 | 19.5 | 136.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F45 | - No separate fire water tank. - Unclear source of water for the fire pumps. | Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. |  | 18 months | In Progress | 2025-09-30 | 2027-03-30 | 19.5 | 136.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F46 | - Poor condition of fire extinguishers i.e. some extinguishers empty with seals missing in Building 5. | Ensure that all building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F47 | - Poor condition of fire extinguishers i.e. some extinguishers empty with seals missing in Building 5. | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. |  | F46 + 2 months | In Progress | 2025-11-30 | 2026-01-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F48 | - Large amounts of chemicals in production areas i.e. Building 3. - Large amounts of chemicals on egress routes i.e. outside of Building 5. - Presence of exposed asbestos potentially presenting a risk to building occupants i.e. Building 9. | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. Review the risk of asbestos and decide on suitable risk mitigation measures. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F49 | - Large amounts of chemicals in production areas i.e. Building 3. - Large amounts of chemicals on egress routes i.e. outside of Building 5. - Presence of exposed asbestos potentially presenting a risk to building occupants i.e. Building 9. | Implement the chemical handling strategy on site as agreed with Accord. |  | F48 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F50 | - Flammable materials are not stored in a fire separated room i.e. Chemical storage rooms in Building 3. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F51 | - Flammable materials are not stored in a fire separated room i.e. Chemical storage rooms in Building 3. | Implement the above plan on site. All chemical storage areas to be compliant with Pakistan Accord Standard. |  | F50 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F52 | - Fire drill documentation is of poor standard. | Conduct a fire drill and make records, including findings and recommended future improvements. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F53 | - Fire drill documentation is of poor standard. | Ensure fire drills are performed a minimum 2 times per year. |  | F52+ 2 months | In Progress | 2025-11-30 | 2026-01-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F54 | - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Pumps. - Inadequate records of testing of Emergency lighting. - Inadequate records of testing of Fire Extinguishers. - Inadequate records of testing of Fire Doors. | -Prepare testing schedule for all life safety systems. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F55 | - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Pumps. - Inadequate records of testing of Emergency lighting. - Inadequate records of testing of Fire Extinguishers. - Inadequate records of testing of Fire Doors. | -Ensure all systems are being tested as per the schedule agreed with Accord . - Keep testing records. |  | F54+ 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F56 | - Inadequate records of maintenance of Extinguishers. - Inadequate records of maintenance of Emergency Lighting. - Inadequate records of maintenance of Fire Pumps. - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Doors. | - Set up a maintenance schedule for all life safety systems. - Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. -The schedule to be submitted to Accord for review and approval. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F57 | - Inadequate records of maintenance of Extinguishers. - Inadequate records of maintenance of Emergency Lighting. - Inadequate records of maintenance of Fire Pumps. - Inadequate records of testing of Fire Detection and Alarm System. - Inadequate records of testing of Fire Doors. | - Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. |  | F56 + 3 months | In Progress | 2025-12-30 | 2026-03-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F58 | - Evacuation diagrams are missing on some levels and final exits. - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
F59 | - Evacuation diagrams are missing on some levels and final exits. - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. |  | F58 + 2 months | In Progress | 2025-11-30 | 2026-01-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E1 |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. |  | 8 weeks | In Progress | 2025-08-05 | 2025-09-30 | 2 | 14 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E2 | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E3 | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. |  | E2+6 months | In Progress | 2025-12-30 | 2026-06-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E4 | It was found that the electrical single line diagrams (SLDs) for the factory were provided but missing with necessary details. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Update the existing electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022) Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E5 | It was found that the electrical single line diagrams (SLDs) for the factory were provided but missing with necessary details. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. |  | E4+6 months | In Progress | 2026-03-30 | 2026-09-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E6 | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. |  | 8 months | In Progress | 2025-09-30 | 2026-05-30 | 8.75 | 61.25 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E7 | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. |  | E6+6 months | In Progress | 2026-05-30 | 2026-11-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E8 | Obsolete oil-type circuit breaker in the HT panel poses safety risks, reduced reliability, and maintenance challenges due to aging components and outdated technology. | Replace the obsolete oil-type circuit breaker with a modern vacuum or SF6 circuit breaker to ensure safety, reliability, and maintainability. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E9 | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. This issue was specifically observed at classic building 1st floor, trends LT Room and warehouse Building 6. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable ampacity after applying derating factors. |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E10 | During the inspection, Thermographic surveys were conducted on the electrical boards. The survey identified numerous hot spots within panels and distribution boards in location such as Stenter 4 and 5 circuit breaker in processing, boiler contactor and ETP control panel. | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E11 | It was also found that the Thermographic report was not available at the site. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E12 | The earth pits were inaccessible and unsuitably located at energy building. | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E13 | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. This issue was specifically observed at energy building and trend building 1st floor. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E14 | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. This issue was specifically observed at energy building and trend building 1st floor. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E15 | It was noted that the earth bar was incorrectly connected to the neutral bar, indicating improper grounding practices. This issue was specifically observed at head office and processing building. | Disconnect the earth bars from the neutral bars with the distribution boards and ensure proper separation and connection. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E16 | Equipotential bonding for the cable trays and metallic panel covers was missing. This issue was observed at batch rotating machine and energy building panels. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E17 | Polythene sheet over live transformer contacts, found in Building 8, poses a fire and electrical hazard due to its flammability and potential for insulation failure. | Remove the polythene sheet from live transformer contacts to eliminate fire and electrical hazards and ensure proper insulation. |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E18 | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed at Head Office Building. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E19 | Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. This issue was specifically observed at Admin Building. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E20 | There were visible signs of damage to panels . This issue was specifically observed at ETP Control Room. | Inspect and repair or replace all damaged panels, cables, and busbars to ensure the integrity of the electrical system in accordance with Section 522 of BS7671 18th Edition + A2 (2022). |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E21 | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed at Head Office Building. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. |  | E20 + 6 months | In Progress | 2025-12-30 | 2026-06-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E22 | During the inspection loop connections were identified within the electrical panels specifically at Building 3 processing LT panel. In these loop connections, one circuit breaker is energised by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. |  | 3 Months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E23 | During our inspection, multilooping was observed in a number of electrical panels across the facility. This issue was specifically observed at trends building, head office processing and finishing areas in Building 2, Building 3 and Building 5. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E24 | During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements. Unsealed openings were discovered in the panels and distribution boards at Buildings 2, 5 and 6. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E25 | At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. This issue was specifically observed at Building 3 (processing) and Building 9 (ETP). | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E26 | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at trends building 1st floor, Canteen Building and RO Building. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). |  | 1 month | In Progress | 2025-09-30 | 2025-10-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E27 | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at trends building 1st floor, Canteen Building and RO Building. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E28 | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E29 | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E30 | There were four fire alarm panels installed in the facility. However, the fire alarm system has major issues, including non-compliant panels, cables, and hooters, inadequate visual and sound coverage, and non-fire rated cable. Additionally, no documentation or certification was available in the facility to verify product listings. | (1) Submit design documentation for new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E31 | Non compliant fire alarm system found installed in the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. |  | E30 + 1 month | In Progress | 2025-12-30 | 2026-01-30 | 1 | 7 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E32 | Non compliant fire alarm system found installed in the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. |  | E31 + 4 months | In Progress | 2026-01-30 | 2026-05-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E33 | Non compliant fire alarm system found installed in the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. |  | E32 +5 months | In Progress | 2026-05-30 | 2026-10-30 | 5.5 | 38.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E34 | Non compliant fire alarm system found installed in the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. |  | E33 +3 months | In Progress | 2026-10-30 | 2027-01-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E35 | Non compliant fire alarm system found installed in the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. |  | E34 + 3 months | In Progress | 2027-01-30 | 2027-04-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E36 | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations such as at Building 3 and Building 8. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E37 | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations such as at Building 3 and Building 8. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E38 | Several areas lack sufficient emergency lighting coverage such as Building 2 (admin) and Building 3 (processing). | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. |  | 6 Months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E39 | Multiple emergency luminaires indicate the need for maintenance such as at Building 9 canteen. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. |  | 2 Months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E40 | Installed emergency lights are too dim to provide adequate illumination in Building 5. | Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E41 | The backup power supply to the emergency luminaires is insufficient. | Upgrade the backup power supply to ensure it can adequately support all emergency luminaires during a power failure. This includes installing additional battery packs or generators as necessary to comply with the Building Code of Pakistan Fire Safety Provisions 2016. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E42 | An assessment of the existing ventilation system was conducted, alongside an evaluation of the lighting setup in various parts of the room, to determine their compliance with recommended standards. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer area. | Redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the generator and transformer receive adequate ventilation. This might involve repositioning vents or adding ductwork. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E43 | An assessment of the existing ventilation system was conducted, alongside an evaluation of the lighting setup in various parts of the room, to determine their compliance with recommended standards. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer area. | Establish regular maintenance and testing of the ventilation system and luminaires within the spaces to ensure adequate performance. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E44 | During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. | Reorganise the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E45 | During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. | Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E46 | During the inspection of the transformer's breathing system, an assessment was conducted on its components, including the conservator tank, breather, and associated valves and piping. The condition of the silica gel or other desiccants within the breather was examined to ensure proper functionality. | Replace the silica gel in the breather and repair any leaks around the breather housing to prevent moisture ingress into the transformer insulation oil. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E47 | During the inspection of the transformer's breathing system, an assessment was conducted on its components, including the conservator tank, breather, and associated valves and piping. The condition of the silica gel or other desiccants within the breather was examined to ensure proper functionality. | Implement a regular maintenance schedule to periodically inspect and service the breathing system components, ensuring the silica gel is replaced as needed and that all seals and connections are intact to maintain system integrity. |  | E46 + 6 months | In Progress | 2025-12-30 | 2026-06-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E48 | During the inspection of the generator, transformer, and substation rooms, the physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. This was observed at HT and transformer room in the Energy Building. | Install temporary fire-resistant barriers and seal any gaps and openings between the generator, transformer, and substation areas to immediately reduce the risk of fire and electrical fault propagation. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E49 | During the inspection of the generator, transformer, and substation rooms, the physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. This was observed at HT and transformer room in the Energy Building. | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E50 | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E51 | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E52 | The placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. | Reposition batteries that are improperly placed to ensure they comply with safety regulations, allowing for safe access and adequate ventilation. Mark and clear pathways around battery installations to ensure easy and safe access for maintenance and emergencies. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E53 | The placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. | Conduct regular audits of battery placements to ensure ongoing compliance with safety standards and regulations. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E54 | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E55 | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E56 | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at trends building, engraving area near ETP and Energy Building. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E57 | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at Trends Building, engraving area near ETP and Energy Building. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E58 | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was observed at trends Building 2nd floor. | install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E59 | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was observed at trends Building 2nd floor. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E60 | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed at ETP area, storage area, Classic Building and behind the engraving processing area. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. |  | 4 months | In Progress | 2025-09-30 | 2026-01-30 | 4.25 | 29.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E61 | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed at ETP area, storage area, Classic Building and behind the engraving processing area. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E62 | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was specifically observed at classic building ground floor and rolling area processing Building 3. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. |  | 2 months | In Progress | 2025-09-30 | 2025-11-30 | 2.25 | 15.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E63 | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was specifically observed at classic building ground floor and rolling area processing Building 3. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E64 | Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was specifically observed at maintenance workshop, energy building, classic building and old processing production area. | Replace combustible wooden ply backings with non-combustible materials to reduce fire risk. |  | 3 months | In Progress | 2025-09-30 | 2025-12-30 | 3.25 | 22.75 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05
E65 | Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was specifically observed at maintenance workshop, energy building, classic building and old processing production area. | Establish a facility-wide standard to use only non-combustible materials for mounting electrical components, and conduct regular audits for compliance. |  | 6 months | In Progress | 2025-09-30 | 2026-03-30 | 6.5 | 45.5 | 2025-08-05 | 2025-09-05 | 2025-10-05 | 2025-11-05 | 2025-12-05 | 2026-01-05 | 2026-02-05 | 2026-03-05 | 2026-04-05 | 2026-05-05 | 2026-06-05 | 2026-07-05 | 2026-08-05 | 2026-09-05 | 2026-10-05 | 2026-11-05 | 2026-12-05 | 2027-01-05 | 2027-02-05 | 2027-03-05 | 2027-04-05 | 2027-05-05 | 2027-06-05 | 2027-07-05 | 2027-08-05 | 2027-09-05 | 2027-10-05 | 2027-11-05 | 2027-12-05 | 2028-01-05 | 2028-02-05 | 2028-03-05 | 2028-04-05 | 2028-05-05 | 2028-06-05 | 2028-07-05 | 2028-08-05 | 2028-09-05 | 2028-10-05 | 2028-11-05 | 2028-12-05 | 2029-01-05 | 2029-02-05 | 2029-03-05 | 2029-04-05 | 2029-05-05 | 2029-06-05 | 2029-07-05 | 2029-08-05 | 2029-09-05 | 2029-10-05 | 2029-11-05 | 2029-12-05 | 2030-01-05 | 2030-02-05 | 2030-03-05 | 2030-04-05 | 2030-05-05 | 2030-06-05 | 2030-07-05 | 2030-08-05 | 2030-09-05 | 2030-10-05 | 2030-11-05 | 2030-12-05 | 2031-01-05 | 2031-02-05 | 2031-03-05 | 2031-04-05 | 2031-05-05 | 2031-06-05 | 2031-07-05 | 2031-08-05 | 2031-09-05 | 2031-10-05 | 2031-11-05 | 2031-12-05 | 2032-01-05

## Finance Schedule
Finance Schedule
| Bismillah Textiles Ltd. - 1 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan | [5 empty] | Aug 25 | Sep 25 | Oct 25 | Nov 25 | Dec 25 | Jan 26 | Feb 26 | Mar 26 | Apr 26 | May 26 | Jun 26 | Jul 26 | Aug 26 | Sep 26 | Oct 26 | Nov 26 | Dec 26 | Jan 27 | Feb 27 | Mar 27 | Apr 27 | May 27 | Jun 27 | Jul 27 | Aug 27 | Sep 27 | Oct 27 | Nov 27 | Dec 27 | Jan 28 | Feb 28 | Mar 28 | Apr 28 | May 28 | Jun 28 | Jul 28 | Aug 28 | Sep 28 | Oct 28 | Nov 28 | Dec 28 | Jan 29 | Feb 29 | Mar 29 | Apr 29 | May 29 | Jun 29 | Jul 29 | Aug 29 | Sep 29 | Oct 29 | Nov 29 | Dec 29 | Jan 30 | Feb 30 | Mar 30 | Apr 30 | May 30 | Jun 30 | Jul 30 | Aug 30 | Sep 30 | Oct 30 | Nov 30 | Dec 30 | Jan 31 | Feb 31 | Mar 31 | Apr 31 | May 31 | Jun 31 | Jul 31
 | time axis 2025-08-05 to 2031-07-05
ITEM NO | REMEDIATION PLAN | TIMELINE |  | DURATION (MONTHS) | Remediation Cost Expenditure ↓ | Monthly Expenditure → | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | START | FINISH
% allocation check ↓
0
S1 | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 2025-08-05 | 2025-09-30 | 2 |  | % in all cells to the right must add up to 100%
S2 | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns or existing cylinder strength data and submit results to Pakistan Accord. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S3 | Verify insitu reinforcement by removing cover and confirming no. and diameter of bars and submit results to Accord. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S4 | Factory Engineer to review design, loads and columns stresses in area identified and submit to Pakistan Accord for review. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S5 | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building , in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 2025-08-05 | 2025-09-30 | 2 |  | % in all cells to the right must add up to 100%
S6 | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S7 | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths along with safe load plans reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan. | 2025-12-30 | 2026-04-30 | 4.25 |  | % in all cells to the right must add up to 100%
S8 | (4) Submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review. | 2026-04-30 | 2026-08-30 | 4.25 |  | % in all cells to the right must add up to 100%
S9 | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord. | 2026-08-30 | 2027-02-28 | 6.5 |  | % in all cells to the right must add up to 100%
S10 | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete. | 2027-02-28 | 2027-03-28 | 1 |  | % in all cells to the right must add up to 100%
S11 | Continue to implement load plan. | 2027-03-28 | 2027-04-28 | 1 |  | % in all cells to the right must add up to 100%
S12 | Verify insitu concrete stresses either by 100mm dia. cores or existing cylinder strength data for the from 4 columns and submit the results to Pakistan Accord to recheck the column stresses. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S13 | Factory Engineer to review design, loads and columns stresses in area identified above and submit to Pakistan Accord for review. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S14 | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | 2026-03-30 | 2026-06-30 | 3.25 |  | % in all cells to the right must add up to 100%
S15 | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S16 | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S17 | Carry out the remedial work. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S18 | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S19 | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S20 | Carry out the remedial work. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S21 | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate and submit to Pakistan Accord for review. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S22 | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S23 | Propose strengthening works as required and submit to Pakistan Accord for review. | 2025-12-30 | 2026-01-30 | 1 |  | % in all cells to the right must add up to 100%
S24 | Carry out remedial works as required. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
S25 | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S26 | Implement the approved remedial work. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S27 | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S28 | Implement the approved remedial work. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S29 | Identify the cause of the damage and propose measures to prevent further water damage. | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
S30 | Inspect damage to the column and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S31 | Implement remedial work. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S32 | Continue to monitor for future damage. | 2026-03-30 | 2026-06-30 | 3.25 |  | % in all cells to the right must add up to 100%
S33 | Propose the remedial measure to protect the reinforcement from future atmospheric corrosion and submit to Pakistan Accord for approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S34 | Implement the approved remedial work. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S35 | Repair damage to column corners and external faces. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S36 | Install protective measures to prevent recurring damage. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S37 | Continue to monitor condition of columns in highly trafficked areas. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S38 | Repair damage to column corners and external faces. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S39 | Install protective measures to prevent recurring damage. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S40 | Continue to monitor condition of columns in highly trafficked areas. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S41 | Identify the source of water ingress and propose measures to prevent further water damage. | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
S42 | Inspect damage to the column and wall and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S43 | Implement works as required and in accordance with documentation reviewed by Pakistan Accord. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
S44 | Continue to monitor for future signs of water ingress/damage. | 2026-03-30 | 2026-06-30 | 3.25 |  | % in all cells to the right must add up to 100%
S45 | Provide adequate edge protection on roof. Ensure similar measures are implemented in any other factory areas where these safety concerns exist. | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
S46 | Provide adequate edge protection on roof. Ensure similar measures are implemented in any other factory areas where these safety concerns exist. | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
S47 | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built drawings. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
S48 | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
S49 | Propose strengthening works as required and submit to Pakistan Accord for approval. | 2025-12-30 | 2026-01-30 | 1 |  | % in all cells to the right must add up to 100%
S50 | Implement strengthening works as required. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
S51 | Building structural engineer to review design documentation to confirm load capacity of the structure. Develop safe load plans and submit to Pakistan Accord for review. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
S52 | Factory to post safe load plans on each floor. | 2026-03-30 | 2026-04-30 | 1 |  | % in all cells to the right must add up to 100%
F1 | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 2025-08-05 | 2025-09-30 | 2 |  | % in all cells to the right must add up to 100%
F2 | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F3 | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
F4 | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
F5 | Remove obstructions on escape routes and keep them clear for escape. Cover any holes and uneven areas in escape routes. Provide warning signs where headroom height is less than 2.05 m on escape routes. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F6 | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) - Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F7 | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. - Implement measures to ensure adequate clear head height is achieved along all escape routes. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F8 | Any area over 46m common path of travel needs to be vacated or the egress routes need to be rearranged. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F9 | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F10 | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F11 | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F12 | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Standard. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F13 | Remove fire load and any other obstructions due to stored items from stairs. Remove devices that leave the doors propped open. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F14 | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F15 | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F16 | Remove all obstructions from stairs. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F17 | Remove all trip hazards from stairs. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F18 | Ensure the following are provided: - Stair structure to be fixed so that stairs are safe for escape. - Ensure all stairs have balustrades. - Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
F19 | Remove obstructions and lockable gates on external escape routes and keep them clear for escape. Turnstiles are not appropriate on an escape route and a pass door should be provided. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F20 | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes. - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes. - Provide additional exits from site. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F21 | - Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high risk areas. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F22 | Remove misleading directional escape signs. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F23 | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
F24 | Ensure that all exit signage is checked periodically and in good working condition. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
F25 | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction.) | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F26 | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F27 | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F28 | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F29 | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F30 | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F31 | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building. - Proposed fire separation details (including fire rating of walls and doors). - Relocate Day Care to Ground floor with exits directly to outside the building. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F32 | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F33 | Remove all informal sleeping areas from all buildings. | 2025-09-30 | 2025-10-14 | 0.5 |  | % in all cells to the right must add up to 100%
F34 | Document proposals for design of remedial measures to ensure compliance with all fire safety requirements for sleeping occupancies to comply with Pakistan Accord Standard. Submit proposals to Pakistan Accord for review. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F35 | Implement remediation measures to ensure full compliance with dormitory requirements of Pakistan Accord Standard and Pakistan Building Code in accordance with previously reviewed design. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F36 | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F37 | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F38 | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with, NFPA 14, 20, 22, and 24. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F39 | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | 2026-01-30 | 2026-02-28 | 1 |  | % in all cells to the right must add up to 100%
F40 | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | 2026-02-28 | 2026-05-28 | 3.25 |  | % in all cells to the right must add up to 100%
F41 | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | 2026-05-28 | 2026-08-28 | 3.25 |  | % in all cells to the right must add up to 100%
F42 | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | 2026-08-28 | 2026-11-28 | 3.25 |  | % in all cells to the right must add up to 100%
F43 | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | 2026-11-28 | Invalid | #VALUE! |  | % in all cells to the right must add up to 100%
F44 | Provide electric duty pump, diesel backup fire pumps and jockey pumps, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 2025-09-30 | 2027-03-30 | 19.5 |  | % in all cells to the right must add up to 100%
F45 | Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 2025-09-30 | 2027-03-30 | 19.5 |  | % in all cells to the right must add up to 100%
F46 | Ensure that all building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
F47 | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | 2025-11-30 | 2026-01-30 | 2.25 |  | % in all cells to the right must add up to 100%
F48 | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. Review the risk of asbestos and decide on suitable risk mitigation measures. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F49 | Implement the chemical handling strategy on site as agreed with Accord. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F50 | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
F51 | Implement the above plan on site. All chemical storage areas to be compliant with Pakistan Accord Standard. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
F52 | Conduct a fire drill and make records, including findings and recommended future improvements. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
F53 | Ensure fire drills are performed a minimum 2 times per year. | 2025-11-30 | 2026-01-30 | 2.25 |  | % in all cells to the right must add up to 100%
F54 | -Prepare testing schedule for all life safety systems. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
F55 | -Ensure all systems are being tested as per the schedule agreed with Accord . - Keep testing records. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
F56 | - Set up a maintenance schedule for all life safety systems. - Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. -The schedule to be submitted to Accord for review and approval. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
F57 | - Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. | 2025-12-30 | 2026-03-30 | 3.25 |  | % in all cells to the right must add up to 100%
F58 | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
F59 | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | 2025-11-30 | 2026-01-30 | 2.25 |  | % in all cells to the right must add up to 100%
E1 | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 2025-08-05 | 2025-09-30 | 2 |  | % in all cells to the right must add up to 100%
E2 | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E3 | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | 2025-12-30 | 2026-06-30 | 6.5 |  | % in all cells to the right must add up to 100%
E4 | Update the existing electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022) Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E5 | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | 2026-03-30 | 2026-09-30 | 6.5 |  | % in all cells to the right must add up to 100%
E6 | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 2025-09-30 | 2026-05-30 | 8.75 |  | % in all cells to the right must add up to 100%
E7 | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | 2026-05-30 | 2026-11-30 | 6.5 |  | % in all cells to the right must add up to 100%
E8 | Replace the obsolete oil-type circuit breaker with a modern vacuum or SF6 circuit breaker to ensure safety, reliability, and maintainability. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E9 | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable ampacity after applying derating factors. | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
E10 | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
E11 | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E12 | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E13 | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E14 | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E15 | Disconnect the earth bars from the neutral bars with the distribution boards and ensure proper separation and connection. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E16 | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E17 | Remove the polythene sheet from live transformer contacts to eliminate fire and electrical hazards and ensure proper insulation. | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
E18 | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E19 | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E20 | Inspect and repair or replace all damaged panels, cables, and busbars to ensure the integrity of the electrical system in accordance with Section 522 of BS7671 18th Edition + A2 (2022). | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E21 | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 2025-12-30 | 2026-06-30 | 6.5 |  | % in all cells to the right must add up to 100%
E22 | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E23 | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E24 | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E25 | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
E26 | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 2025-09-30 | 2025-10-30 | 1 |  | % in all cells to the right must add up to 100%
E27 | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E28 | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
E29 | If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E30 | (1) Submit design documentation for new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E31 | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | 2025-12-30 | 2026-01-30 | 1 |  | % in all cells to the right must add up to 100%
E32 | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | 2026-01-30 | 2026-05-30 | 4.25 |  | % in all cells to the right must add up to 100%
E33 | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | 2026-05-30 | 2026-10-30 | 5.5 |  | % in all cells to the right must add up to 100%
E34 | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | 2026-10-30 | 2027-01-30 | 3.25 |  | % in all cells to the right must add up to 100%
E35 | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | 2027-01-30 | 2027-04-30 | 3.25 |  | % in all cells to the right must add up to 100%
E36 | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
E37 | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E38 | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E39 | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
E40 | Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
E41 | Upgrade the backup power supply to ensure it can adequately support all emergency luminaires during a power failure. This includes installing additional battery packs or generators as necessary to comply with the Building Code of Pakistan Fire Safety Provisions 2016. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E42 | Redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the generator and transformer receive adequate ventilation. This might involve repositioning vents or adding ductwork. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E43 | Establish regular maintenance and testing of the ventilation system and luminaires within the spaces to ensure adequate performance. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E44 | Reorganise the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E45 | Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E46 | Replace the silica gel in the breather and repair any leaks around the breather housing to prevent moisture ingress into the transformer insulation oil. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E47 | Implement a regular maintenance schedule to periodically inspect and service the breathing system components, ensuring the silica gel is replaced as needed and that all seals and connections are intact to maintain system integrity. | 2025-12-30 | 2026-06-30 | 6.5 |  | % in all cells to the right must add up to 100%
E48 | Install temporary fire-resistant barriers and seal any gaps and openings between the generator, transformer, and substation areas to immediately reduce the risk of fire and electrical fault propagation. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
E49 | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E50 | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
E51 | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E52 | Reposition batteries that are improperly placed to ensure they comply with safety regulations, allowing for safe access and adequate ventilation. Mark and clear pathways around battery installations to ensure easy and safe access for maintenance and emergencies. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
E53 | Conduct regular audits of battery placements to ensure ongoing compliance with safety standards and regulations. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E54 | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E55 | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E56 | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E57 | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E58 | install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
E59 | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E60 | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 2025-09-30 | 2026-01-30 | 4.25 |  | % in all cells to the right must add up to 100%
E61 | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E62 | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2025-09-30 | 2025-11-30 | 2.25 |  | % in all cells to the right must add up to 100%
E63 | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
E64 | Replace combustible wooden ply backings with non-combustible materials to reduce fire risk. | 2025-09-30 | 2025-12-30 | 3.25 |  | % in all cells to the right must add up to 100%
E65 | Establish a facility-wide standard to use only non-combustible materials for mounting electrical components, and conduct regular audits for compliance. | 2025-09-30 | 2026-03-30 | 6.5 |  | % in all cells to the right must add up to 100%
Only edit items highlighted in yellow

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
anotehr electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1