## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
8 & 9-Jul-2024
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | Feroze 1888 Mills Limited, Plot No. H‐23/4A, Scheme No.3, Landhi Industrial Area, Karachi, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 8 & 9 -Jul-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg. | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). | 3 months | Substation detailed drawing is available & provided to Accord for review & approval. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but not up to date also there were missing necessary details such as circuit identification, cable/breaker sizes, protective devices, voltage levels, standard legends, and distribution board tags. | Upgrade comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 months | SLDs are updated for breakers rating & sizes, busbar voltages and connected load, however further details of cable sizes is in progress. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts but the all-layout drawings were missing necessary details. | Upgrade comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). | 8 months | Electrical layouts available & will provided to Accord team for review & approval. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | During the survey It was observed that, - Burnt Circuit Breaker found in first floor new compressor room building A control distribution board at high risk of fire - Circuit breakers are mounted inappropriately at finishing first floor building-A dying and processing - Unmounted live circuit breaker found inside compressor panel at 3rd floor of building E - Power House | Inspect and repair or replace all damaged circuit breakers to ensure the integrity of the electrical system in accordance with BS7671 18th Edition + A2 (2022) | 1 month | Damaged/Burnt out circuit breaker replaced on all highlighted location. Unmounted circuit breakers mounted properly now. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E5 | DBs & Elec Protection Systems | Circuit breakers | - It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes at Building B - Stitching and Packing M3. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. | E4 + 3 months | Detailed working is being carried out and replacement is being done where possible. For all new installation proper sizing of cables & breakers will be done. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots, - Loose connections and Insulation degradation in first floor new compressor room (Building A) - Faulty components and Improper sized cable behind turbine distribution board in powerhouse. (Building E) - Overloading observed in transformer placed in powerhouse (Building E). | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | Thermography was carried out of all panels, breakers were checked for any loose connection, caring loads and rating. All the highlighted hotspot removed and report will be shared with Accord team for review & approval. Breakers thermography will be performed quarterly. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | E7 | DBs & Elec Protection Systems | Hot Spots | There was available thermographic snaps for few areas. However, a complete thermographic report of the facility was not available on site. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | E6 + 6 months | All breakers thermography will be performed quarterly. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | During the inspection it was observed that, i. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections such as behind turbine at power house. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 3 months | Earthing cables installed at missing locations and all loose connections were made proper. Inspection will be carried out quarterly. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | [10 empty] | E9 | DBs & Elec Protection Systems | Earthing system | During the inspection it was found that equipotential bonding for the cable trays, machines body and metallic panel covers was missing such as at feed pump in power house (building E) | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | E8 + 2 months | cable trays & machines body are being inspected for said observation. We have done equipotential bonding of highlighted points in the report. Cable trays are being covered properly with equipotential bonding. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | During the inspection It was also found that the Earth testing record was available, but the Earth distribution layout drawing was not available. | Develop the earth distribution layout drawing, earth testing record, and submit them to the Pakistan Accord. | 3 months | Earth testing is being done regularly and record is updated, however layout drawing work is in process. |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was observed that electrical components were not suitable for the environmental conditions in which they were installed such as panel installed behind boiler in printing (Building E). Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements such as in old spinning building at ground floor (Building A) and workshop area (Building E). | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | Corroded panels are being refurbished and modification job has been performed on some panels. |  |  |  | In Progress
No | 3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was observed that there was loose wiring, cables had joints, improper bus-bar arrangement, cables touching with busbars and panel body inside the distribution boards such as in powerhouse control panel. (Building E) | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | E11+ 3 months | Connections have been made proper where possible without system shutdown. However complete working is in process. |  |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection It was found that in many distributions board lack of dedicated neutral connection for outgoing power circuits such as in production area distribution boards. | Conduct a thorough inspection of the existing wiring to identify circuits sharing a neutral wire. Provide dedicated neutral wires for each circuit, ensuring that each circuit's return path is properly isolated. | E12 + 1 month | Neutral wires will be identified accordingly & would be led accordingly. |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multi looping was observed. Multiple circuits were being protected by a single circuit break in locations such as office area, 1st and 2nd floor stitching distribution board and production areas (Building A, B and D). | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022) | 3 months | Implementation would be made as per Accord recommendations. |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | [10 empty] | E15 | DBs & Elec Protection Systems | Openings | During the inspection below observation are made regarding openings: - Unsealed openings were discovered in the panels in main LT panel and generator control room (Building E) - Unsealed openings and strain on cables were discovered in the distribution boards at old weaving ground floor and VFD panel at finishing first floor (Building B and A). | Corrective actions are required to seal all openings and replace missing panels covers to restore the integrity and safety of the electrical systems. Install cable glands or bushings to provide strain relief and protect cables at entry points in distribution boards. | 3 months | Distribution boards have been sealed, for large panels work is in process, modification may require partial or complete shutdown of machine or department. |  |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Adequate accessibility | During the inspection at numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components in locations such as distribution boards In Front of generator room, VFD panel in finishing area, stitching first floor and at water cooler circuit breaker at stitching second floor (Building B and E). | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022) | 1 month | It requires complete relocation of panels, one of the DB in power house already relocated. It will require civil work & will be done accordingly. |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | [10 empty] | E17 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels, and trunking systems in (building A and E). | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022) | 1 month | Regular inspection is being done for panels & trunking. |  |  |  | In Progress
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection a lightning protection system was found, however, there was no adequate risk assessment, study, design, and documentation available to confirm its adequacy. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. | 2 months | 3rd party inspection is required to check efficacy of the LPS. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 | [12 empty] | E19 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection it was observed that no test results were provided for the lightning protection system, making it difficult to verify its effectiveness and compliance with relevant standards. | Perform a thorough inspection of all LPS conductors. Replace any conductors showing signs of corrosion or rust with new components that meet the current standards. Apply protective coatings or use materials resistant to corrosion to prevent future deterioration of LPS components. | 2 months | 3rd party inspection is required to check efficacy of the LPS. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 | [12 empty] | E20 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection it was observed that a surge counter was found on LPS conductor, however there was no available document supporting the number of surge counter installed and its adequate placement. | Modify or install surge protective devices after LPS assessment throughout the facility. | 6 months | 3rd party inspection is required to check efficacy of the LPS. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, FADS panel(s) were surveyed. • One panel was addressable which was covering old weaving area. However, there was another addressable panel which was covering production buildings and associated departments. • Repeater panels were observed in basements at an inaccessible height. • Both panels were not listed. • Multiple fault indications are being displayed on the addressable Fire Alarm Panel (FAP) of production buildings. However, the fault was correctly identified with the mention zones. • Both Fire Alarm Panel were at built-in battery supply. The following observations were made regarding the detectors within the facility's Fire Alarm and Detection System (FADS): Inadequate detection coverage provided in several areas: - Generator Area (Building E) - Production Area (Building A and B) - Powerhouse (Building E) - Detection devices were not listed. - Detectors were incorrectly installed or obstructed, potentially causing delayed activation such as in weaving Section The following observations were made with regard to the Manual Call Points: • Manual call points were not listed throughout the facility, not installed at all required locations at finishing hall exits. • Manual call points were installed with inadequate fixings at stitching floor. • Manual call points were installed with inappropriate locations in production storage area and finishing 1st Floor The following observations were made with regards to the sounders and visual alarms: • Sounders were inaudible due to low volume or high ambient noise, resulting in insufficient audibility in certain locations. • Sounders were not installed with proper supporting arrangements. | This Related to the Main Buildings A and B (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Services of consultant will be acquired to assess the installation as per NFPA 72. Gaps, if any, shall be produced in the design document for Accord Team's approval. Existing FADS is duly aligned with LPCB standards. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E21+ 1 month | Existing FADS is duly aligned with LPCB standards. Supporting documents shall be shared with Accord Team for review/approval. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E22+ 4 months | Existing FADS is duly aligned with LPCB standards. Supporting documents shall be shared with Accord Team for review/approval. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E23+ 5 months | FADS is installed with LPCB equipment. Upon receipt of consultant's report, upgradation will be made part of existing system. Completion report along with as built document will be shared thereafter. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E24+ 3 months | Accord Team will be invited for verification after the completion of upgradation/filling up of gaps. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E25+ 3 month | Accord Team will be invited for verification after the completion of upgradation/filling up of gaps. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the FADS panel(s) were surveyed. • One panel was addressable which was covering old weaving area. However, there was another addressable panel which was covering production buildings and associated departments. • Repeater panels were observed in basements at an inaccessible height. • Both of the panels were not listed. • Multiple fault indications are being displayed on the addressable Fire Alarm Panel (FAP) of production buildings. However, the fault was correctly identified with the mention zones. • Both Fire Alarm Panel were at built-in battery supply. The following observations were made regarding the detectors within the facility's Fire Alarm and Detection System (FADS): • Inadequate detection coverage was provided in several areas such as • Generator Area (Building E) • Production Area (Building A and B) • Powerhouse (Building E) • Detection devices were not listed. • Detectors were incorrectly installed or obstructed, potentially causing delayed activation such as in weaving Section The following observations were made with regard to the Manual Call Points: • Manual call points were not listed throughout the facility. • Manual call points were not installed at all required locations at finishing hall exits. • Manual call points were installed with inadequate fixings at stitching floor. • Manual call points were installed with inappropriate locations in production and storage area and finishing 1st Floor The following observations were made with regards to the sounders and visual alarms: • Sounders were inaudible due to low volume or high ambient noise, resulting in insufficient audibility in certain locations. • Sounders were not installed with proper supporting arrangements. | This Related to the Main Buildings C (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Services of consultant will be acquired to assess the installation as per NFPA 72. Gaps, if any, shall be produced in the design document for Accord Team's approval. Existing FADS is duly aligned with LPCB standards. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E27 + 1 month | Existing FADS is duly aligned with LPCB standards. Supporting documents shall be shared with Accord Team for review/approval. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E28 + 4 months | Existing FADS is duly aligned with LPCB standards. Supporting documents shall be shared with Accord Team for review/approval. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E29 + 5 months | FADS is installed with LPCB equipment. Upon receipt of consultant's report, upgradation will be made part of existing system. Completion report along with as built document will be shared thereafter. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E30 + 3 months | Accord Team will be invited for verification after the completion of upgradation/filling up of gaps. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E31 + 3 months | Accord Team will be invited for verification after the completion of upgradation/filling up of gaps. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | FADS panel(s) were surveyed. One panel was addressable covered the old weaving area. Another addressable panel was covering production buildings and associated departments. • Repeater panels were observed in basements at an inaccessible height, both of the panels were not listed. • Multiple fault indications are displayed on the addressable Fire Alarm Panel (FAP) of production buildings. However, the fault was correctly identified with the mention zones. Both Fire Alarm Panels were at built-in battery supply. Fire Alarm and Detection System (FADS): - Inadequate detection coverage was provided in Generator Area (Building E), Production Area (Building A and B), Powerhouse (Building E). - Detectors were not listed and incorrectly installed or obstructed, potentially causing delayed activation such as in weaving Section Manual Call Points: • Manual call points were not listed throughout the facility and were not installed at all required locations at finishing hall exits. • Manual call points were installed with inadequate fixings at stitching floor and installed at inappropriate locations in production and storage area and finishing 1st Floor Sounders and Visual alarms: • Sounders were inaudible due to low volume or high ambient noise, resulting in insufficient audibility in certain locations. • Sounders were not installed with proper supporting arrangements. | This Related to the Main Buildings D and E (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Services of consultant will be acquired to assess the installation as per NFPA 72. Gaps, if any, shall be produced in the design document for Accord Team's approval. Existing FADS is duly aligned with LPCB standards. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E33 + 1 month | Existing FADS is duly aligned with LPCB standards. Supporting documents shall be shared with Accord Team for review/approval. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E34 + 4 months | Existing FADS is duly aligned with LPCB standards. Supporting documents shall be shared with Accord Team for review/approval. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E35 + 5 months | FADS is installed with LPCB equipment. Upon receipt of consultant's report, upgradation will be made part of existing system. Completion report along with as built document will be shared thereafter. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E36 + 3 months | Accord Team will be invited for verification after the completion of upgradation/filling up of gaps. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E37 + 3 months | Accord Team will be invited for verification after the completion of upgradation/filling up of gaps. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E39 | Emergency Lighting | Provided but insufficient | During the inspection, the emergency lighting arrangement throughout the facility was assessed: i. Several areas lack sufficient emergency lighting coverage. • Storage Area Building D basement • Ground Floor to First Floor Stairs building B stitching • First Floor to Second Floor Stairs building A. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional listed emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 1 month | 1. Fire Safety Team along with PE Electrical Team will conduct a survey of complete facility to identify the gaps requiring additional lighting. 2. Recommendation along with Cost will be shared with Management for approval followed by execution. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Emergency Lighting | Provided but insufficient | ii. Multiple emergency During the inspection luminaires indicate the need for maintenance in old weaving, spinning and printing area (Building E). | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | E39 + 5 months | Inspection of all lights is part of routine and issues related to cleaning, replacement, rectification etc. are addressed promptly. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | Existing emergency lights are duly configured to be illuminated as general lighting power fails. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Emergency Lighting | General Lighting | During the inspection it was noted: - Several locations were identified as lacking sufficient general lighting including building external areas, stairs, walkways (Building B). | Conduct a thorough assessment of lighting throughout the facility to find areas with insufficient illumination. Install additional lighting fixtures in these spots to ensure adequate brightness. Ensure the new lighting design meets safety and efficiency guidelines to provide clear visibility for all tasks and emergency situations. | 1 month | 1. Security Team along with PE Electrical Team will conduct a survey of complete facility to identify the gaps requiring additional lighting. 2. Recommendation along with Cost will be shared with Management for approval followed by execution. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Emergency Lighting | General Lighting | During the inspection it was noted that - General lighting was controlled directly from the breakers within the Distribution Boards rather than through standard light switches in warehouse (Building A) | Reconfigure the electrical control system to ensure that general lighting is operated via standard wall-mounted light switches instead of circuit breakers. This involves installing appropriate switches and rewiring the control circuits as per the National Electrical Code (NEC) and other relevant electrical safety standards. Ensure that all switches are easily accessible and clearly labelled to enhance operational efficiency and safety. | E42 + 3 months | Agreed |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Cabling & Wiring | Cables support and protection | During the inspection it was noted that proper supports were not provided for cables; they were laid directly on the ground. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure such as in basement (Building E). | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 3 months | Supports are being installed to avoid sagging. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E45 | Cabling & Wiring | Cables support and protection | During the inspection it was noted that numerous loose connections were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections such as in mechanic workshop and generator control room (Building E). | Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). | E44 + 1 month | Agreed & closed. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E46 | Cabling & Wiring | Cables support and protection | During the inspection it was noted that It was found that at many locations, the insulation of cables was damaged. Damaged insulation can expose live conductors, posing a risk of electrical shock to anyone who comes into contact with the cables such as stitching 2nd floor (Building B). | Upgrade insulation or replace damaged cables to prevent electrical hazards. | E45 + 1 month | Cables are either being replaced or insulation sleeves are being used on existing cables. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E47 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. (Building A and B) 1st floor stitching. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 2 months | Agreed |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E48 | Cabling & Wiring | Splicing of cables | During the inspection it was found that cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections (Building E) | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022) | 2 months | Agreed |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E49 | Cabling & Wiring | Splicing of cables | During the inspection it was observed that PVC tape joints were found in several locations - including within distribution boards (Building A and B) | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | E48 + 2 months | Agreed |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E50 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. | 2 months | Will refer the issue to electrical consultant to seek solution to this problem. Timeline to take a workable solution |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E51 | Cabling & Wiring | Fixture | During the inspection, damage electrical fixtures and loose power receptacles were found at Powerhouse (Building E) and Workshop (Building A) | Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed. | 3 months | Damaged/Burnt fixtures rectified. |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
8 & 9-Jul-2024
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [12 empty] | Feroze 1888 Mills Limited, Plot No. H‐23/4A, Scheme No.3, Landhi Industrial Area, Karachi, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 8 & 9-July-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Protection of stairs | Unprotected openings into stairs throughout all buildings Unprotected penetrations into stairs at 1st floor Building-01. Doors to stairs not fire doors in all the buildings. Services passing through most of the stairs in Building-01 & Building-02. Fire load under stair S 26 at Building-02. | Remove fire load and any obstructions due to stored items from stairs. | 2 weeks | Obstruction has been removed from identified stairs. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Protection of stairs | Unprotected openings into stairs throughout all buildings Unprotected penetrations into stairs at 1st floor Building-01. Doors to stairs not fire doors in all the buildings. Services passing through most of the stairs in Building-01 & Building-02. Fire load under stair S 26 at Building-02. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect the stairs. Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 1. A detailed survey of complete facility has been conducted to identify penetration points and unprotected openings. 2. Identified areas with proposal to seal the stairs from penetration/unprotected opening are being plugged in the Drawings by Project Team. 3. Duly updated drawing will be shared with Accord Team for Review/Approval as per shared timeline. 31-12-2025 4. After drawing approval execution of task will be done according to the timelines. |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Protection of stairs | Unprotected openings into stairs throughout all buildings Unprotected penetrations into stairs at 1st floor Building-01. Doors to stairs not fire doors in all the buildings. Services passing through most of the stairs in Building-01 & Building-02. Fire load under stair S 26 at Building-02. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90 minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: All doors into stairs should be fire resisting doors with self-closing mechanisms. Penetrations through doors are not permitted. Doors into stairs should be kept closed (but not locked) at all times. | F2 + 4 months | 1. Existing emergency exit doors will be improved to provide 90 minutes resistance through following:- a. Globally recognized fire retardant insulation/paint will procured. b. Specifications of fire retardant insulation/paint, doors along with its accessories will be shared with Accord Team for review/approval. c. Upon approval by Accord Team, sample door will be prepared for final consent. d. 100% doors will be improved as per approved sample. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Travel distance | Travel distance to the nearest of alternative exits exceeds distance limits at Dyeing ground floor of Building-01 (77 m). Travel distance to the nearest of alternative exits exceeds distance limits at basement floor of Building-01 (86 m). | Identify & propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | Following strategy will follow:- 1. Phase I:- Detail survey by Fire Team to identify travel distances exceeding 60 meters which is in progress. 2. Phase II:- Readjustment of existing Exit Pathways to comply with requirement. 3. Phase III:- Recommendation duly vetted by Management will be shared with Accord Team for Review/Approval. 4. Phase IV:-Post Management & Accord approval execution work for construction of additional Escape Routes/Exit Points will be done. |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Travel distance | Travel distance to the nearest of alternative exits exceeds distance limits at Dyeing ground floor of Building-01 (77 m). Travel distance to the nearest of alternative exits exceeds distance limits at basement floor of Building-01 (86 m). | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F4 + 4 months | Following strategy will follow:- 1. Phase I:- Detail survey by Fire Team to identify travel distances exceeding 60 meters which is in progress. 2. Phase II:- Readjustment of existing Exit Pathways to comply with requirement. 3. Phase III:- Recommendation duly vetted by Management will be shared with Accord Team for Review/Approval. 4. Phase IV:-Post Management & Accord approval execution work for construction of additional Escape Routes/Exit Points will be done. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Escape doors | Escape doors are lockable throughout all buildings. Sliding doors serve for escape from areas with more than 10 occupants, Fabric warehouse and chemical warehouse, production floor at Ground floor Building-01. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | As discussed and agreed by Accord Team, existing locking devices with single motion were accepted. No change is recommended. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Escape doors | Escape doors are lockable throughout all buildings. Sliding doors serve for escape from areas with more than 10 occupants, Fabric warehouse and chemical warehouse, production floor at Ground floor Building-01. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Pakistan Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | Pocket doors, opening the direction of escape have been installed/fixed to provide easy exit. |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Escape doors | Escape doors are lockable throughout all buildings. Sliding doors serve for escape from areas with more than 10 occupants, Fabric warehouse and chemical warehouse, production floor at Ground floor Building-01. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F7 + 3 months | As discussed and agreed by Accord Team, existing locking devices with single motion were accepted. No change is recommended. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit access | Obstructions in escape route at 2nd floor Building-02 & 1st floor Building-01. Protected stair S 3 & S 6 discharge inside the building at a distance from building exit at Building-01. | Remove obstructions from escape route. | 2 weeks | All obstructions removed from Escape Route. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | Obstructions in escape route at 2nd floor Building-02 & 1st floor Building-01. Protected stair S 3 & S 6 discharge inside the building at a distance from building exit at Building-01. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect stair discharge corridors Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | 1. A detailed survey of complete facility has been conducted to identify stairs discharging within the building thus requiring dedicated fire rated corridors to provide safe exit. 2. Identified areas are being plugged in the Drawings by Project Team. 3. Duly updated drawing will be shared with Accord Team for Review/Approval as per shared timeline.31-12-2025 4. After drawing approval execution of task will be done according to the timelines. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Obstructions in escape route at 2nd floor Building-02 & 1st floor Building-01. Protected stair S 3 & S 6 discharge inside the building at a distance from building exit at Building-01. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F10 + 4 months | 1. A detailed survey of complete facility has been conducted to identify stairs discharging within the building thus requiring dedicated fire rated corridors to provide safe exit. 2. Identified areas are being plugged in the Drawings by Project Team. 3. Duly updated drawing will be shared with Accord Team for Review/Approval as per shared timeline.31-12-2025 4. After drawing approval execution of task will be done according to the timelines. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit signage | Missing exit signs at entry into stairs Missing exit signs at stair discharge routes Missing exit signs in corridors and circulation areas Missing exit signs in production areas Missing exit signs at exits from site Missing exit signs at roof Electrically powered exit signs are not a tested and listed system | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | Exit signages marked/pasted and old/turnout replaced with new. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit signage | Missing exit signs at entry into stairs Missing exit signs at stair discharge routes Missing exit signs in corridors and circulation areas Missing exit signs in production areas Missing exit signs at exits from site Missing exit signs at roof Electrically powered exit signs are not a tested and listed system | Ensure that all exit signage is checked periodically and in good working condition. | F12 + 3 months | Inspection of exit signages added in fire team monthly inspection schedule. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Rated Construction | Separation of high risk areas | Electrical rooms are not fire separated from storage areas at 1st floor Building-01. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | 1. A detailed survey of complete facility is in progress to identify increased fire hazard areas to include storage, electrical rooms, mechanical rooms etc. 2. Identified areas are being plugged in the Drawings by Project Team. 3. Duly updated drawing will be shared with Accord Team for Review/Approval for execution 31-12-2025 4. After drawing approval execution of task will be done according to the timelines. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Fire Rated Construction | Separation of high risk areas | Electrical rooms are not fire separated from storage areas at 1st floor Building-01. | Provide 2 hour fire rated construction including 90 minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F14 + 4 months | 1. A detailed survey of complete facility is in progress to identify increased fire hazard areas to include storage, electrical rooms, mechanical rooms etc. 2. Identified areas are being plugged in the Drawings by Project Team. 3. Duly updated drawing will be shared with Accord Team for Review/Approval 31-12-2025 4. After drawing approval execution of task will be done according to the timelines. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Rated Construction | Separation of shafts | All the lift shafts are not separated with fire rated construction from production at Building-01 & Building-02. Unprotected vertical shaft not separated with fire rated construction connecting all floors at Building-01 | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors enclosing vertical shafts. Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Cargo Lift Shafts: 1. All the shafts are RCC Structure. 2. Doors will be improved to provide 90 minutes of fire resistance through: a. Globally recognized fire retardant insulation/paint will procured. b. Specifications of fire retardant insulation/paint, doors along with its accessories will be shared with Accord Team for review/approval 12/31/2025 c. Upon approval by Accord Team, sample door will be prepared for final consent. 06/30/2026 d. 100% doors will be improved upon sample approval and timeline will be shared accordingly. Dumbwaiter & Beam Carozole Lift 1. Existing shafts of Dumbwaiter & Beam Carozole Lift are covered with Iron Mesh & Sheet. 2. Consultant will be approached to suggest appropriate material to meet the Accord requirement. 3. Recommendation by the consultant will be shared with Accord Team for review/approval 31-12-2025 4. 100% shafts will be replaced/improved after approval. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Rated Construction | Separation of shafts | All the lift shafts are not separated with fire rated construction from production at Building-01 & Building-02. Unprotected vertical shaft not separated with fire rated construction connecting all floors at Building-02 | Provide 2 hour fire rated protection to vertical shafts according to the layouts and documents reviewed by Pakistan Accord. | F 16 + 4 months | Cargo Lift Shafts: 1. All the shafts are RCC Structure. 2. Doors will be improved to provide 90 minutes of fire resistance through: a. Globally recognized fire retardant insulation/paint will procured. b. Specifications of fire retardant insulation/paint, doors along with its accessories will be shared with Accord Team for review/approval 12/31/2025 c. Upon approval by Accord Team, sample door will be prepared for final consent. 06/30/2026 d. 100% doors will be improved upon sample approval and timeline will be shared accordingly. Dumbwaiter & Beam Caposole Lift 1. Existing shafts of Dumbwaiter & Beam Carozole Lift are covered with Iron Mesh & Sheet. 2. Consultant will be approached to suggest appropriate material to meet the Accord requirement. 3. Recommendation by the consultant will be shared with Accord Team for review/approval 31-12-2025 4. 100% shafts will be replaced/improved after approval. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Separation of occupancies | Basements are not fire separated from the rest of the Building-01 (All parts) & Building-02 (Part B). Canteen not separated from production at 1st floor Building-02 (Part D). Large office areas not fire separated from the storage area at 1st floor Building-01 (Part 3 & 4). | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building Proposed fire separation details (including fire rating of walls and doors) | 4 months | 1. Services of Civil Consultant being acquired to formulate the plan for isolating/separating basement, offices, canteen and buildings. 2. Firm plan in the shape of drawings will be shared with Accord Team for review/approval followed for execution. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Separation of occupancies | Basements are not fire separated from the rest of the Building-01 (All parts) & Building-02 (Part B). Canteen not separated from production at 1st floor Building-02 (Part D). Large office areas not fire separated from the storage area at 1st floor Building-01 (Part 3 & 4). | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building Proposed fire separation details (including fire rating of walls and doors) | F18 + 4 months | 1. Services of Civil Consultant being acquired to formulate the plan for isolating/separating basement, offices, canteen and buildings. 2. Firm plan in the shape of drawings will be shared with Accord Team for review/approval followed for execution. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Floor openings | Floor opening linking different floors is not fire separated at 1st floor Building-01 (Part 3 & 4). | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings - Proposed fire separation details (including fire rating of walls and doors) | 4 months | 1. Services of Civil Consultant being acquired to formulate the plan for isolating/separating basement, offices, canteen and buildings. 2. Firm plan in the shape of drawings will be shared with Accord Team for review/approval followed for execution. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Floor openings | Floor opening linking different floors is not fire separated at 1st floor Building-01(Part 3 & 4). | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F20 + 4 months | 1. Services of Civil Consultant being acquired to formulate the plan for isolating/separating basement, offices, canteen and buildings. 2. Firm plan in the shape of drawings will be shared with Accord Team for review/approval followed for execution. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Storage | Storage areas are not fire separated from cutting/production areas at Building-01 (Part 1 to 6, Phase 4) & Building-02 (All parts). | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Work in consultation with Production Floor In charges is in progress to meet the required standard through re-arranging the storage management. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Storage | Storage areas are not fire separated from cutting/production areas at Building-01(Part 1 to 6, Phase 4) & Building-02 (All parts). | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F22 + 4 months | Work in consultation with Production Floor In charges is in progress to meet the required standard through re-arranging the storage management. |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Sprinkler system | Parts of Building-01 have occupied floors at a height greater than 18m and the building is not sprinkler protected. Sprinkler hazard classification is not appropriate based on the use of the building areas at Building-01. Sprinkler system is in poor condition and installed only at basement floor Building-01. | (1) Submit design documentation for a sprinkler system, along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 month | 1. Exemption as provided in the Building Code of Pakistan (2016) clause 9.1.1.4.2, for the installation of sprinkler system in the existing structure subject to approval by AHJ will be explored. 2. Services of consultant will be hired in addition to assess the operational difficulties negating/allowing installation of sprinkler system in the existing structure. 3. Consultant report & AHJ advice will be shared with Accord Team for review/approval. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 | [12 empty] | F25 | Fire Suppression | Sprinkler system | Parts of Building-01 have occupied floors at a height greater than 18m and the building is not sprinkler protected. Sprinkler hazard classification is not appropriate based on the use of the building areas at Building-01. Sprinkler system is in poor condition and installed only at basement floor Building-01. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F24 + 1 month | 1. Exemption as provided in the Building Code of Pakistan (2016) clause 9.1.1.4.2, for the installation of sprinkler system in the existing structure subject to approval by AHJ will be explored. 2. Services of consultant will be hired in addition to assess the operational difficulties negating/allowing installation of sprinkler system in the existing structure. 3. Consultant report & AHJ advice will be shared with Accord Team for review/approval. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 | [12 empty] | F26 | Fire Suppression | Sprinkler system | Parts of Building-01 have occupied floors at a height greater than 18m and the building is not sprinkler protected. Sprinkler hazard classification is not appropriate based on the use of the building areas at Building-01. Sprinkler system is in poor condition and installed only at basement floor Building-01. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F25 + 3 months | 1. Exemption as provided in the Building Code of Pakistan (2016) clause 9.1.1.4.2, for the installation of sprinkler system in the existing structure subject to approval by AHJ will be explored. 2. Services of consultant will be hired in addition to assess the operational difficulties negating/allowing installation of sprinkler system in the existing structure. 3. Consultant report & AHJ advice will be shared with Accord Team for review/approval . |  |  |  | In Progress
No | 3 | 8 |  | 132 | 421 | 6 | 5 | [12 empty] | F27 | Fire Suppression | Sprinkler system | Parts of Building-01 have occupied floors at a height greater than 18m and the building is not sprinkler protected. Sprinkler hazard classification is not appropriate based on the use of the building areas at Building-01. Sprinkler system is in poor condition and installed only at basement floor Building-01. | (4) Once installation of the SUPS system is complete, factory to submit full "as built" documentation of the system to Pakistan Accord for review. Provide full testing and commissioning (T&C) | F26 + 3 months | 1. Exemption as provided in the Building Code of Pakistan (2016) clause 9.1.1.4.2, for the installation of sprinkler system in the existing structure subject to approval by AHJ will be explored. 2. Services of consultant will be hired in addition to assess the operational difficulties negating/allowing installation of sprinkler system in the existing structure. 3. Consultant report & AHJ advice will be shared with Accord Team for review/approval . |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 | [12 empty] | F28 | Fire Suppression | Sprinkler system | Parts of Building-01 have occupied floors at a height greater than 18m and the building is not sprinkler protected. Sprinkler hazard classification is not appropriate based on the use of the building areas at Building-01. Sprinkler system is in poor condition and installed only at basement floor Building-01. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | F27 + 3 months | 1. Exemption as provided in the Building Code of Pakistan (2016) clause 9.1.1.4.2, for the installation of sprinkler system in the existing structure subject to approval by AHJ will be explored. 2. Services of consultant will be hired in addition to assess the operational difficulties negating/allowing installation of sprinkler system in the existing structure. 3. Consultant report & AHJ advice will be shared with Accord Team for review/approval. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Suppression | Sprinkler system | Parts of Building-01 have occupied floors at a height greater than 18m and the building is not sprinkler protected. Sprinkler hazard classification is not appropriate based on the use of the building areas at Building-01. Sprinkler system is in poor condition and installed only at basement floor Building-01. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F28 + 4 months = 18 months | 1. Exemption as provided in the Building Code of Pakistan (2016) clause 9.1.1.4.2, for the installation of sprinkler system in the existing structure subject to approval by AHJ will be explored. 2. Services of consultant will be hired in addition to assess the operational difficulties negating/allowing installation of sprinkler system in the existing structure. 3. Consultant report & AHJ advice will be shared with Accord Team for review/approval . |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs of Building-01 & Building-02 which requires due to height greater than 15m & number of floors more than 3. | Provide design for a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system and submit to Accord for review by following steps (1) to (6) above. | 18 months | As discussed and agreed by Accord Team, existing standpipes will be inspected and if deemed necessary, shall be recommended for change. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Suppression | Fire pumps | Fire pump set is not listed installed at Building-01. Fire pumps are not in a fire separated room at Building-01. | Provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Pakistan Accord for review by following steps (1) to (6) above. | 18 months | 1. Existing Pumps are manufactured in accordance with EN-12845. 2. To assess the compatibility of existing fire pumps with NFPA 20 & BCP Standards, services of consultant will be hired for recommendation in the light of provision referred vide NFPA & BCP standard. 3. Same will be shared with Accord Team for review/approval. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Hazardous Materials | Chemicals handling | Unsafe handling procedures at printing areas at 2nd floor Building-02. Large amounts of chemicals in production area at 2nd floor Building-02. | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. | 4 months | Procedure for chemical handling, storage are already developed & implemented. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Hazardous Materials | Chemicals handling | Unsafe handling procedures at printing areas at 2nd floor Building-02. Large amounts of chemicals in production area at 2nd floor Building-02. | Implement the chemical handling strategy on site as agreed with Accord. | F32 + 4 months | Procedure for chemical handling, storage are already developed & implemented. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Hazardous Materials | Chemicals storage | Main chemical store is not fire separated from dying & accessories store at ground floor Building-01. Inadequate ventilation of chemical storage areas at ground floor Building-01. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all chemical storage areas Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) Ventilation provisions to each of these rooms | 4 months | 1. Survey of the storage areas has been conducted to identify the gap. 2. Same will be incorporated in drawings for further sharing with Accord Team. 3. Upon review/approval by Accord Team, estimated cost will be shared for the review/approval by the management along with timelines to complete the job. 4. Same will be shared with Accord Team for review. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Hazardous Materials | Chemicals storage | Main chemical store is not fire separated from dying & accessories store at ground floor Building-01. Inadequate ventilation of chemical storage areas at ground floor Building-01. | Implement the above plan on site. All chemical storage areas to be compliant with Accord Standard. | F34 + 4 months | 1. Survey of the storage areas has been conducted to identify the gap. 2. Same will be incorporated in drawings for further sharing with Accord Team. 3. Upon review/approval by Accord Team, estimated cost will be shared for the review/approval by the management along with timelines to complete the job. 4. Same will be shared with Accord Team for review. |  |  |  | In Progress
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Sprinkler system Inadequate records of maintenance of Standpipes Inadequate records of maintenance of Fire Extinguishers | Prepare maintenance schedule for all life safety systems. | 3 months | Already in practice & maintained by fire team. |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Sprinkler system Inadequate records of maintenance of Standpipes Inadequate records of maintenance of Fire Extinguishers | Prepare a schedule of proposed system maintenance. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | Already in practice & maintained by fire team. |  |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Sprinkler system Inadequate records of maintenance of Standpipes Inadequate records of maintenance of Fire Extinguishers | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep maintenance records. | F37 + 3 months | Already in practice & maintained by fire team. |  |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps Inadequate records of testing of Sprinkler system Inadequate records of testing of Standpipes Inadequate records of testing of Fire Extinguishers | Prepare testing schedule for all life safety systems. | 3 months | Already in practice & maintained by fire team. |  |  |  | In Progress
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps Inadequate records of testing of Sprinkler system Inadequate records of testing of Standpipes Inadequate records of testing of Fire Extinguishers | Prepare a schedule of proposed system testing. Identify how systems will be tested and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | Already in practice & maintained by fire team. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Fire Safety Management | Records of system testing | Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Sprinkler system Inadequate records of maintenance of Standpipes Inadequate records of maintenance of Fire Extinguishers | Ensure all systems are being tested as per the schedule agreed with Accord. Keep testing records. | F40 + 3 months | Already in practice & maintained by fire team. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels. There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. | 2 months | Already in practice & maintained by fire team. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F43 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels. There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. | F42 + 2 months | Already in practice & maintained by fire team. |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
8 & 9-Jul-2024
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [12 empty] | Feroze 1888 Mills Limited, Plot No. H‐23/4A, Scheme No.3, Landhi Industrial Area, Karachi, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 8 & 9-Jul-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building B-450 sq columns were found to be potentially overstressed. We note incomplete drawings and unusual vertical load path were observed in this building also. | Verify in-situ reinforcement by carrying out ferro-scanning and by chipping away cover to two sides of a column reinforcement and confirming no. and diameter of bars and submit results to Accord with pictorial evidence. | 3 months | Structure Engineer visit Identification of columns for Ferro scan Review and Approval of columns for Ferro scan Selection of vendors Work award Ferro scan Result and report Repair works |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building B-450 sq columns were found to be potentially overstressed. We note incomplete drawings and unusual vertical load path were observed in this building also. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns from each Building or existing cylinder strength data and submit results to Accord.. | 3 months | Structure Engineer visit Identification of columns for cores Review and Approval of columns for core Selection of vendors Work award Arrangement for works Core sample Result and report Repair works |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building B-450 sq columns were found to be potentially overstressed. We note incomplete drawings and unusual vertical load path were observed in this building also. | Factory Engineer to review design, loads and columns stresses in area identified and submit report to Accord for review. Note that depending on the results of these tests it may be necessary to carry out a Detailed Engineering Assessment (DEA). This will be confirmed by Accord. | S2 + 3 months | Site Inspection and sketching Develop Structure Layouts Develop analytical model Develop Design loads Develop analytical model Develop Architectural Layouts Assessment Report |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building B-450 sq columns were found to be potentially overstressed. We note incomplete drawings and unusual vertical load path were observed in this building also. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S3 + 3 months | - Site Inspection and sketching - Develop Structure Layouts - Developed Floor load plan |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building B-450 sq columns were found to be potentially overstressed. We note incomplete drawings and unusual vertical load path were observed in this building also. | Complete any remedial work identified by DEA if found to be necessary | S3 + 6 months | TBD based on S3 Scope / nature of works shall be identified based on S3 |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building C-Typical columns were found to be potentially overstressed, when accounting for water tank below the ground floor (precise location not known and not indicated on drawings). We note that cracking was observed at the ground floor in two columns also, although it is likely related to impact damage and to corrosion. | Verify in-situ reinforcement by carrying out ferro-scanning and by chipping away cover to two sides of a column reinforcement and confirming no. and diameter of bars and submit results to Accord with pictorial evidence. | 3 months | Structure Engineer visit Identification of columns for Ferro scan Review and Approval of columns for Ferro scan Selection of vendors Work award Ferro scan Result and report Repair works |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | [10 empty] | S7 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building C-Typical columns were found to be potentially overstressed, when accounting for water tank below the ground floor (precise location not known and not indicated on drawings). We note that cracking was observed at the ground floor in two columns also, although it is likely related to impact damage and to corrosion. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns from each Building or existing cylinder strength data and submit results to Accord. | 3 months | - Structure Engineer visit - Identification of columns for cores - Review and - Approval of columns for core - Selection of vendors - Work award - Arrangement for works - Core sample - Result and report - Repair works |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | [10 empty] | S8 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building C-Typical columns were found to be potentially overstressed, when accounting for water tank below the ground floor (precise location not known and not indicated on drawings). We note that cracking was observed at the ground floor in two columns also, although it is likely related to impact damage and to corrosion. | Factory Engineer to review design, loads and columns stresses in area identified and submit report to Accord for review. Note that depending on the results of these tests it may be necessary to carry out a Detailed Engineering Assessment (DEA). This will be confirmed by Accord. | S7 + 3 months | - Site Inspection and sketching - Develop Structure Layouts - Develop analytical model - Develop Design loads - Develop analytical model - Develop Architectural Layouts - Assessment Report |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S9 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building C-Typical columns were found to be potentially overstressed, when accounting for water tank below the ground floor (precise location not known and not indicated on drawings). We note that cracking was observed at the ground floor in two columns also, although it is likely related to impact damage and to corrosion. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S8 + 3 months | - Site Inspection and sketching - Develop Structure Layouts - Developed Floor load plan |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S10 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building C-Typical columns were found to be potentially overstressed, when accounting for water tank below the ground floor (precise location not known and not indicated on drawings). We note that cracking was observed at the ground floor in two columns also, although it is likely related to impact damage and to corrosion. | Complete any remedial work identified by DEA if found to be necessary | S8 + 6 months | TBD based on S8 Scope / nature of works shall be identified based on S8 |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S11 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building D-Typical columns were found to be potentially overstressed this is related to large grids and age of the building. | Verify in-situ reinforcement by carrying out ferro-scanning and by chipping away cover to two sides of a column reinforcement and confirming no. and diameter of bars and submit results to Accord with pictorial evidence. | 3 months | Structure Engineer visit Identification of columns for Ferro scan Review and Approval of columns for Ferro scan Selection of vendors Work award Ferro scan Result and report Repair works |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S12 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building D-typical columns were found to be potentially overstressed this is related to large grids and age of the building. | carry out tensile strength testing on rebar taken from column stubs on the roof | 3 months | Based on S11 results if required Exposing the required bar Cutting sample and sending to Lab Lab testing and report |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S13 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building D-Typical columns were found to be potentially overstressed this is related to large grids and age of the building. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns from each Building or existing cylinder strength data and submit results to Accord. | 3 months | - Structure Engineer visit - Identification of columns for cores - Review and - Approval of columns for core - Selection of vendors - Work award - Arrangement for works - Core sample - Result and report - Repair works |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S14 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building D-Typical columns were found to be potentially overstressed this is related to large grids and age of the building. | Factory Engineer to review design, loads and columns stresses in area identified and submit report to Accord for review. Note that depending on the results of these tests it may be necessary to carry out a Detailed Engineering Assessment (DEA). This will be confirmed by Accord. | S13 + 3 months | - Design loads and criteria shared for review |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S15 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building D-Typical columns were found to be potentially overstressed this is related to large grids and age of the building. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S14 + 3 months | Site Inspection and sketching Develop As-built Develop Design loads Develop analytical model Develop floor load plans |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S16 | Potential Overstress | Highly stressed columns | This observation concerns potential overstress of columns, based upon loading observed and assumptions made. We note that this observation concerns building which are older and for which concrete strength data was unavailable. Building D-Typical columns were found to be potentially overstressed this is related to large grids and age of the building. | Complete any remedial work identified by DEA if found to be necessary | S14 + 6 months | - TBD on review of design criteria and tests based on S14 |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S17 | Cracking | Column | This observation concerns cracking to three columns in Building C. • The first column had a vertical crack running close to one edge at around mid-height of the column. The plaster was chipped away, and the rebar was found to be corroded. It is likely that this crack was due to corrosion. • A second column was found to have damage close to the floor level, with plaster coming away and damage to the column itself. The factory team suggested that this damage was due to impact. The level of damage would suggest repeated and forceful impact. • A third column was found to have a vertical crack running close to one edge towards its base | Carry out thorough check of all columns in Building C ground floor to check for cracks | 3 months | - Visit by Structure Engineer - Site Visit / Inspection report |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S18 | Cracking | Column | This observation concerns cracking to three columns in Building C. • The first column had a vertical crack running close to one edge at around mid-height of the column. The plaster was chipped away, and the rebar was found to be corroded. It is likely that this crack was due to corrosion. • A second column was found to have damage close to the floor level, with plaster coming away and damage to the column itself. The factory team suggested that this damage was due to impact. The level of damage would suggest repeated and forceful impact. • A third column was found to have a vertical crack running close to one edge towards its base | Structural engineer to carry out a detailed assessment of the columns affected to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar and submit to Pakistan Accord for review. | 3 months | - Site Inspection and sketching - Develop Structure Layouts - Develop analytical model - Develop Design loads - Develop analytical model - Develop Architectural Layouts |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S19 | Cracking | Column | This observation concerns cracking to three columns in Building C. • The first column had a vertical crack running close to one edge at around mid-height of the column. The plaster was chipped away, and the rebar was found to be corroded. It is likely that this crack was due to corrosion. • A second column was found to have damage close to the floor level, with plaster coming away and damage to the column itself. The factory team suggested that this damage was due to impact. The level of damage would suggest repeated and forceful impact. • A third column was found to have a vertical crack running close to one edge towards its base | Propose measures to prevent future damage and to repair the existing damage and submit to Accord for approval | S18 + 1 month | - Identification of root cause - Propose measures - Preparation of repair work methodology |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Cracking | Column | This observation concerns cracking to three columns in Building C. • The first column had a vertical crack running close to one edge at around mid-height of the column. The plaster was chipped away, and the rebar was found to be corroded. It is likely that this crack was due to corrosion. • A second column was found to have damage close to the floor level, with plaster coming away and damage to the column itself. The factory team suggested that this damage was due to impact. The level of damage would suggest repeated and forceful impact. • A third column was found to have a vertical crack running close to one edge towards its base | Carry out remedial works | S19 + 3 months | - All the identified crack are repaired & rectified as per methodology. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Structural System | Vertical load path | This concerns the vertical load path of Building B which was observed to have an irregular and discontinuous column grid, with additional steel and RC columns at mezzanine floor, which were not present at the floors above or below. It was unclear why these columns had been added. It was also unclear whether the beams/slab which were supporting these additional columns had been designed/checked for the point load they will apply. We have only received a drawing for the third floor of Building B and so are unable to review whether this is captured on the drawings. | Structural engineer to review the vertical load path for the building, in particular for columns which are not carried down to the foundations, to confirm the design is adequate and submit to Pakistan Accord for Review. | 3 months | - Site Inspection and sketching - Develop Structure Layouts - Develop analytical model - Develop Design loads - Develop analytical model - Review of framing system - Preparation and submission of report |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S22 | Structural System | Vertical load path | This concerns the vertical load path of Building B which was observed to have an irregular and discontinuous column grid, with additional steel and RC columns at mezzanine floor, which were not present at the floors above or below. It was unclear why these columns had been added. It was also unclear whether the beams/slab which were supporting these additional columns had been designed/checked for the point load they will apply. We have only received a drawing for the third floor of Building B and so are unable to review whether this is captured on the drawings. | Structural engineer to confirm that the drawings reflect the as-built condition and share a full set accordingly to Pakistan Accord | S21 + 3 months | - Site Inspection and sketching - Develop As-built layout |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S23 | Structural System | Lateral stability system | This observation concerns Buildings B, where the structural stability system varies between flat slab to moment frame. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. Building B –A 4 story structure, a combination of flat slab with some beams provided at boundary movement joints. | Building structural engineer to review the as-built design, carry out a stability analysis and confirm if the stability system is adequate. Propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 3 months | Phase 1: Site Inspection and sketching Develop Structure Layouts Develop analytical model Develop Design loads Develop analytical model Develop Architectural Layouts Model assessment and review of design Phase 2: Propose stability procedure and systems Timeline T.B.D based on Phase 1 design review |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S24 | Structural System | Lateral stability system | This observation concerns Buildings B, where the structural stability system varies between flat slab to moment frame. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. Building B–A 4 story structure, a combination of flat slab with some beams provided at boundary movement joints. | Implement strengthening works as required. | S23 + 3 months | - TBD after structure design analysis and review in S23 |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S25 | Structural System | Lateral stability system | This observation concerns Buildings C, where the structural stability system varies between flat slab to moment frame. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. Building C – A 5 story structure, consists of flat slab construction at ground and first floor and the floors above consist of RC moment frame (beam and columns). | Building structural engineer to review the as-built design, carry out a stability analysis and confirm if the stability system is adequate. Propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 3 months | Phase 1: Site Inspection and sketching Develop Structure Layouts Develop analytical model Develop Design loads Develop analytical model Develop Architectural Layouts Model assessment and review of design Phase 2: Propose stability procedure and systems Timeline T.B.D based on Phase 1 design review |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S26 | Structural System | Lateral stability system | This observation concerns Buildings C, where the structural stability system varies between flat slab to moment frame. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. Building C – A 5 story structure, consists of flat slab construction at ground and first floor and the floors above consist of RC moment frame (beam and columns). | Implement strengthening works as required. | S25 + 3 months | - TBD based on structure design analysis in S25 |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S27 | Other Damage/Defects | Spalling concrete | Spalling concrete was observed in a number of locations as described below. Where a potential cause was seen this has been described below also. • Part 6-10 Roof – Column rebar is exposed to weathering in a number of locations across the roof. Over time this will allow water ingress into columns degrading their condition and capacity. It is noted that the intention is to provide a steel roof in future, which should serve to protect the columns from weathering. | For each instance of corrosion/spalling: Propose measures to prevent further water damage Inspect damage and propose repairs to structure Submit report capturing above to Accord for approval | 3 months | Data Sheet of coating attached Proof of coating work attached |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S28 | Other Damage/Defects | Spalling concrete | Spalling concrete was observed in a number of locations as described below. Where a potential cause was seen this has been described below also. • Part 6-10 Roof – Column rebar is exposed to weathering in a number of locations across the roof. Over time this will allow water ingress into columns degrading their condition and capacity. It is noted that the intention is to provide a steel roof in future, which should serve to protect the columns from weathering. | Implement reviewed works. Continue to monitor for future signs of water ingress/damage | S27 + 3 months | - Preparation & Approval of building inspection criteria - Annual inspection of building |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S29 | Other Damage/Defects | Spalling concrete | Spalling concrete was observed in a number of locations as described below. Where a potential cause was seen this has been described below also. • Building A/B external walkways – The cantilever slabs have spalled with corroded rebar now visible. This is likely due to insufficient waterproofing. | For each instance of corrosion/spalling: Propose measures to prevent further water damage Inspect damage and propose repairs to structure Submit report capturing above to Accord for approval | 3 months | Vendor selection Mobilization & work arrangements Repair work as per approved methodology |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S30 | Other Damage/Defects | Spalling concrete | Spalling concrete was observed in a number of locations as described below. Where a potential cause was seen this has been described below also. • Building A/B external walkways – The cantilever slabs have spalled with corroded rebar now visible. This is likely due to insufficient waterproofing. | Implement reviewed works. Continue to monitor for future signs of water ingress/damage | S29 + 3 months | - Preparation & Approval of building inspection criteria - Annual inspection of building |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S31 | Other Damage/Defects | Spalling concrete | Spalling concrete was observed in a number of locations as described below. Where a potential cause was seen this has been described below also. • Building D roof – inverted roof beams were showing some small signs of corrosion. It was not possible to inspect the whole roof due to the height of the inverted beams. • Building D roof – column stubs were badly cracked as a result of rebar corrosion, with some bars completely exposed. This is due to insufficient waterproofing. • Building D roof – water damage was observed around the water tank at roof level, this is likely a result of water leaking through the tank itself. • Building D level 1 – spalling was observed to the concrete slab. This is likely due to the age of the structure (constructed around 2001) and may also be related to insufficient cover when constructed. | For each instance of corrosion/spalling: Propose measures to prevent further water damage Inspect damage and propose repairs to structure Submit report capturing above to Accord for approval | 3 months | - Site Inspection report for inverted beams / repair work where required. - Removal of loose concrete / Repair of column stubs - Inspection of tank structure - Identify points and apply repair plugs - Slab repair work to maintain cover |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S32 | Other Damage/Defects | Spalling concrete | Spalling concrete was observed in a number of locations as described below. Where a potential cause was seen this has been described below also. • Building D roof – inverted roof beams were showing some small signs of corrosion. It was not possible to inspect the whole roof due to the height of the inverted beams. • Building D roof – column stubs were badly cracked as a result of rebar corrosion, with some bars completely exposed. This is due to insufficient waterproofing. • Building D roof – water damage was observed around the water tank at roof level, this is likely a result of water leaking through the tank itself. • Building D level 1 – spalling was observed to the concrete slab. This is likely due to the age of the structure (constructed around 2001) and may also be related to insufficient cover when constructed. | Implement reviewed works. Continue to monitor for future signs of water ingress/damage | S31 + 3 months | - Preparation & Approval of building inspection criteria - Annual inspection of building |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S33 | Other Damage/Defects | Corrosion of structural steel | This observation concerns severe corrosion of a number of steel tanks which form part of the ETP. The tank roofs had corroded away in a number of places, with the most serve locations leading to partial collapse of the roof. | Confirm extent of corrosion and replace affected areas. | 3 months | - Replacement of tank |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S34 | Other Damage/Defects | Column impact damage | Building D, First floor – a column was found to be damaged at floor level and at mid height. • At floor level one of the corners of the column has been broken away exposing the aggregate. It is likely this is due to impact damage. • At mid-height a patch of the columns surface has entirely broken away, again exposing the aggregate. It is unclear what the cause of this damage might be. | Break away any loose/damaged concrete and repair the column and submit to Pakistan Accord with pictorial evidence | 3 months | - Inspection to assess damage and repair works - Apply repair mortar as per methodology |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S35 | Other Damage/Defects | Column impact damage | Building D, First floor – a column was found to be damaged at floor level and at mid height. • At floor level one of the corners of the column has been broken away exposing the aggregate. It is likely this is due to impact damage. • At mid-height a patch of the columns surface has entirely broken away, again exposing the aggregate. It is unclear what the cause of this damage might be. | Install impact protection to prevent further damage in future and submit to Pakistan Accord with pictorial evidence. | S34 + 3 months | - Review requirement for impact protection - Install missing column protection |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S36 | Structural Documentation | Lack of safe load plans | This observation concerns all buildings in the factory. No safe load plans posted in the factory. Loading plans and sections were made available as part of the documentation that was shared for newer construction, but were unavailable for Buildings A-D. Where loading plans were available, they were not posted on the floors in the factory. | Building structural engineer to review design documentation to confirm load capacity of the structure. Factory to post safe load plans on each floor and submit to Pakistan Accord with pictorial evidence. | 6 months | - Preparation of load plans of old building - Load plans to be posted on floors - Preparation of As-built floor plans - Review load plans against As-built floor plan |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S37 | Structural Documentation | Documentation unavailable | The following design documentation was not available/shared with us: • Structural building sections for all buildings • Plans for Buildings B and C shared were incomplete (plans for some floors were missing) | Building Structural Engineer to review existing design documentation for gaps and share with Pakistan Accord for review. | 6 months | - To be completed after S3 and S8 |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S38 | Structural Documentation | Documentation unavailable | The following design documentation was not available/shared with us: • Structural building sections for all buildings • Plans for Buildings B and C shared were incomplete (plans for some floors were missing) | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation accordingly | 6 months | Detail visit of each floor Review and compare as-built with floor plan Prepare / amend as-built drawings |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S39 | Other Damage/Defects | Health and Safety | This observation concerns missing edge protection in the locations described below. This presents a health and safety falling hazard for workers in these areas. • Part 6 to 10 – Temporary edge protection to slab edge is provided in some but not all places. | Install edge protection in locations identified above | 1 month | Edge protection at identified location installed. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S40 | Other Damage/Defects | Health and Safety | This observation concerns missing edge protection in the locations described below. This presents a health and safety falling hazard for workers in these areas. • Part 3 and 4 - Edge protection to roof by access stair is incomplete | Install edge protection in locations identified above | 1 month | Edge protection at identified location installed. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S41 | Other Damage/Defects | Health and Safety | This observation concerns missing edge protection in the locations described below. This presents a health and safety falling hazard for workers in these areas. • Powerhouse first floor – opening in wall with no edge protection | Install edge protection in locations identified above | 1 month | Edge protection at identified location installed. |  |  |  | In Progress

## E Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Fixtures
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## F Categories
Categories | Means of Escape | Fire Rated Construction | Hazardous Materials | Fire Suppression | Fire Safety Management
Means of Escape | Protection of stairs | Structural fire rating | Chemicals handling | Standpipe system | Fire drills
Fire Rated Construction | Number of exits | Extensive voids | Chemicals storage | Fire extinguishers | Records of systems maintenance
Fire Suppression | Travel distance | Separation of high-risk areas | Diesel storage | Fire pumps | Records of system testing
Hazardous Materials | Exit capacity | Separation of shafts | Gas storage | Sprinkler system | Staff training
Fire Safety Management | Exit access | Separation of occupancies |  | Water supply | Emergency Action Plan
| Escape stair condition | Floor openings |  | Exterior hydrants | Fire vehicle access
| Exit discharge | Storage
| Escape doors | Atrium
Exit signage
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## S Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Leaking Pipes
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type