## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
2024-07-10
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Gadoon Textile Mills Ltd. (Knits Division) - 57 Km Milestone, near Lucky Cement, beside Edhi Village, Superhighway, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2024-07-10
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-06-03 | 2025-07-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. | Develop comprehensive electrical layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-07-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E2 + 2 months | 2026-01-29 | 2026-03-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Sub-station room layout drg | substation room layout drawings were not available for the factory. | Develop detailed substation room layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Sub-station room layout drg | substation room layout drawings were not available for the factory. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E4 + 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Single Line Diagram (SLD) | electrical single-line diagrams (SLDs) for the factory were missing several information. | Develop comprehensive electrical single-line diagrams for the entire facility following the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-07-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Single Line Diagram (SLD) | electrical single-line diagrams (SLDs) for the factory were missing several information. | Implement a regular review and update process for the single-line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E6 + 2 months | 2026-01-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | Multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. This issue was observed in LT Room and production area. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current carrying capacity. If the breaker has adjustable settings, it must be configured to allow current within the cable ampacity after applying derating factors. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. This issue was observed in production department Building 1. | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring the safe and reliable operation of the electrical systems. Thermography records should be maintained that comply with the standards. | 6 months | 2025-07-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. This issue was observed in production department Building 1. | Regular thermographic inspections should be incorporated into the maintenance schedule after 6 months to proactively manage and mitigate the risks associated with overheating. | E9 + 1 months | 2026-01-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Earthing system | It was noted that the earth bar was incorrectly connected to the neutral bar, indicating improper grounding practices. This issue was observed in front of LT Room. | Disconnect the earth bars from the neutral bars with the distribution boards and ensure proper separation and connection. | 1 month | 2025-07-29 | 2025-08-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | Earth bars and termination bolts were rusted. This issue was observed in front of LT Room. | Replace the rusted bolts and bars with new ones. | E11 + 1 month | 2025-08-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | Bare copper was exposed to an open environment. | Make sure bare copper is covered and not exposed openly. | 2 months | 2025-07-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | Cable trays were not bonded. This issue was observed in front of LT Room. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. Earthing layout diagram should be developed for a better understanding of how the network is being spread throughout the facility. | 2 months | 2025-07-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | Cable trays were not bonded. This issue was observed in front of LT Room. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E14 + 1 month | 2025-09-29 | 2025-10-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Multiple Connections | Multilooping was observed in several electrical panels across the facility. This issue was observed in office area. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each circuit following Section 430 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels, and trunking systems. This issue was observed in LT Room and production department. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint following Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 months | 2025-07-29 | 2025-08-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels, and trunking systems. This issue was observed in LT Room and production department. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E17 + 1 month | 2025-08-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was observed that no lightning protection system was installed, and there was no risk assessment provided to confirm whether it was not required. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 2 months | 2025-07-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was observed that no lightning protection system was installed, and there was no risk assessment provided to confirm whether it was not required. | If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). | E19 + 6 months | 2025-09-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | For Building 1: - Office area detection was inactive. - No design documentation was present at the time of inspection - Heat detectors were installed in the basement area. | Make sure the existing system is fully functional. | 1 months | 2025-07-29 | 2025-08-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | For Building 1: - Office area detection was inactive. - No design documentation was present at the time of inspection - Heat detectors were installed in the basement area. | Submit the complete design documentation of the existing system for Accord review. After reviewing complete submit all, Accord will decide that how much compliant system and equipment is installed. If found non-listed, the whole system will be replaced with listed one. | E21 + 3 months | 2025-08-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | FADS was not installed in Building 2. | Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | FADS was not installed in Building 2. | Submit documentation to the Pakistan Accord showing that an L/C has been opened for the import of any components required for the FADS design submitted earlier. | E23 + 1 months | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | FADS was not installed in Building 2. | Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E24 + 4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | FADS was not installed in Building 2. | Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E25 + 5 months | 2026-03-29 | 2026-08-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | FADS was not installed in Building 2. | Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E26 + 3 months | 2026-08-29 | 2026-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | FADS was not installed in Building 2. | Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E27 + 3 months | 2026-11-29 | 2027-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | Emergency Lighting | No emergency lighting | emergency lighting was not installed in several areas within the facility. | To address the lack of emergency lighting in the facility, emergency lighting systems should be designed and installed following the Building Code of Pakistan Fire Safety Provisions 2016. This includes ensuring proper placement in all egress routes and compliance with specified illumination and battery backup standards. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | Emergency Lighting | No emergency lighting | emergency lighting was not installed in several areas within the facility. | Maintain comprehensive records of all installations, tests, and maintenance activities. Train facility personnel on the operation and maintenance of emergency lighting systems to ensure prompt identification and resolution of any issues. | E29 + 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | Emergency Lighting | Independent power source | emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-07-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Emergency Lighting | Independent power source | emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E31 + 1 months | 2026-01-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables. This issue was observed in LT Room and on Building 2 roof. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables. This issue was observed in LT Room and on Building 2 roof. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | E33 + 1 months | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Cabling & Wiring | Cables support and protection | Numerous loose connections were identified. This issue was observed in LT Room and on Building 2 roof. | Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). | 1 months | 2025-07-29 | 2025-08-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Cabling & Wiring | Cables support and protection | Numerous loose connections were identified. This issue was observed in LT Room and on Building 2 roof. | Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices. | E35 + 1 months | 2025-08-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Cabling & Wiring | Splicing of cables | cable terminations within panels and switchgear were made without cable lugs. This issue was observed in office area. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-07-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Cabling & Wiring | Splicing of cables | cable terminations within panels and switchgear were made without cable lugs. This issue was observed in office area. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 2 months | 2025-07-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Cabling & Wiring | Cable trench and channel cleanliness | cleanliness of the cable trunking system had not been maintained. This issue was observed in VCB and Transformer Room. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 1 months | 2025-07-29 | 2025-08-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Cabling & Wiring | Cable trench and channel cleanliness | cleanliness of the cable trunking system had not been maintained. This issue was observed in VCB and Transformer Room. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 1 months | 2025-07-29 | 2025-08-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5
| 3 | 8 |  | 352 | 421 | 6 | 5
| 3 | 8 |  | 353 | 421 | 6 | 5
| 3 | 8 |  | 354 | 421 | 6 | 5
| 3 | 8 |  | 355 | 421 | 6 | 5
| 3 | 8 |  | 356 | 421 | 6 | 5
| 3 | 8 |  | 357 | 421 | 6 | 5
| 3 | 8 |  | 358 | 421 | 6 | 5
| 3 | 8 |  | 359 | 421 | 6 | 5
| 3 | 8 |  | 360 | 421 | 6 | 5
| 3 | 8 |  | 361 | 421 | 6 | 5
| 3 | 8 |  | 362 | 421 | 6 | 5
| 3 | 8 |  | 363 | 421 | 6 | 5
| 3 | 8 |  | 364 | 421 | 6 | 5
| 3 | 8 |  | 365 | 421 | 6 | 5
| 3 | 8 |  | 366 | 421 | 6 | 5
| 3 | 8 |  | 367 | 421 | 6 | 5
| 3 | 8 |  | 368 | 421 | 6 | 5
| 3 | 8 |  | 369 | 421 | 6 | 5
| 3 | 8 |  | 370 | 421 | 6 | 5
| 3 | 8 |  | 371 | 421 | 6 | 5
| 3 | 8 |  | 372 | 421 | 6 | 5
| 3 | 8 |  | 373 | 421 | 6 | 5
| 3 | 8 |  | 374 | 421 | 6 | 5
| 3 | 8 |  | 375 | 421 | 6 | 5
| 3 | 8 |  | 376 | 421 | 6 | 5
| 3 | 8 |  | 377 | 421 | 6 | 5
| 3 | 8 |  | 378 | 421 | 6 | 5
| 3 | 8 |  | 379 | 421 | 6 | 5
| 3 | 8 |  | 380 | 421 | 6 | 5
| 3 | 8 |  | 381 | 421 | 6 | 5
| 3 | 8 |  | 382 | 421 | 6 | 5
| 3 | 8 |  | 383 | 421 | 6 | 5
| 3 | 8 |  | 384 | 421 | 6 | 5
| 3 | 8 |  | 385 | 421 | 6 | 5
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
10-Jul-2024
Corrective Action Plan - Fire
Gadoon Textile Mills Ltd. (Knits Division) - 57 Km Milestone, near Lucky Cement, beside Edhi Village, Superhighway, Karachi, Sindh, Pakistan
[9 empty] | Factory Name & Address | [13 empty] | 10-Jul-2024
Date of Initial Inspection
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-06-03 | 2025-07-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in Building 1 basement via ramp and Building 3 Kitchen and Canteen. - Sliding door observed in Building 1 escape towards Building 3. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. Replace all security gates along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | 2 weeks | 2025-07-29 | 2025-08-12 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in Building 1 basement via ramp and Building 3 Kitchen and Canteen. - Sliding door observed in Building 1 escape towards Building 3. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in Building 1 basement via ramp and Building 3 Kitchen and Canteen. - Sliding door observed in Building 1 escape towards Building 3. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3+3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways Building 1 S1 and Building 2 S1 are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Protection of stairs | Exit stairways Building 1 S1 and Building 2 S1 are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. - All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. - Where stairs discharge within a building, a fire separated corridor shall be provided that leads outside building. | F5+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Exit access | Protected stair S1 Building 1 discharge inside the building at a distance from building exit. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge routes. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Exit access | Protected stair S1 Building 1 discharge inside the building at a distance from building exit. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Accord Building Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into exit discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge routes need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F7+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Number of exits | Single exit from level 1 and 2 of Building 2 occupied floors, whereas the layout shows two more staircase S2 and S3 not currently constructed, and the floors are occupied. | Review each floor and area to ensure that the number of exits complies with Accord Building Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Accord for review and approval prior to commencing rectification works. | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Number of exits | Single exit from level 1 and 2 of Building 2 occupied floors, whereas the layout shows two more staircase S2 and S3 not currently constructed, and the floors are occupied. | Implement the above plan as agreed with Accord. Exit numbers from all floors and parts of the building should comply with Accord Building Standard. | F9+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Travel distance | Common Path Travel distance to the nearest of exit exceeds distance limits in Building 2 level 1 and 2. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Travel distance | Common Path Travel distance to the nearest of exit exceeds distance limits in Building 2 level 1 and 2. | Implement the plan previously reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F11+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Exit signage | Missing exit signage on exit doors, throughout floors and final exit to building and premises, in Building 1 and 2. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Exit signage | Missing exit signage on exit doors, throughout floors and final exit to building and premises, in Building 1 and 2. | Ensure that all exit signage is checked periodically and in good working condition. | F13+3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Fire Rated Construction | Separation of shafts | The lift shafts have unprotected opening in production floors in Building 2. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Fire Rated Construction | Separation of shafts | The lift shafts have unprotected opening in production floors in Building 2. | Ensure that the proposed design modifications are implemented and operational on site. | F15+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Fire Rated Construction | Separation of occupancies | - Basement is not fire separated from the production on ground floor of Building 1. - Building 1 office block has open ceiling to production and doors are not fire doors which makes it not fire separated from the production areas in Building 1. - Building 1 executive reception is not fire separated from the production and fire doors are missing. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Fire Rated Construction | Separation of occupancies | - Basement is not fire separated from the production on ground floor of Building 1. - Building 1 office block has open ceiling to production and doors are not fire doors which makes it not fire separated from the production areas in Building 1. - Building 1 executive reception is not fire separated from the production and fire doors are missing. | Ensure that the above plan is implemented on site. | F17+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Fire Rated Construction | Floor openings | Open void used as chute connecting basement and level ground in Building 1. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Floor openings | Open void used as chute connecting basement and level ground in Building 1. | Ensure that the above plan is implemented on site. | F19+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Storage | Dedicated storage area not separated by fire rated construction in Building 1. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-07-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Storage | Dedicated storage area not separated by fire rated construction in Building 1. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F21+4 months | 2025-11-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-07-29 | 2025-09-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F23+2 months | 2025-09-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
2024-07-10
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Gadoon Textile Mills Ltd. (Knits Division) - 57 Km Milestone, near Lucky Cement, beside Edhi Village, Superhighway, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 10-Jul-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-06-03 | 2025-07-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Structural System | Lack of local stability | This is related to the loading platform of Building 2. The stability system of platform seems insufficient, as this is supported by only single slender column. | Building Engineer to review design of platform and propose any strengthening measures as required. The remediation proposal must be submitted to Accord for approval before implementation. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Structural System | Lack of local stability | This is related to the loading platform of Building 2. The stability system of platform seems insufficient, as this is supported by only single slender column. | Implement the approved remediation proposal as required. | S2+ 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Other Damage/Defects | Spalling concrete | The concrete of Roof slab of Main production building was spalling at multiple locations due to lack of waterproofing on the roof. Standing water was observed on the roof during the inspection as a result of inadequate drainage. | Building Engineer to inspect the area and propose waterproofing measures to prevent further damage occurring as well as beam repair/remedial work. The remediation proposal must be submitted to Accord for approval before implementation. | 3 months | 2025-07-29 | 2025-10-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Other Damage/Defects | Spalling concrete | The concrete of Roof slab of Main production building was spalling at multiple locations due to lack of waterproofing on the roof. Standing water was observed on the roof during the inspection as a result of inadequate drainage. | Factory to implement the approved remedial work. Continue to monitor for signs of future water damage. | S4+ 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Structural Documentation | Lack of safe load plans | No safe load plans posted in the factory. | Building Structural Engineer to produce loading plans for all floors within the factory considering floor capacity and column capacity. Loading to be actively managed by Factory Management. | 6 months | 2025-07-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Other Damage/Defects | Health and Safety | This relates to the Building 1 Warehouse. The lack of a masonry wall on the first floor adjacent to the cargo loading deck creates a significant fall risk for workers. | Provide adequate edge protection. | 1 month | 2025-07-29 | 2025-08-29 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1