## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
21-Apr-2025
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Gul Ahmed Textile Mills Ltd. - Plot No.'s 368, 369, Main National Highway, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 21-Apr-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-31 | 2025-09-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There were no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There were no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2+6 months | 2025-12-25 | 2026-06-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but not up to date and detailed for overall facility, also there were missing necessary details such as circuit identification, cable/breaker sizes, protective devices, voltage levels, standard legends, and distribution board tags. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but not up to date and detailed for overall facility, also there were missing necessary details such as circuit identification, cable/breaker sizes, protective devices, voltage levels, standard legends, and distribution board tags. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4+6 months | 2026-03-25 | 2026-09-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings for all buildings - including small power layouts, lighting layouts, and containment layouts. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 months | 2025-09-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings for all buildings - including small power layouts, lighting layouts, and containment layouts. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6+6 months | 2026-05-25 | 2026-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. This issue was specifically observed at the following locations: - Block A main LT, where a 100A circuit breaker is connected with a 6mm² cable. - 3rd floor Block A, where a 225A circuit breaker is connected with a 35mm² cable. - Main LT Building B, where a 200A circuit breaker is connected with a 2.5mm² cable. - Block C main LT, where a 60A circuit breaker is connected with a 1.5mm² cable. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable ampacity after applying derating factors. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Hot Spots | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. This issue was specifically observed at the following locations: - Block A main LT, where a 100A circuit breaker is connected with a 6mm² cable. - 3rd floor Block A, where a 225A circuit breaker is connected with a 35mm² cable. - Main LT Building B, where a 200A circuit breaker is connected with a 2.5mm² cable. - Block C main LT, where a 60A circuit breaker is connected with a 1.5mm² cable. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards at main LT Building B MRT 01 Building C, 3rd Floor Building C and Canteen area. | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | E9 + 6 months | 2025-10-25 | 2026-04-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | It was also found that the Thermographic report was not available at the site. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | E10 + 6 months | 2026-04-25 | 2026-10-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | There was no earth design and testing report available in the facility. | Design and evaluate the earthing system installation throughout the facility. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations such as mosque. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | It was noted that the earth bar was incorrectly connected to the neutral bar in Shed E, indicating improper grounding practices. | Disconnect the earth bars from the neutral bars with the distribution boards and ensure proper separation and connection. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | Equipotential bonding for the cable trays and metallic panel covers was missing at location such as DB 02 Building A and solar panel main LT base frame. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations such as mosque. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. This issue was specifically observed at the following locations such as Building B ground floor, Building A outer area, Building D ground floor and 2nd floor Building A. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed at the following locations such as Building B ground floor, Building A outer area, Building D ground floor and 2nd floor Building A. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. This issue was specifically observed at the following locations such as Building B ground floor, Building A outer area, Building D ground floor and 2nd floor Building A. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | Inappropriately placed variable frequency drive VFD found installed inside panel. This issue was specifically observed at the following locations such as Building B ground floor, Building A outer area, Building D ground floor and 2nd floor Building A. | Ensure all equipment is installed in accordance with manufacturer guidelines, including proper placement, ventilation, and accessibility for safe and reliable operation | 2 months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed at the following locations such as Building B ground floor, Building A outer area, Building D ground floor and 2nd floor Building A. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E17 + 6 months | 2025-11-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Loop Connection | In these loop connections, one circuit breaker is energised by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. This issue was specifically observed at Building C and Shed F. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 3 Months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Multiple connections | In these cases, multiple circuits were being protected by a single circuit breaker. This issue was specifically observed at Building A DB 01 and LT panel circuit breaker. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Openings | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at LT room Building A, Shed E and F. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Openings | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at LT room Building A, Shed E and F. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was installed, but there was no risk assessment provided to confirm whether it was not required. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 2 months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was installed, but there was no risk assessment provided to confirm whether it was not required. | If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). | E25 + 6 months | 2025-11-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at LT room Building A, Shed E and F. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at LT room Building A, Shed E and F. | A regular maintenance procedure shall be establiShed to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E27 + 6 months | 2025-10-25 | 2026-04-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The facility had five fire alarm panels installed, all of which were of the conventional type. The overall fire alarm system was found to be noncompliant, utilizing outdated panels, non–fire-rated cables, and substandard hooters. Furthermore, no documentation or certification was available on-site to verify the compliance or listing of any installed equipment. Audibility across the facility was inadequate. A faulty sounder was found on the 2nd floor near the elevator. Building C had poor or no audibility at the mezzanine, roof, and in surrounding rooms of ground floor, including the main gate. Similarly, Block D showed insufficient coverage at the Canteen roof, 3rd floor checking section, and Packing Line 1. Block A’s 1st floor packing area also had poor sound levels. In Sheds E and F, very few devices were installed, resulting in weak or absent sound coverage. Device functionality issues were also noted. Smoke detectors in the metal-free zone of Building C were found inoperative. Additionally, a smoke detector in Block D failed to respond during the testing process. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 2 weeks | 2025-09-25 | 2025-10-09 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non-compliant Fire alarm and detection system found installed in the facility. | This relates to the entire facility. (1) Submit design documentation for new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non-compliant Fire alarm and detection system found installed in the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E30 + 1 month | 2025-12-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non-compliant Fire alarm and detection system found installed in the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E31 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non-compliant Fire alarm and detection system found installed in the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E32 +5 months | 2026-05-25 | 2026-10-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non-compliant Fire alarm and detection system found installed in the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E33 +3 months | 2026-10-25 | 2027-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | A non-compliant Fire alarm and detection system found installed in the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E34 + 3 months | 2027-01-25 | 2027-04-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Maintenance records | Routine testing of the Fire Alarm and Detection System (FADS) has not been performed consistently. The testing and maintenance of the Fire Alarm and Detection System (FADS) have not been conducted in accordance with the requirements specified in Chapter 14 of NFPA 72. | Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | E35 + 3 months | 2027-04-25 | 2027-07-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | General & Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations. This issue was specifically observed at Building A, Building C and Shed E. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 2 months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | General & Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations. This issue was specifically observed at Building A, Building C and Shed E. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | General & Emergency Lighting | Provided but insufficient | Several areas lack sufficient emergency lighting coverage in Building A and C. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation | 6 Months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | General & Emergency Lighting | Provided but insufficient | Multiple emergency luminaires indicate the need for maintenance Building A and C. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | 2 Months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | General & Emergency Lighting | Provided but insufficient | A central UPS was utilized to provide backup power to the emergency lighting; however, the battery autonomy was insufficient, and non-fire rated cables were used at Building A. | Upgrade the UPS system to ensure sufficient battery autonomy for providing backup power to the emergency fittings throughout the facility, and ensure installation with fire-rated cabling. | 6 Months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | General & Emergency Lighting | Provided but insufficient | External emergency lighting was not provided at external areas of Building A and C, preventing people from reaching a place of safety outside the facility during nighttime evacuations | Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s). | 2 Months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | General & Emergency Lighting | Provided but insufficient | Multiple emergency luminaires indicate the need for maintenance Building A and C. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 Months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | General & Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Proper circuitry is crucial to ensure that emergency lighting is automatically activated when general lighting fails. This automatic activation is essential for maintaining sufficient illumination, allowing for the safe evacuation of occupants and preventing panic during power outages. Further the emergency lights and exit signs be reconfigured to be connected on a dedicated single circuit | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | General & Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Proper circuitry is crucial to ensure that emergency lighting is automatically activated when general lighting fails. This automatic activation is essential for maintaining sufficient illumination, allowing for the safe evacuation of occupants and preventing panic during power outages. Further the emergency lights and exit signs be reconfigured to be connected on a dedicated single circuit | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Generator, Transformer & Sub-Station Room | Battery | During the inspection of the battery system, the battery cells, connections, and enclosures were thoroughly examined. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Generator, Transformer & Sub-Station Room | Battery | It was observed that the placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. This issue was observed at the gate office, Building A, and Building B HT Room. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. This issue was specifically observed at the following locations: - Block A 2nd floor stitching. - Block A 1st floor stitching. - Block A 1st floor packing. - Building D boiler area 4th floor (unsupported cable). - Block E quilting (noted at two separate points). | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. This issue was specifically observed at the following locations: - Block A 2nd floor stitching. - Block A 1st floor stitching. - Block A 1st floor packing. - Building D boiler area 4th floor (unsupported cable). - Block E quilting (noted at two separate points). | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at the following locations: - Block A 1F stitching, - Main trench. - Block D 2F cutting. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 2 months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at the following locations: - Block A 1F stitching, - Main trench. - Block D 2F cutting. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This issue was specifically observed at the following locations: - DB 02 Block A ground floor warehouse. - F4 DB 3 Block A. - FLIR hotspot area. - Cutting area 2nd floor. - Block A 2nd floor cutting. - Block C ground floor DB 3. - Roof C,. - Panel 6 Building C. - 2nd floor, Block C. - 4th floor sewing. - DB No. 4. - Shed F. - Warehouse area. - Maintenance workshop. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This issue was specifically observed at the following locations: - DB 02 Block A ground floor warehouse. - F4 DB 3 Block A. - FLIR hotspot area. - Cutting area 2nd floor. - Block A 2nd floor cutting. - Block C ground floor DB 3. - Roof C,. - Panel 6 Building C. - 2nd floor, Block C. - 4th floor sewing. - DB No. 4. - Shed F. - Warehouse area. - Maintenance workshop. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This issue was specifically observed at the following locations: DB 02 Block A ground floor warehouse, F4 DB 3 Block A, FLIR hotspot area, cutting area 2nd floor, Block A 2nd floor cutting, Block C ground floor DB 3, Roof C, Panel 6 Building C, 2nd floor, Block C 4th floor sewing, DB No. 4 Shed F, warehouse area, and maintenance workshop. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This issue was specifically observed at the following locations: DB 02 Block A ground floor warehouse, F4 DB 3 Block A, FLIR hotspot area, cutting area 2nd floor, Block A 2nd floor cutting, Block C ground floor DB 3, Roof C, Panel 6 Building C, 2nd floor, Block C 4th floor sewing, DB No. 4 Shed F, warehouse area, and maintenance workshop. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Cabling & Wiring | Splicing of cables | Machine power wires were inserted directly into power receptacles without a power plug. This issue was specifically observed at the following locations: DB 02 Block A ground floor warehouse, F4 DB 3 Block A, FLIR hotspot area, cutting area 2nd floor, Block A 2nd floor cutting, Block C ground floor DB 3, Roof C, Panel 6 Building C, 2nd floor, Block C 4th floor sewing, DB No. 4 Shed F, warehouse area, and maintenance workshop. | Replace the directly inserted power wires with proper power plugs to ensure safe and secure connections. | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Cabling & Wiring | Splicing of cables | Machine power wires were inserted directly into power receptacles without a power plug. This issue was specifically observed at the following locations: DB 02 Block A ground floor warehouse, F4 DB 3 Block A, FLIR hotspot area, cutting area 2nd floor, Block A 2nd floor cutting, Block C ground floor DB 3, Roof C, Panel 6 Building C, 2nd floor, Block C 4th floor sewing, DB No. 4 Shed F, warehouse area, and maintenance workshop. | Develop and enforce a facility-wide electrical safety protocol that mandates the use of power plugs for all equipment. Conduct regular safety audits and provide training sessions to staff to reinforce the importance of using proper power plugs and adherence to electrical safety standards. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. This issue was specifically observed at the following locations: DB 02, 2nd Floor Block A; F1 DB 03 Block A; Building D ground floor (green wire on phase); and E Shed main LT. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. This issue was specifically observed at the following locations: DB 02, 2nd Floor Block A; F1 DB 03 Block A; Building D ground floor (green wire on phase); and E Shed main LT. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 370 | 421 | 6 | 5 |  | Initial | [11 empty] | E60 | Cabling & Wiring | Fixtures | Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. | Replace broken and exposed power receptacles immediately to restore safe and secure connections. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 371 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Fixtures | Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. | Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E62 | Cabling & Wiring | Fixtures | Inappropriately mounted fixtures were observed, which may lead to potential electrical failure due to unstable or improper installations | Ensure all fixtures are properly mounted using standard-compliant methods to maintain electrical integrity and system reliability. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E63 | Cabling & Wiring | Fixtures | Inappropriately mounted fixtures were observed, which may lead to potential electrical failure due to unstable or improper installations. | Identify and rectify all improperly mounted fixtures across the facility and implement regular inspections to ensure continued compliance. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 374 | 421 | 6 | 5 |  | Initial | [11 empty] | E64 | Cabling & Wiring | Fixtures | Circuit breaker was found installed without a safety cover, posing a risk of accidental contact, electrical shock, or short circuit. | Install appropriate safety covers on all circuit breakers to ensure safe operation and compliance with electrical safety standards. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 375 | 421 | 6 | 5 |  | Initial | [11 empty] | E65 | Cabling & Wiring | Fixtures | Circuit breaker was found installed without a safety cover, posing a risk of accidental contact, electrical shock, or short circuit. | Conduct a facility-wide audit of all circuit breaker installations and retrofit safety covers where missing to prevent direct exposure. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 376 | 421 | 6 | 5
| 3 | 8 |  | 377 | 421 | 6 | 5
| 3 | 8 |  | 378 | 421 | 6 | 5
| 3 | 8 |  | 379 | 421 | 6 | 5
| 3 | 8 |  | 380 | 421 | 6 | 5
| 3 | 8 |  | 381 | 421 | 6 | 5
| 3 | 8 |  | 382 | 421 | 6 | 5
| 3 | 8 |  | 383 | 421 | 6 | 5
| 3 | 8 |  | 384 | 421 | 6 | 5
| 3 | 8 |  | 385 | 421 | 6 | 5
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
21-Apr-2025
Corrective Action Plan - Fire
Gul Ahmed Textile Mills Ltd. - Plot No.'s 368, 369, Main National Highway, Karachi, Sindh, Pakistan
[9 empty] | Factory Name & Address | [13 empty] | 21-Apr-2025
Date of Initial Inspection
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-31 | 2025-09-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | Most of the escape doors are lockable at Building A, Building C (5th floor & ground floor) and at Building E. Sliding doors serve for escape from areas with more than 10 occupants at Building A & Building C (ground floor). Doors is not sufficiently wide for escape (found .75m) at Building A (Mezzanine floor). | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-09-25 | 2025-10-09 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | Most of the escape doors are lockable at Building A, Building C (5th floor & ground floor) and at Building E. Sliding doors serve for escape from areas with more than 10 occupants at Building A & Building C (ground floor). Doors is not sufficiently wide for escape (found .75m) at Building A (Mezzanine floor). | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | Most of the escape doors are lockable at Building A, Building C (5th floor & ground floor) and at Building E. Sliding doors serve for escape from areas with more than 10 occupants at Building A & Building C (ground floor). Doors is not sufficiently wide for escape (found .75m) at Building A (Mezzanine floor). | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3 + 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | Obstructions on escape route at Building A (ground floor) storage hall. | Remove obstructions on escape routes and keep them clear for escape. | 2 weeks | 2025-09-25 | 2025-10-09 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Number of exits | There are areas with over 500 occupants that are only served by 2 exits at Building A & Building C (5th floor). There is only a single exit from site (On both facilities) and there is a risk it may not be available in the event of fire in the building. | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Number of exits | There are areas with over 500 occupants that are only served by 2 exits at Building A & Building C (5th floor). There is only a single exit from site (On both facilities) and there is a risk it may not be available in the event of fire in the building. | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Standard. | F6 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Protection of stairs | Unprotected openings (windows or open to production floor) into stairs S1 to S3, S10 to S12 (all floor) and S5 (3rd floor). Doors not fire doors at S4, S10, S11 & S12 (all floors), S31 & S32 (all floors). Fire load in stairs at S11 & S12 (all floors), S10 (ground floor), S4 (ground floor & 1st floor), S31 and S32 (all floors). Services passing through or within stairs S1 , S10 & S12 (all floors). | Remove fire load and any other obstruction due to stored item from stairs. | 2 weeks | 2025-09-25 | 2025-10-09 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Protection of stairs | Unprotected openings (windows or open to production floor) into stairs S1 to S3, S10 to S12 (all floor) and S5 (3rd floor). Doors not fire doors at S4, S10, S11 & S12 (all floors), S31 & S32 (all floors). Fire load in stairs at S11 & S12 (all floors), S10 (ground floor), S4 (ground floor & 1st floor), S31 and S32 (all floors). Services passing through or within stairs S1 , S10 & S12 (all floors). | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Protection of stairs | Unprotected openings (windows or open to production floor) into stairs S1 to S3, S10 to S12 (all floor) and S5 (3rd floor). Doors not fire doors at S4, S10, S11 & S12 (all floors), S31 & S32 (all floors). Fire load in stairs at S11 & S12 (all floors), S10 (ground floor), S4 (ground floor & 1st floor), S31 and S32 (all floors). Services passing through or within stairs S1 , S10 & S12 (all floors). | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F9 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Exit discharge | Stair discharge routes of S4 , S5 and S10 are not fire separated from the rest of the building. External escape routes are through high risk areas e.g. external escape from Building E is not fire separated from storage & steamer. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Pakistan Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes Provide additional exits from site. | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Exit discharge | Stair discharge routes of S4 , S5 and S10 are not fire separated from the rest of the building. External escape routes are through high risk areas e.g. external escape from Building E is not fire separated from storage & steamer. | Ensure external exit discharge routes are adequately fire separated from the rest of the building. Ensure external escape routes do not pass close to unprotected high risk areas. | F11 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Exit signage | Missing exit signs at entry into stairs at Building C (5th floor). Missing exit signs in production areas in all over the facility. Misleading exit signs at Building D (1st floor). | Remove misleading directional escape signs. | 2 weeks | 2025-09-25 | 2025-10-09 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Exit signage | Missing exit signs at entry into stairs at Building C (5th floor). Missing exit signs in production areas in all over the facility. Misleading exit signs at Building D (1st floor). | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the Floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Exit signage | Missing exit signs at entry into stairs at Building C (5th floor). Missing exit signs in production areas in all over the facility. Misleading exit signs at Building D (1st floor). | Ensure that all exit signage is checked periodically and in good working condition. | F14 + 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Fire Rated Construction | Separation of high-risk areas | Steam generator room door is not a sturdy door at Building A(1st floor) , Building C (4th floor) & Building D (2nd floor). Steam generator room doors do not have a self-closer and/or a latch at Building A(1st floor) , Building C (4th floor) & Building D (2nd floor). | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Accord for review. and approval prior to the rectification works. The drawings should cover: - Separation to electric steam generator up to 3 m above the finished floor level. This should be achieved using reinforced concrete / masonry walls with a solid steel doors. - The door must have a self-closer and a positive latch. - Blast vent should be provided to outside the building. | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Fire Rated Construction | Separation of high-risk areas | Steam generator room door is not a sturdy door at Building A(1st floor) , Building C (4th floor) & Building D (2nd floor). Steam generator room doors do not have a self-closer and/or a latch at Building A(1st floor) , Building C (4th floor) & Building D (2nd floor). | Implement the above plan on site. All buildings to be compliant with Pakistan Accord Standard. | F16 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building. Electrical rooms are not fire separated at e.g. M/c room at Building C (5th floor), Mian HV & LT rooms at front of Building C are not separated with fire rated construction. Boiler area is not fire separated from raw material store at Building D (ground floor). | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). Locations of fire rated walls and doors to protect these rooms. Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building. Electrical rooms are not fire separated at e.g. M/C room at Building C (5th floor), Mian HV & LT rooms at front of Building C are not separated with fire rated construction. Boiler area is not fire separated from raw material store at Building D (ground floor). | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F18 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction at Building A,C and D (all floors). | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors enclosing vertical shafts. Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction at Building A,C and D (all floors). | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F20 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Floor openings | Drain pipe (Pvc material) linking different levels are not fire separated at Building A & C (all floors). | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Floor openings | Drain pipe (Pvc material) linking different levels are not fire separated at Building A & C (all floors). | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F22 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Separation of occupancies | Canteen not separated from machine workshop at Building C (5th floor). | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of occupancies | Canteen not separated from machine workshop at Building C (5th floor). | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F24 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building at Building A (all floors except mezzanine floor) & Building C (Ground ,2nd , 3rd , 4th & 5th floor), Building B (ground floor & 1st floor) and Building E. Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) at Building A (3rd floor) & Building C (2nd floor). Storage in exit discharge route on front side of Building D. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors. Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building at Building A (all floors except mezzanine floor) & Building C (Ground ,2nd , 3rd , 4th & 5th floor), Building B (ground floor & 1st floor) and Building E. Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) at Building A (3rd floor) & Building C (2nd floor). Storage in exit discharge route on front side of Building D. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F26 + 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Suppression | Sprinkler system | Sprinkler system is not provided in Building A, C & Building D which is required due to height more than 18.29m. | (1) Submit design documentation for a Sprinkler system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | 2025-09-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Suppression | Sprinkler system | Sprinkler system is not provided in Building A, C & Building D which is required due to height more than 18.29m. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F28 + 1 month | 2026-01-25 | 2026-02-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Suppression | Sprinkler system | Sprinkler system is not provided in Building A, C & Building D which is required due to height more than 18.29m. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F29 + 3 months | 2026-02-25 | 2026-05-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Suppression | Sprinkler system | Sprinkler system is not provided in Building A, C & Building D which is required due to height more than 18.29m. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F30 + 4 months | 2026-05-25 | 2026-09-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Sprinkler system | Sprinkler system is not provided in Building A, C & Building D which is required due to height more than 18.29m. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F31 + 3 months | 2026-09-25 | 2026-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Suppression | Sprinkler system | Sprinkler system is not provided in Building A, C & Building D which is required due to height more than 18.29m. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete. | F32 + 3 months | 2026-12-25 | 2027-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Suppression | Standpipe system | Connection points are not compliant in Building A. Missing standpipe outlets in all stairs (Building A , C and D). | Provide standpipe system in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 18 months | 2025-09-25 | 2027-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Suppression | Fire pumps | Fire pumps are not in a fire separated room (From other utility pumps & storage of fire fighting equipment). Fire pumps installed with negative suction arrangement. | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 18 months | 2025-09-25 | 2027-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps. Inadequate records of testing of Standpipes. Inadequate records of testing of Fire Extinguishers. | Prepare a schedule of proposed system testing. Identify how systems will be tested and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps. Inadequate records of testing of Standpipes. Inadequate records of testing of Fire Extinguishers. | Ensure all systems are being tested as per the schedule agreed with Accord . Keep testing records. | F36 + 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Standpipes. Inadequate records of maintenance of Fire Extinguishers. | Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Standpipes. Inadequate records of maintenance of Fire Extinguishers. | Ensure all systems are being maintained as per the schedule agreed with Accord . Keep maintenance records. | F38 + 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Safety Management | Emergency Action Plan | There is an EAP document but it does not details procedures, roles and responsibilities in the event of fire. | Prepare an Emergency Action Plan report. | 2 months | 2025-09-25 | 2025-11-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Fire Safety Management | Emergency Action Plan | There is an EAP document but it does not details procedures, roles and responsibilities in the event of fire. | Ensure EAP is being practiced as part of fire drills. | F40 + 2 months | 2025-11-25 | 2026-01-25 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
21-Apr-2025
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Gul Ahmed Textile Mills Ltd. - Plot No.'s 368, 369, Main National Highway, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 21-Apr-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-31 | 2025-09-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | Verify insitu reinforcement by removing cover and confirming no. and diameter of bars and submit results to Pakistan Accord. | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | Verify the depth of the slab and the finishes on all floors by extracting the cores from the slab and submit the results to Pakistan Accord | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | Verify strength of reinforcement through laboratory tensile strength testing by extracting a rebar at ground floor level. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns(in presence of (Pakistan Accord engineer) or existing cylinder strength data and submit results to Pakistan Accord. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | Factory Engineer to review design, loads and columns stresses in area identified and submit to Pakistan Accord for review. | S5+ 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building, in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 2 months | 2025-07-31 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review. | S7+ 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths along with safe load plans reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | S8+ 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | (4) Submit proposals for any retrofitting work that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review | S9+ 4 months | 2026-04-30 | 2026-08-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | (5) Carry out all retrofitting work if needed as proposed and previously reviewed by Pakistan Accord. | S10 + 6 months | 2026-08-30 | 2027-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | (6) Factory to advise Pakistan Accord when all retrofitting work are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting work in accordance with previously reviewed proposals, then this item will be complete. | S11 + 1 months | 2027-02-28 | 2027-03-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of the Building A. The Internal columns of Building A are found to be overstressed based on initial assessment. The potential cause of overstressing can be larger grid sizes (7.31x 14.6) and variation in the rebars in the column. The drawing shows 36 Nos. 1"dia reinforcing bar while we scanned 24 Nos. 1" Dia reinforcing bar. | Continue to implement load plan. | S12 + 3 months | 2027-03-28 | 2027-06-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | Verify insitu reinforcement by removing cover and confirming no. and diameter of bars and submit results to Pakistan Accord. | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | Verify the depth of the slab and the finishes on all floors by extracting the cores from the slab and submit the results to Pakistan Accord. | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | Verify strength of reinforcement through laboratory tensile strength testing by extracting a rebar at ground floor level. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns(in presence of (Pakistan Accord engineer) or existing cylinder strength data and submit results to Pakistan Accord. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | Factory Engineer to review design, loads and columns stresses in area identified and submit to Pakistan Accord for review. | S17 + 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building, in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 2 months | 2025-07-31 | 2025-09-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | S19 + 3 months | 2025-09-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths along with safe load plans reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | S20 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | (4) Submit proposals for any retrofitting work that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review | S21+ 4 months | 2026-04-30 | 2026-08-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | (5) Carry out all retrofitting work if needed as proposed and previously reviewed by Pakistan Accord | S22+ 6 months | 2026-08-30 | 2027-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | (6) Factory to advise Pakistan Accord when all retrofitting work are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting work in accordance with previously reviewed proposals, then this item will be complete. | S23+ 1 months | 2027-02-28 | 2027-03-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Potential Overstress | Highly stressed columns | This refers to the internal and external columns of Building C. The internal columns of Building C appear to be overstressed against the observed load at ground floor level. The potential cause of overstressing can be larger grid sizes (7.31 x 14.6) and variation in the rebar. The drawing shows 32 Nos 1"dia reinforcing bar while we scanned 24 Nos 1"dia rebar. | Continue to implement load plan. | S24+ 3 months | 2027-03-28 | 2027-06-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S26 | Cracking | Column | The peripheral columns of building B were found to be cracked at ground floor level. The potential cause of cracking can be corrosion of reinforcement due to moisture ingress. The columns were not found to be overstressed at the ground floor level. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S27 | Cracking | Column | The peripheral columns of building B were found to be cracked at ground floor level. The potential cause of cracking can be corrosion of reinforcement due to moisture ingress. The columns were not found to be overstressed at the ground floor level. | Propose measures to prevent future damage and to repair the existing damage and submit to Pakistan Accord for review. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S28 | Cracking | Column | The peripheral columns of building B were found to be cracked at ground floor level. The potential cause of cracking can be corrosion of reinforcement due to moisture ingress. The columns were not found to be overstressed at the ground floor level. | Carry out the remedial work. | S27+ 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S29 | Cracking | Column | This refers to Building D, One column on ground floor of building D was found to be cracked. The Column is not overstressed. Potential cause of cracking can due be impact damage. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Pakistan Accord for approval. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S30 | Cracking | Column | This refers to Building D, One column on ground floor of building D was found to be cracked. The Column is not overstressed. Potential cause of cracking can due be impact damage. | Carry out the remedial work. | S29 + 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S31 | Cracking | Column | This refers to the cracking observed on the peripheral columns of Building C. The potential cause of cracking can be corrosion of reinforcement due to moisture ingress. The column is also observed to be overstressed at ground floor level. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S32 | Cracking | Column | This refers to the cracking observed on the peripheral columns of Building C. The potential cause of cracking can be corrosion of reinforcement due to moisture ingress. The column is also observed to be overstressed at ground floor level. | Propose measures to prevent future damage and to repair the existing damage. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S33 | Cracking | Column | This refers to the cracking observed on the peripheral columns of Building C. The potential cause of cracking can be corrosion of reinforcement due to moisture ingress. The column is also observed to be overstressed at ground floor level. | Carry out the remedial work. | S32+ 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S34 | Structural System | Lack of local stability | This refers to the lack of lateral stability in Building E and Building F. The lateral bracing on the sides of both the buildings appear to be missing at a few locations. The missing bracing can be the cause of reduced lateral stability against the lateral loads. | Factory to install the missing bracing cables as needed and ensure cables are tightened so that they can act in tension. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S35 | Structural System | Lateral stability system | This relates to a potential lack of structural stability system against the lateral loads in Building B. The whole building is an RC Flat slab structure with peripheral beams. The beams are generally provided for lateral stability between beams and columns. Therefore, the structure is highly vulnerable in lateral direction when subjected to lateral loads. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads). Carry out a stability analysis and confirm if the stability system is adequate. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S36 | Structural System | Lateral stability system | This relates to a potential lack of structural stability system against the lateral loads in Building B. The whole building is an RC Flat slab structure with peripheral beams. The beams are generally provided for lateral stability between beams and columns. Therefore, the structure is highly vulnerable in lateral direction when subjected to lateral loads. | Propose additional stability system if it is necessary and Submit proposals to Pakistan Accord | S35+ 1 month | 2025-12-25 | 2026-01-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S37 | Structural System | Lateral stability system | This relates to a potential lack of structural stability system against the lateral loads in Building B. The whole building is an RC Flat slab structure with peripheral beams. The beams are generally provided for lateral stability between beams and columns. Therefore, the structure is highly vulnerable in lateral direction when subjected to lateral loads. | Carry out remedial work as required. | S36+ 4 months | 2026-01-25 | 2026-05-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S38 | Other Damage/Defects | Corrosion of reinforcement | This refers to the OHWT on Building C where corrosion of reinforcement is present in the column reinforcing bars extruding from OHWT. The exposed rebars are corroded and this corrosion can lead to reduction in the capacity of the rebars. | Building engineer to propose measures to prevent further corrosion damage and submit to Pakistan Accord for review. | 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S39 | Other Damage/Defects | Corrosion of reinforcement | This refers to the OHWT on Building C where corrosion of reinforcement is present in the column reinforcing bars extruding from OHWT. The exposed rebars are corroded and this corrosion can lead to reduction in the capacity of the rebars. | Implement remedial work. | S38 + 3 months | 2025-12-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S40 | Other Damage/Defects | Corrosion of reinforcement | This refers to the OHWT on Building C where corrosion of reinforcement is present in the column reinforcing bars extruding from OHWT. The exposed rebars are corroded and this corrosion can lead to reduction in the capacity of the rebars. | Continue to monitor future signs of corrosion. | S39+3 months | 2026-03-25 | 2026-06-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S41 | Other Damage/Defects | Spalling concrete | This refer to the 4th floor of the Building A. The slab of 4th floor of the building is spalling, the potential cause of spalling can be lack of waterproofing on the 5th floor. | Identify the cause of the damage / source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S42 | Other Damage/Defects | Spalling concrete | This refer to the 4th floor of the Building A. The slab of 4th floor of the building is spalling, the potential cause of spalling can be lack of waterproofing on the 5th floor. | Inspect damage to the slab and propose repairs to structure. | 3 month | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S43 | Other Damage/Defects | Spalling concrete | This refer to the 4th floor of the Building A. The slab of 4th floor of the building is spalling, the potential cause of spalling can be lack of waterproofing on the 5th floor. | Submit report capturing above to Pakistan Accord for approval. | S42 + 1 month | 2025-12-25 | 2026-01-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S44 | Other Damage/Defects | Spalling concrete | This refer to the 4th floor of the Building A. The slab of 4th floor of the building is spalling, the potential cause of spalling can be lack of waterproofing on the 5th floor. | Implement remedial work. | S43 + 3 months | 2026-01-25 | 2026-04-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S45 | Other Damage/Defects | Spalling concrete | This refer to the 4th floor of the Building A. The slab of 4th floor of the building is spalling, the potential cause of spalling can be lack of waterproofing on the 5th floor. | Continue to monitor for future signs of water ingress/damage. | S44 + 3 months | 2026-04-25 | 2026-07-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S46 | Other Damage/Defects | Spalling concrete | This refers to the 4th floor of Building C and the inverted beams present on the roof of OHWT where the slab was spalling. The potential cause of spalling can be lack of waterproofing on the 5th floor and the OHWT. | Identify the cause of the damage / source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-09-25 | 2025-10-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S47 | Other Damage/Defects | Spalling concrete | This refers to the 4th floor of Building C and the inverted beams present on the roof of OHWT where the slab was spalling. The potential cause of spalling can be lack of waterproofing on the 5th floor and the OHWT. | Inspect damage to the slab and propose repairs to structure. | 3 month | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S48 | Other Damage/Defects | Spalling concrete | This refers to the 4th floor of Building C and the inverted beams present on the roof of OHWT where the slab was spalling. The potential cause of spalling can be lack of waterproofing on the 5th floor and the OHWT. | Submit report capturing above to Pakistan Accord for approval. | S47+ 1 month | 2025-12-25 | 2026-01-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S49 | Other Damage/Defects | Spalling concrete | This refers to the 4th floor of Building C and the inverted beams present on the roof of OHWT where the slab was spalling. The potential cause of spalling can be lack of waterproofing on the 5th floor and the OHWT. | Implement remedial work. | S48 + 3 months | 2026-01-25 | 2026-04-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S50 | Other Damage/Defects | Spalling concrete | This refers to the 4th floor of Building C and the inverted beams present on the roof of OHWT where the slab was spalling. The potential cause of spalling can be lack of waterproofing on the 5th floor and the OHWT. | Continue to monitor for future signs of water ingress/damage. | S49 + 3 months | 2026-04-25 | 2026-07-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S51 | Structural Documentation | Documentation unavailable | This refers to whole facility, the architectural drawings and the structural sections of all the buildings are not available. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[21 empty] | S52 | Structural Documentation | Differs from as-built structure | This refers to the building D where the structural drawing provided do not match the as-built site conditions. There are additional columns in the building which are marked in the architectural drawings, but the columns are missing in the structural drawings. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S53 | Structural Documentation | Lack of safe load plans | This refers to the Building A, Building B, Building C and Building D where the safe load plans were not posted on floors. | Building structural engineer to review design documentation to confirm load capacity of the structure. | 6 months | 2025-09-25 | 2026-03-25 | AGREE |  |  |  | In Progress
Initial | [8 empty] | Initial | [11 empty] | S54 | Structural Documentation | Lack of safe load plans | This refers to the Building A, Building B, Building C and Building D where the safe load plans were not posted on floors. | Factory to post safe load plans on each floor. | S53+ 1 month | 2026-03-25 | 2026-04-25 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1