## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
25-Mar-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Indus Home Limited, 2.5 Km off Manga Raiwind Road, Manga Mandi, District Kasur, Lahore, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 25-Mar-2024, 27-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | It was found that substation drawing was not available at the site. | Consult a qualified electrical engineer to provide detail as-built electrical drawings including the switchgear and other equipment including cable route, trenches, ladder, trays and supports. | 3 months | Factory will hire a qualified electrical engineer to provide as-built electrical drawings including the switchgear and other equipment including cable route, trenches, ladder, trays and supports. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | The provided drawings for single line diagram does not depict the sufficient information of the electrical system There were no single line diagrams showing how the overall system is connected. Some drawings are printed at A4 which are too small to be able to read the details. | Consult a qualified electrical engineer to update the Single Line Diagram to include information on all panels, distribution boards and on sub-distribution boards. Ensure all relevant details are accurately depicted to maintain the integrity and safety of the electrical system. | 6 months | Factory will Consult a qualified electrical engineer to update the Single Line Diagram to include information on all panels, distribution boards and on sub-distribution boards. Ensure all relevant details are accurately depicted to maintain the integrity and safety of the electrical system. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | During the inspection it is found that The electrical drawings for the LT room, generator and transformer room were not available. | Consult a qualified electrical engineer to provide detail as-built electrical drawings including the switchgear and other equipment including cable route, trenches, ladder, trays and supports. | 6 months | Factory will Consult a qualified electrical engineer to provide detail as-built electrical drawings including the switchgear and other equipment including cable route, trenches, ladder, trays and supports. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | Breakers installed were observed that did not provide adequate protection for connected cables eg. - 125A MCCB with 16 Sq.mm cable at stitching lighting pane 01 | Evaluate the breaker rating with respect to the cable sizes. The rating of the breaker must not be more than the cable ampacity further adjustable setting of breaker (if any) must be selected to allow current within the cable ampacity after derating factor implementation. | 3 months | Factory has started the evaluation of breakers in accordance with load provided. Factory will ensure the rating will not more than cable ampacity , future breaker selection will be made on the bases of allowable current limit. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed abnormally high temperatures in multiple locations, among those observed were the following (non-exclusive): - Waving Unit ground floor distribution boards. - Stitching bathrobe unit distribution boards Boiler House Panels | Inspect the electrical panels to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 6 months | Factory will Conduct a thorough inspection of the electrical panels to identify the cause of abnormal temperatures Factory will resolve the identified issues by tightening connections, redistributing loads, or replacing defective components as necessary |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing reports were missing for the factory | Create a schedule to have a thermograph survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. Carry out independent thermographic survey. | E4 + 6 months | Factory is in process of conducting the Thermographic Inspection by qualified third party. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | Earth pit for the powerhouse was inaccessible and inappropriately located. Earthing system was missing in multiple locations. -Many distribution boards lacked earthing bus bars. e.g LV panel adjacent to transformer -Electrical machines were not connected to earth at numerous location. observed specifically at stitching bathrobes | Consult a qualified electrical engineer to design and evaluate the earthing system. Submit the design to Pakistan Accord for review prior to completing the installation of the earthing system The grounding system should be provided for all facility panels, distribution boards, equipment, and cable trays. Separate earth bar of appropriate size shall be installed in electrical panels and distribution. The size of the earth conductor should comply with IEC standards. Additionally, ensure that the earth pits are located appropriately for easy accessibility. | 6 months | a) The facility will engage a qualified electrical engineer to design and evaluate the earthing system, ensuring it meets all safety and operational requirements. b)The proposed design will be submitted to Pakistan Accord for review and approval before installation begins. c)The grounding system will be implemented for all facility panels, distribution boards, equipment, and cable trays, with separate earth bars of appropriate size installed in all electrical panels and distribution boards. d) The earth conductors used will comply with IEC standards to ensure safety and reliability. Additionally, earth pits will be strategically located to allow easy accessibility for inspection and maintenance.. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | Equipotential bonding for cable trays was missing in entire facility Specifically at cable trays in entire facility | Equipotential bonding for cable trays must be provided in entire facility as per BS-7671 | E7 + 3 months | Factory will provide the Equipotential bonding for cable trays in entire facility as per BS-7671 |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Panel/cabling/busbar | electrical panels and distribution boards were discovered to feature cables that terminated without lugs at the breakers specifically at Weaving unit distribution boards | Conduct a thorough inspection of all distribution boards in the Weaving Unit to identify all cables that terminate without lugs. Assess the condition of the cables and breakers for any signs of damage (e.g., burns, insulation degradation) due to improper termination | 3 months | Factory will conduct a thorough inspection of all distribution boards in the Weaving Unit to identify all cables that terminate without lugs. and will also assess the condition of the cables and breakers for any signs of damage (e.g., burns, insulation degradation) due to improper termination |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Loop Connection | At numerous locations there were multiple cable connections originating from a single breaker, as well as instances of cables being looped multiple times within the distribution boards. E.g distribution boards at stitching bathrobe | Multiple connection from single point is strongly not recommended. This connection must be removed for outgoing circuit wires and with the panels/Distribution boards. Separated breaker should be installed for each outgoing circuit. | 3 months | The facility will address the issue of multiple connections from a single point, All such connections will be removed for outgoing circuit wires and within panels or distribution boards. To ensure proper circuit separation and safety, individual breakers will be installed for each outgoing circuit, providing dedicated protection and compliance with electrical standards |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed.Fixing foam was used to seal the opening gaps in the panels. Observed at stitching units | The IP rating of the panels/Distribution boards. must be incompliance with the IEC-61439 standards. All measure should be taken to ensure compliance to standards this may include replacing the panels/Distribution boards. | 3 months | Factory will start the evaluation of existing panels & distribution to start replacing with IP rating panels & distribution boxes in compliance with IEC-61439 Standards. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Lint & dust inside panel board | Lint and dust found in number of distribution boards.specifically at the following distribution boards. -Kitchen distribution board. -ETP panel -lift distribution board. | Schedule maintenance should be carried out for cleaning of panels and distribution boards. All measure should be taken to ensure the removal of dust, dirt, and any other sort of containment inside the panels. | 3 months | Factory has made a schedule of cleaning of all panels to avoid the accumulation of dust/fluff. Factory will submit proposals for permanent protection of dust and lint |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning arrestor was installed however the risk assessment and the design drawing were missing for the lightning protection system. | Consult a qualified electrical engineer to provide risk assessment report for lightning protection as per the IEC 63205 Standards and submit to Pakistan Accord prior to any modification on site in this regard. Consult a qualified electrical engineer to design the lightning protection system as per the IEC 62305 standards. The design drawings shall be submitted to Pakistan Accord prior to installation on site. | 6 months | The facility will engage a qualified electrical engineer to conduct a risk assessment for lightning protection in accordance with IEC 62305 standards. The risk assessment report will be submitted to Pakistan Accord for review before making any modifications on-site. Additionally, the facility will consult a qualified electrical engineer to design a comprehensive lightning protection system aligned with IEC 62305 standards. The design drawings will be submitted to Pakistan Accord for approval prior to initiating the installation process on-site. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. Some of the related issues include: - Incomplete coverage of fire alarm devices in some areas - type of detection devices not appropriate -cables not fire rated. - conventional non listed panel installed - Sounders inaudible due to low volume, or without distinctive audible signals | (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 5 months | The facility will prepare and submit comprehensive design documentation for the upgrade or replacement of the current Fire Alarm and Detection System (FADS) to Pakistan Accord for review prior to purchasing any new equipment. The documentation will include detailed drawings, technical data sheets, and product certifications for all listed equipment to demonstrate full compliance with NFPA 72 standards. This ensures that the proposed system meets the necessary safety and operational requirements before implementation |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Fire Alarm & Detection System (FADS) | Detectors | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E14 + 1 months | Facility will raise Demand of FADS System where required after getting it evaluated from Accord. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Fire Alarm & Detection System (FADS) | Fire Alarm Panel | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation | E15 + 4 months | Facility will start installing system once material is in-house. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Fire Alarm & Detection System (FADS) | Manual Call Points | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E16 + 5 months | Facility will acquire As-Built Drawing from vendor and will share with Accord after work completion. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Fire Alarm & Detection System (FADS) | Alarm Sounders | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E17 + 3 month | After system is installed and tested by facility, facility will then request Accord to visit and test system |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Fire Alarm & Detection System (FADS) | Maintenance records | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E17 + 3 months | After complying Step-5, facility will be in position of Remediation of FADS with help and guidance of Accord |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Emergency Lighting | Provided but insufficient | During the test it has been found that the few of the emergency lights in the factory area are non-functional further the number of lights was found to be insufficient to illuminate the escape routes as per the standard requirements specifically at weaving units,stitching bathrobe,boiler house | Consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements. Submit the design to Pakistan Accord prior to installation. All emergency lights must be listed and in proper working condition | 6 months | Factory will hire qualified company to design the emergency lightning system as per the NFPA standards, & will submit the design to Pakistan Accord for review Factory will ensure all emergency lights will be listed & in good working conditions. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Emergency Lighting | Independent power source | It has been observed that the emergency lights have been energized by utilizing the nearby light and power circuits.and does not have independent circuits risking the continuous power supply reliability and hindrance in testing of each light for maintenance and record. observed throughout the facility it was | The circuit for emergency lighting with built-in battery must be isolated from general lighting and power. Each zone should have its own dedicated emergency lighting circuit. The lights shall be provided with switches, it must not be operated from the breaker. | 6 months | The facility will ensure that the emergency lighting circuit with built-in batteries is isolated from general lighting and power circuits to enhance safety and reliability. Dedicated emergency lighting circuits will be established for each zone, providing clear separation and efficient operation. Additionally, switches will be installed for controlling the emergency lights, ensuring they are not operated directly from the breakers, in compliance with best practices and safety standards. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Emergency Lighting | General Lighting | It was observed that most of the factory area lights are being switched on and off directly from the circuit breakers. Operating a circuit breaker directly from the breaker itself is unsafe and not recommended. observed throughout the facility. | Lighting should not be switched off at the breakers instead, it should be controlled via light switches for individual and group of lights. | 1 month | The facility consult with Accord on ways to ensure that lighting is controlled using adequately. This may involve installing appropriate light switches to manage the operation of lights effectively and safely, aligning with best practices for electrical systems and operational convenience. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | It has been observed that the power house specifically the cable cellar area underneath the panels room lack safe ventilation. And lighting | Lights fixtures in the LV room should be added to enhance the illumination. Consult a Qualified Engineer to install an exhaust mechanism in the LV room to improve air circulation. Also to upgrade the existing ventilation system that can provide sufficient air changes for the room. Ensure that the new system is properly sized and designed to meet the ventilation requirements of the LV room. | 1 month | 1)Additional light fixtures will be installed to enhance illumination, ensuring adequate brightness for safety and efficiency. 2)A qualified engineer will be consulted to design and implement an exhaust mechanism to improve air circulation. 3)Simultaneously, the existing ventilation system will be upgraded to ensure sufficient air changes, providing proper airflow and maintaining optimal environmental conditions. 4)he new ventilation system will be carefully sized and designed to meet the specific requirements of the LV room, ensuring compliance with safety and operational standards. These actions will collectively enhance the functionality and safety of the LV room. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Cabling & Wiring | Cables support and protection | It is observed from the inspection that at the numerous locations that cables are laid without appropriate support and dressing.specifically dressing of wire inside the trays at the stitching units and cable cellar room underneath the LV room | All cables must be contained within cable trays and conduits, properly dressed, and organised as per the standards. All cables must be contained within suitable enclosures, properly dressed, and organised as per the BS 7671 standard. | 6 months | Factory will ensuring that all cables are contained within appropriate cable trays, conduits, or enclosures, properly dressed and organized to meet safety and operational standards. This will include verifying that cable installations comply with the requirements of BS 7671, ensuring safe and professional handling of electrical systems. The corrective measures will involve inspecting existing installations, rectifying any deficiencies, and implementing proper containment solutions. This approach will enhance system reliability, safety, and compliance with recognized standards. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Cabling & Wiring | Cable trench and channel cleanliness | It was observed that the cable trenches and channel were significantly contaminated with lint and dust. It was observed at cable trenches at switchgear rooms. | The cable trenches must be kept clear of debris and dirt, and any open trenches must be covered to prevent entry by rodents and other contaminants. | 3 months | Factory has made a schedule of cleaning of all cable trays to avoid the accumulation of dust/fluff. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Cabling & Wiring | Splicing of cables | It has been observed on the numerous location cables are openly laid on floor, undressed and unmanaged observed specifically at Cable cellar room under the LV panels | Wire joints should be avoided at all costs. If any joints are present due to short length, the wire must be replaced entirely wherever applicable. Suitably design cable joints may be installed as per standard engineering practices however tape joint must not be used. | 6 months | Factory will start elimination of wire joints to ensure system integrity and safety. Wherever joints are found due to insufficient wire length, the affected wire will be replaced entirely where feasible. In cases where wire replacement is not possible, properly designed cable joints will be installed following standard engineering practices to maintain reliability and safety. Under no circumstances will tape joints be used, as they compromise the quality and safety of the electrical connections. These measures will enhance the durability and compliance of the electrical system. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Cabling & Wiring | Colour coding | It was noted that within various panels and distribution boards, the phase of the cables could not be determined based on their colour coding at multiple locations e.g lift panels and Cables at LV room panels | Each cable must be colour coded according to the respective phase colour. further colour sleeves must be applied on buss bars for phase identification. | 3 months | Factory will ensure that all cables are appropriately color-coded to align with the respective phase colors for clear and accurate phase identification |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Cabling & Wiring | Fixtures | It is observed that at the numerous location the receptacle for the appliance lacks the earth connection and found broken/unsafe to use observed at stitching unit | All power receptacles must be connected to the main earth bar with an earth cable to ensure proper grounding. Additionally, any broken receptacles must be replaced with IP-rated covers specifically for wet and outdoor areas. | 3 months | Factory will ensure that all power receptacles will be connected to the main earth bar with an earth cable to ensure proper grounding. Additionally, any broken receptacles will be replaced with IP-rated covers specifically for wet and outdoor areas |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 139 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 140 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 141 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 142 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 143 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 144 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 145 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 146 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 147 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 148 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 149 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 151 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 152 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
25-Mar-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Indus Home Limited, 2.5 Km off Manga Raiwind Road, Manga Mandi, District Kasur, Lahore, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 25-Mar-2024, 27-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Non-compliant locking mechanisms were observed in (non-exhaustive): • Few of the doors in Canteen building Workshop facility & WWTP area • Both of Godown buildings have non-compliant locking mechanism. • Weaving Unit – process areas , offices (GM Office etc ),workshops (Electrical and Mechanical), chiller room • Few of the doors in Power House, RO plant, WWTP, Boiler House buildings found with non-compliant locking mechanisms • Few of the doors in Dyeing and Stitching Unit buildings | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | Facility has reassessed all areas as mentioned in report and remove all catches installed with doors. - In some areas ( Godown, Weaving) Wicket/Escape gate will be installed and facility is in process of collecting BOQs. After vetting, facility will start Providing wicket/escape gate where required. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Non-compliant locking mechanisms were observed in (non-exhaustive): • Few of the doors in Canteen building Workshop facility & WWTP area • Both of Godown buildings have non-compliant locking mechanism. • Weaving Unit – process areas , offices (GM Office etc ),workshops (Electrical and Mechanical), chiller room • Few of the doors in Power House, RO plant, WWTP, Boiler House buildings found with non-compliant locking mechanisms • Few of the doors in Dyeing and Stitching Unit buildings | Provide easily opening mechanisms complying with Pakistan Accord Building Standard Section 1 Clauses 1.4 & 1.5 | 3 months | Facility has reassessed all areas as mentioned in report and remove all catches installed with doors. - In some areas ( Godown, Weaving) Wicket/Escape gate will be installed and facility is in process of collecting BOQs. After vetting, facility will start Providing wicket/escape gate where required. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Sliding doors are installed in following locations -examples are: • All the Yarn Godowns have sliding doors. • Most of the sliding doors are found in Weaving unit • Chemical stores in Godown area are found with sliding doors. | Replace sliding door(s) or Provide pocket door in existing sliding doors with side hung swinging door(s) which swing in the direction of egress travel as per Pakistan Accord Building Standard clause 1.5. | 3 months | Facility is in process of provision of wicket/pocket door in mentioned Sections. For that purpose, facility is taking quotations from vendors. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Emergency Exit stairs are not protected in following locations -examples are: • Weaving Unit – grey fabric store stair not protected. • Weaving Unit -1st Floor Exit Stairs . • Weaving Unit main store-room stairs not protected. • Exit stair between Stitching Towel & Stitching Bathrobe buildings is not protected. • Exit Stair of Biomass Plant not protected. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs; - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | Facility is arranging layout for provision of fire doors and fire separation walls in areas as mentioned in report. Drawings will be received by 23-Dec-2024 and will be shared with Accord first for vetting. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Emergency Exit stairs are not protected in following locations -examples are: • Weaving Unit – grey fabric store stair not protected. • Weaving Unit -1st Floor Exit Stairs . • Weaving Unit main store-room stairs not protected. • Exit stair between Stitching Towel & Stitching Bathrobe buildings is not protected. • Exit Stair of Biomass Plant not protected. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. | F4 + 4 months | Facility is arranging layout for provision of fire doors and fire separation walls in areas as mentioned in report. Drawings will be received by 23-Dec-2024 and will be shared with Accord first for vetting. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Exit access | Exit access routes are not fire separated from the rest of the building-examples are: • Stitching Towel building level 1 stair discharges into the Stitching towel ground level before leading to an exit • Weaving Unit-Main storeroom stairs discharge into store area ground floor | Prepare drawings showings proposed fire separation details of the exit discharge routes. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors; - Details of fire rated walls and doors (e.g. listing, fire rating period, door self-closers, door opening direction). | 4 months | Facility is arranging layout for provision of fire doors and fire separation walls in areas as mentioned in report. Drawings will be received by 23-Dec-2024 and will be shared with Accord first for vetting. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Exit access | Exit access routes are not fire separated from the rest of the building-examples are: • Stitching Towel building level 1 stair discharges into the Stitching towel ground level before leading to an exit • Weaving Unit-Main storeroom stairs discharge into store area ground floor | Ensure exit discharge routes are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow Pakistan Accord Building Standard. Where stairs discharge within the building, a fire separated corridor shall be provided that leads to outside building | F6 + 4 months | Quotation awaited, Layout preparation is in progress |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Travel distance | The common path travel distance from a storage occupancy not meeting the travel distance criteria- examples are: • Sample Storage room at ground level has a common path travel distance of more than 23m for a single exit in the Stitching Towel building. | Provide alternative exiting arrangements to reduce the travel distances to be in accordance with the Pakistan Accord Building Standard. | 4 months | Facility has re-evaluated areas where there is only one egress way and facility is planning to install fire rated door in Sampling Store. Quotation is awaited and Layout preparation is in progress |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit access | Exit access routes are not fire separated from the rest of the building-examples are: • Weaving Unit – Material Storage along an exit route. • This will ensure safe passage of all occupants in case of emergency. | Remove obstruction to provide sufficient exit access as per Building Code of Pakistan & Pakistan Accord Building Standard. | 1 months | Task completed |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Fire Suppression | Standpipe system | Stitching Towel & Stitching Bathrobe Building does not have a Class I standpipe system but requires one because the building is not sprinklered, is more than 2 storeys (Stitching Towel) , and has a floor area greater than 2,325 m2 | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24. | 4 months | Facility is redesigning its fire protection system as per requirement of NFPA and share with Accord for approval. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Fire Suppression | Standpipe system | Stitching Towel & Stitching Bathrobe Building does not have a Class I standpipe system but requires one because the building is not sprinklered, is more than 2 storeys (Stitching Towel) , and has a floor area greater than 2,325 m3 | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F10 + 1 month | Facility is redesigning its fire protection system as per requirement of NFPA and share with Accord for approval. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Fire Suppression | Standpipe system | Stitching Towel & Stitching Bathrobe Building does not have a Class I standpipe system but requires one because the building is not sprinklered, is more than 2 storeys (Stitching Towel) , and has a floor area greater than 2,325 m4 | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F11 + 4 months | Facility is redesigning its fire protection system as per requirement of NFPA and share with Accord for approval. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Fire Suppression | Standpipe system | Stitching Towel & Stitching Bathrobe Building does not have a Class I standpipe system but requires one because the building is not sprinklered, is more than 2 storeys (Stitching Towel) , and has a floor area greater than 2,325 m5 | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F12 + 3 months | Facility is redesigning its fire protection system as per requirement of NFPA and share with Accord for approval. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Suppression | Standpipe system | Stitching Towel & Stitching Bathrobe Building does not have a Class I standpipe system but requires one because the building is not sprinklered, is more than 2 storeys (Stitching Towel) , and has a floor area greater than 2,325 m6 | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F13 + 3 months | After vetting from Accord, facility will install system and then inform Accord for verification. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Fire Suppression | Standpipe system | Stitching Towel & Stitching Bathrobe Building does not have a Class I standpipe system but requires one because the building is not sprinklered, is more than 2 storeys (Stitching Towel) , and has a floor area greater than 2,325 m7 | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F14 + 3 months | After vetting from Accord and installing system, facility will obtain Testing & Commissioning Certificate. Facility will then ask Accord for final inspection. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Suppression | Fire pumps | Following issues were observed in fire pumps: • Fire pump set is not listed. • Diesel Pump, Main Fire pump, Jockey pump and Controller are all installed but not listed | Prepare pump room layout that demonstrate compliance with Building code of Pakistan section 9.4 and submit to Pakistan Accord along with equipment’s documentation giving technical details and certifications for review, before purchasing equipment. | 4 months | UL Listed FM approved 1500 GPM at 12 bar pump installation is in progress. Facility will share layout with Accord to advice if there are changes required |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Suppression | Fire pumps | Following issues were observed in fire pumps: • Fire pump set is not listed. • Diesel Pump, Main Fire pump, Jockey pump and Controller are all installed but not listed | Provide the required listed fire pumps as per documentation reviewed by Pakistan Accord. Ensure the fire pump room and the full fire pump system complies with NFPA 20 as part of the supporting infrastructure to the SUPS system by following steps (1) to (6) above | 18 months | UL Listed FM approved 1500 GPM at 12 bar pump installation is in progress. Facility will share layout with Accord to advice if there are changes required |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Separation of shafts | Lift Shaft not protected by fire and smoke resistant construction in following locations. Examples are : • Stitching Units Lift Shafts at all floors are not separated from production / storage areas • Weaving Unit – cargo lift needs fire separation from rest of the floors. • Yarn Godown – Ground Floor & 1st Floor lift shafts not separated from storage areas | Submit proposal for how lift openings will be addressed to Pakistan for review. | 4 months | Facility is Planning to install fire rated doors at one opening of lift and 2nd side to be closed permanently with civil construction. Facility will seek further guidance from Accord. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Separation of shafts | Lift Shaft not protected by fire and smoke resistant construction in following locations. Examples are : • Stitching Units Lift Shafts at all floors are not separated from production / storage areas • Weaving Unit – cargo lift needs fire separation from rest of the floors. • Yarn Godown – Ground Floor & 1st Floor lift shafts not separated from storage areas | Separate lift shaft by fire-rated construction, implementing the previously reviewed design proposal. | F18 + 4 months | Facility is Planning to install fire rated doors at one opening of lift and 2nd side to be closed permanently with civil construction. Facility will seek further guidance from Accord. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Structural fire rating | Unprotected steel structures not meeting structural fire resistance requirements - examples are: •Dying Unit building - an unprotected steel structure (Type 2 Construction) over 1800m2 in floor area not meeting structural fire resistance requirements. •Stitching Bathrobe building - an unprotected steel structure (Type 2 Construction) over 1800m2 in floor area not meeting structural fire resistance requirements. | Provide proposal for the fire protection of the steel structure showing compliance with fire rating requirements and submit to Pakistan Accord for review. | 4 months | Facility is reassessing its structure and planning to have fire resistant material at at Dyeing shed. Facility is seeking quotations from vendors which will be available by end of December-20214. Facility is planning to install sprinkler System at DC-1 Hall. Facility will submit proposals to Accord and seek guidance before execution of both tasks. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Structural fire rating | Unprotected steel structures not meeting structural fire resistance requirements - examples are: •Dying Unit building - an unprotected steel structure (Type 2 Construction) over 1800m2 in floor area not meeting structural fire resistance requirements. •Stitching Bathrobe building - an unprotected steel structure (Type 2 Construction) over 1800m2 in floor area not meeting structural fire resistance requirements. | Apply fire protection to the steel structure in accordance with the proposal submitted earlier for review. | F20 + 4 months | Facility is reassessing its structure and planning to have fire resistant paint at at Dyeing shed. Facility is seeking quotations from vendors which will be available by end of December-20214. Facility is planning to install sprinkler System at DC-1 Hall. Facility will seek guidance from Accord before execution of both tasks. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Floor openings | Floor openings/ assemblies not achieving required fire resistance ratings (Type I Construction)- examples are: • Power House – basement under generator rooms is open to all floors and need fire rated separation through type I construction and fire doors | Prepare drawings showing proposals for fire rated floor separation by sealing penetrations, use of fire-rated floor/ceiling assemblies or protection of the openings with a fire rated enclosure in accordance with the Pakistan Accord Building Standard. Proposals to be submitted to Pakistan Accord for review and acceptance prior to the rectification works | 4 months | Facility is preparing layout as accordance with Accord and will share with Accord before execution to get it vet. Tentatively facility will get layout in Third week of Jan-2025. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Floor openings | Floor openings/ assemblies not achieving required fire resistance ratings (Type I Construction)- examples are: • Power House – basement under generator rooms is open to all floors and need fire rated separation through type I construction and fire doors | Provide the required fire separation as per documentation reviewed by Pakistan Accord | F22 + 3 months | After verifying layout with Accord, facility will start execution work |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Separation of occupancies | Occupancies observed that may not be incidental and are not separated by fire and smoke resisting construction are as follows (non-exhaustive): • Dyeing unit: Offices not separated from dyeing area, dyeing lab. • Dyeing unit: Praying area is not separated from dyeing area. | Prepare drawings showing proposed fire separation details of separation of occupancies. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors. - Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Facility is preparing drawings/layouts of areas as identified by Accord for provision of Fire Separation Wall and will share with Accord first before execution. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Separation of occupancies | Occupancies observed that may not be incidental and are not separated by fire and smoke resisting construction are as follows (non-exhaustive): • Dyeing unit: Offices not separated from dyeing area, dyeing lab. • Dyeing unit: Praying area is not separated from dyeing area. | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | F24 + 4 months | Facility will execute work after getting it verified with Accord |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Rated Construction | Storage | Storage was observed that did not appear to meet miscellaneous storage requirements-examples are: • Weaving Unit – storage height at production floor found above 8 feet. • Weaving Unit – beam stock storage may exceed storage limits; may need separation from sizing machines (production). • Stitching Towel Unit: Storage area not separated from production area.) | Identify all designated storage areas. | 1 months | Facility has identified its storage areas (that includes temporary storage areas as well). Facility is now ensuring to limit stack height do not exceed 8 feet limit. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Storage | Storage was observed that did not appear to meet miscellaneous storage requirements-examples are: • Weaving Unit – storage height at production floor found above 8 feet. • Weaving Unit – beam stock storage may exceed storage limits; may need separation from sizing machines (production). • Stitching Towel Unit: Storage area not separated from production area.) | Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Facility has identified its storage areas where fire separation is required. Facility is making layout to make it seperated from Production area and layout will be completed by mid of Jan-2025. Facility will then share these layouts with Accord |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Rated Construction | Storage | Storage was observed that did not appear to meet miscellaneous storage requirements-examples are: • Weaving Unit – storage height at production floor found above 8 feet. • Weaving Unit – beam stock storage may exceed storage limits; may need separation from sizing machines (production). • Stitching Towel Unit: Storage area not separated from production area.) | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F27 + 4 months | After verification from Accord, facility will start executing task. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Separation of high-risk areas | Increased fire risk areas are not fire separated from the rest of the building-examples are: • Weaving Unit – dust collectors found alongside production floor are not fire separated. • Weaving Unit –high risk area (compressor room, chiller room, electrical room, AC plant) found not fire separated from production floor. • Dying Area- Electrical room not separated by fire and smoke resisting construction from steam generators. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of all increased fire hazard areas in the building (e.g storage, electrical rooms, mechanical rooms etc.) - Locations of fire rated walls and doors to protect these rooms; - Details of proposed fire walls and fire doors (e.g. door listing, self-closers, door opening direction); | 4 months | Facility has identified its storage areas where fire separation is required. Facility is making layout to make it seperated from Production area and layout will be completed by mid of Jan-2025. Facility will then share these layouts with Accord |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Separation of high-risk areas | Increased fire risk areas are not fire separated from the rest of the building-examples are: • Weaving Unit – dust collectors found alongside production floor are not fire separated. • Weaving Unit –high risk area (compressor room, chiller room, electrical room, AC plant) found not fire separated from production floor. • Dying Area- Electrical room not separated by fire and smoke resisting construction from steam generators. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F29 + 4 months | Facility is re-evaluating its areas as highlighted by Accord for provision of 2 hours fire rating and fire rated doors and arranging quotations accordingly. By end of Jan-2025, facility will have all data and then reach out Accord for vetting before execution. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Hazardous Materials | Chemicals storage | Hazardous materials - Chemical storage issues are observed in following locations : • Power House – level 1 chemical storage. • Day storage of chemicals on production floor at Dying unit | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. Submit storage arrangement proposals to Pakistan Accord for review. | 4 months | Facility has instructed departments to limit stock to one day use only in Sub-Store and also making storage conditions in accordance with standards as mentioned in MSDS. Facility will share plan with Accord as well |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Hazardous Materials | Chemicals storage | Hazardous materials - Chemical storage issues are observed in following locations : • Power House – level 1 chemical storage. • Day storage of chemicals on production floor at Dying unit | Implement the chemical storage arrangements on site as per documentation reviewed by Accord. | F31 + 4 months | After getting it verified from Accord, facility will implement plan. |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Hazardous Materials | Diesel storage | Storage, handling, and use of flammable and combustible liquids and/or solids was not compliant - examples are: • Weaving Unit – warping area maintenance office flammable hydraulic oil is present. • Weaving Unit – ground floor folding, diesel storage of approx. 420 litres. • Weaving Unit – warping area maintenance office flammable hydraulic oil is present. | Interior diesel storage (maximum 1265 litres on ground level) is permitted if it is fire separated from other areas by 1-hr fire rated construction and stored in accordance with other requirements of NFPA 30. Diesel storage is permitted within generator rooms and fire pump rooms if adequately stored and that room is separated from adjacent occupancies. | 2 months | Facility has discontinued practice of storing flammable chemical and diesel in Production Department. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
25-Mar-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Indus Home Limited, 2.5 Km off Manga Raiwind Road, Manga Mandi, District Kasur, Lahore, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 25-Mar-2024, 27-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Other Damage/Defects | Health and Safety | Greige Godown roof: a) Steel ladder providing access to the roof exhibited significant instability, indicating inadequate attachment to the structural system b) No edge protection is provided to the roof. | Provide a stable ladder for the Greige Godown roof for access and maintenance. Provide an appropriate roof edge protection to all accessible roofs | 3 months | Ladder Removed |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Other Damage/Defects | Health and Safety | Weaving building roof: a) There is an inadequate access across the weaving building roof which is attributed to the presence of deep inverted RC beams. Maintenance staff are currently required to traverse the MEP pipes near the roof’s edge to gain the roof access. Furthermore, a lack of provision for the roof edge protection is observed, | Provide safe access across the weaving building for services and maintenance. Consider installation of crossover stairs. | 3 months | 1) Facility is assessing two options: a) Provision of parapet wall with height of 1.1 meter. b) Adding Aluminum railing on existing parapet wall. 2) Facility is working over BOQ to make walkway structure across Cooling Tower so that Maintenance Staff has easy approach for work at Cooling Tower to avoid traveling over MEP Pipes. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Other Damage/Defects | Health and Safety | Coal Boiler, Stitching Towel building’s roofs: a) Lower parapet height walls were observed along the roof edges of noted buildings. Railings or guards shall not be less than 1065mm above the aisle surface in accordance with cl. 15.3.3.1 of the BCP Fire Safety Provisions – 2016. | Provide an appropriate roof edge protection to all accessible roofs. | 3 months | Facility is assessing two options: a) Provision of parapet wall with height of 1.1 meter. b) Adding Aluminum railing on existing parapet wall. Will finalize once the BOQs for said task finalized. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Other Damage/Defects | Health and Safety | Corroded steelwork platform observed at waste-water treatment plant (WWTP). | Replace the rusted walkways and install the missing rail bars. Ensure building walkway maintenance to be proper. | 3 months | Facility is assessing two options: a) Need to Replace with FRP railing b) Need to add railing bars along with paint work. Facility is making over BOQ to make the safer walkway. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Other Damage/Defects | Health and Safety | Corroded steelwork platform observed at waste-water treatment plant (WWTP). | Building Engineer to investigate and assess the steelwork in this area. Replace it with a designed walkway structure if necessary. | S4 + 3 months | Facility will work to upgrade / Strengthen existing Side railing by adding members in it. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Corrosion of reinforcement | This relates to the RC columns of the RO Plant building at the ground floor level. Cracking is observed in almost all RC columns (at least 11 nos.) surrounding the salt room. These cracks are likely attributed to the penetration of salty water, causing concrete deterioration and corrosion of the column reinforcement. A Schmidt hammer test was carried on one of the perimeter columns and was not able to get a reading, indicating poor condition of the concrete. | Drain off the pool of salty water at ground floor level, and temporarily relocate the solid storage of salt from the RO building. Appoint a qualified and experienced structural engineer to carry out a detailed assessment of the affected columns to establish the residual load capacity and the cause of column cracking , and submit to Pakistan Accord for review. | 3 months | Factory will drain the pool of salty water at the ground floor level and temporarily relocate the solid salt storage from the RO building. A qualified and experienced third party will be appointed to conduct a detailed assessment of the affected columns to determine their residual load capacity and identify the cause of column cracking, with the findings submitted to Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Other Damage/Defects | Corrosion of reinforcement | This relates to the RC columns of the RO Plant building at the ground floor level. Cracking is observed in almost all RC columns (at least 11 nos.) surrounding the salt room. These cracks are likely attributed to the penetration of salty water, causing concrete deterioration and corrosion of the column reinforcement. A Schmidt hammer test was carried on one of the perimeter columns and was not able to get a reading, indicating poor condition of the concrete. | Based on the results of the detailed assessment, factory will propose necessary remedial works for concrete repairs and stress reduction, if required, and submit these proposals to Pakistan Accord. Additionally,factory will recommend a safe storage solution for the salt to prevent any damage to this or other structures in the future. | 3 months | PEC registered AA associate and Kraftkon engaged for detailed assessment of Structure. Once report received, will work on Storage condition of salt after final approval from Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Other Damage/Defects | Corrosion of reinforcement | This relates to the RC columns of the RO Plant building at the ground floor level. Cracking is observed in almost all RC columns (at least 11 nos.) surrounding the salt room. These cracks are likely attributed to the penetration of salty water, causing concrete deterioration and corrosion of the column reinforcement. A Schmidt hammer test was carried on one of the perimeter columns and was not able to get a reading, indicating poor condition of the concrete. | Implement the remedial works | S7 + 3 months | PEC registered AA associate and Kraftkon engaged for detailed assessment of Structure. Once report received, factory will work on remediation work after final approval from Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Towel building at the ground floor level appear to be highly stressed for the applied load. Excessive storage or live load is not observed on the superstructural levels. | (1) Appoint a qualified and competent Structural Engineer to carry out Detailed Engineering Assessment (DEA) on the full building, in accordance with the requirements and scope attached in the Structural Initial Assessment report | 1 month | Factory has engaged the PEC certified third party consultancy for detailed assessment of full building upon the guidelines provided by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Towel building at the ground floor level appear to be highly stressed for the applied load. Excessive storage or live load is not observed on the superstructural levels. | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | S9 + 3 months | Factory has contracted PEC registered AA associate and Kraftkorn company for detailed assessment including all key elements & also material strengths of all affected Columns / Beams. Once report ready, will be sent to Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Towel building at the ground floor level appear to be highly stressed for the applied load. Excessive storage or live load is not observed on the superstructural levels. | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | S10 + 4 months | Factory will submit a structural engineering assessment, including supporting calculations based on the as-built drawings and previously reviewed material strengths. This will be done using a model-based design that demonstrates the building’s safety and serviceability under the specified loading conditions, in accordance with the Building Code of Pakistan. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Towel building at the ground floor level appear to be highly stressed for the applied load. Excessive storage or live load is not observed on the superstructural levels. | (4) Submit proposals for retrofitting works to be undertaken to demonstrate the adequacy of the structure to Pakistan Accord for review | S11 + 4 months | Factory will submit proposals for retrofitting works to Pakistan Accord for review, aimed at demonstrating the adequacy of the structure. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Towel building at the ground floor level appear to be highly stressed for the applied load. Excessive storage or live load is not observed on the superstructural levels. | (5) Carry out all retrofitting works as proposed and previously reviewed by Pakistan Accord | S12 + 6 months | Work will be carried out once assessment will be finalized by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Towel building at the ground floor level appear to be highly stressed for the applied load. Excessive storage or live load is not observed on the superstructural levels. | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then DEA will be complete | S13 + 1 month | Factory will take Pakistan Accord on board for verification of work. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Cracking | Beams | This observation is related to the Weaving building. Cracks are observed in the rectangular inverted cast in situ RC beams (10m span) near the internal column support, where post-tensioned inverted RC beams (41.5m span, I-shaped section) are also supported. Location of the cracks is consistent among the adjacent inverted beams and appeared to be due to inadequate reinforcement in the rectangular RC beams at the column support to resist the large hogging moment induced by the long span of post-tensioned beam. It is worth to note that the width of rectangular RC beam is considerably narrower and has much shorter span than that of the I-shaped post-tension beam section. Extensive corrosion of rebar was also noted along the base of the inverted post tensioned RC beams | Building Engineer to carry out condition survey of the RC beams to investigate cause and impact of these cracks on the capacity of the roof and check if these can carry the load in simply supported condition. This should be carried out in conjunction with the investigation of the spalling of concrete in beams affecting the weaving building | 2 months | Factory will involve the Building Engineer for conducting a condition survey of the RC beams to investigate the cause and impact of the cracks on the roof's capacity, and to assess whether the beams can support the load in a simply supported condition. This survey will be carried out alongside the investigation of concrete spalling in beams affecting the weaving building. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Cracking | Beams | This observation is related to the Weaving building. Cracks are observed in the rectangular inverted cast in situ RC beams (10m span) near the internal column support, where post-tensioned inverted RC beams (41.5m span, I-shaped section) are also supported. Location of the cracks is consistent among the adjacent inverted beams and appeared to be due to inadequate reinforcement in the rectangular RC beams at the column support to resist the large hogging moment induced by the long span of post-tensioned beam. It is worth to note that the width of rectangular RC beam is considerably narrower and has much shorter span than that of the I-shaped post-tension beam section. Extensive corrosion of rebar was also noted along the base of the inverted post tensioned RC beams | Propose the remedial works, if the RC beams are not in line with the design requirements.Also share with Accord for review. | 2 months | PEC registered AA associate and Kraftkon engaged for detailed assessment of all affected Columns / Beams. Factory Will engage approved contractor for remedial work after detailed assessment. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Cracking | Beams | This observation is related to the Weaving building. Cracks are observed in the rectangular inverted cast in situ RC beams (10m span) near the internal column support, where post-tensioned inverted RC beams (41.5m span, I-shaped section) are also supported. Location of the cracks is consistent among the adjacent inverted beams and appeared to be due to inadequate reinforcement in the rectangular RC beams at the column support to resist the large hogging moment induced by the long span of post-tensioned beam. It is worth to note that the width of rectangular RC beam is considerably narrower and has much shorter span than that of the I-shaped post-tension beam section. Extensive corrosion of rebar was also noted along the base of the inverted post tensioned RC beams | Implement the remedial works (if any). Continue monitoring them on an on-going basis. | S 16 + 4 months | Remediation work will be carried out as per the assessment report received. Factory has monitoring mechanism for building structures, Engineering team is working to further improve the mechanism. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Other Damage/Defects | Column impact damage | This is related to the Coal boiler building. Impact damage in an RC column is observed near the vehicle passageway which suggests the exposing of rebar is due to the due to a vehicle impact, resulting in corrosion of rebar. We have visually inspected the loading in this area and observed there is no concerns regarding the overstressing. | Repair the column and protect the column to avoid vehicle impact in future | 3 months | Factory has plan to install M.S Safety railing along columns to save columns from damage. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S19 | Other Damage/Defects | Column impact damage | This is related to the Coal boiler building. Impact damage in an RC column is observed near the vehicle passageway which suggests the exposing of rebar is due to the due to a vehicle impact, resulting in corrosion of rebar. We have visually inspected the loading in this area and observed there is no concerns regarding the overstressing. | Provide suitable protection around all RC columns in areas with vehicle or loaded trolley movement to prevent damage or collapse of columns from potential impacts | S18 + 3 months | Factory will Install appropriate protective barriers around all reinforced concrete (RC) columns in areas with vehicle or loaded trolley traffic to prevent damage or potential collapse caused by impacts |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Other Damage/Defects | Spalling concrete | Cracking and spalling of reinforced concrete are observed at various locations such as: Weaving: Concrete spalling is evident on most highly spanned inverted RC beams near the roof level, potentially due to inadequate waterproofing at the lower sections of the inverted beams. | Building Engineer to inspect areas with water damage and propose measures to prevent further damage. This should be carried out in conjunction with the investigation of the cracking in beams affecting the weaving building. | 3 months | 1) PEC registered AA associate and Kraftkon engaged for detailed assessment of factory structure, factory Will engage approved contractor for remedial work after detailed assessment |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Other Damage/Defects | Spalling concrete | Cracking and spalling of reinforced concrete are observed at various locations such as: Weaving: Concrete spalling is evident on most highly spanned inverted RC beams near the roof level, potentially due to inadequate waterproofing at the lower sections of the inverted beams. | Carry out repair works | S20 + 3 months | Factory will engage the approved contractor for remediation work once the assessment report received. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S22 | Other Damage/Defects | Spalling concrete | Cracking and spalling of reinforced concrete are observed at various locations such as: Coal Boiler: Cracking in an eastern column is observed which appears to be related to the lack of rainwater pipe just above the ground | Building Engineer to inspect areas with water damage and propose measures to prevent further damage and carry out repair works | 6 months | 1) PEC registered AA associate and Kraftkon engaged for detailed assessment of all buildings 2) Factory Will engage approved contractor for inspection of damaged areas with areas & propose the best possible measures to prevent further damage. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S23 | Other Damage/Defects | Spalling concrete | Cracking and spalling of reinforced concrete are observed at various locations such as: Scrap store near Yarn Godown: Wire reinforcement running in the ribs of the precast slab tiles is rusted and appears to be in poor condition at some locations. Rusting of reinforcement could be due to lack of waterproofing layer over the roof or due to insufficient cover to the bottom reinforcement. Typically, the rest of the panel is unreinforced. | Building Engineer to inspect areas with water damage and propose measures to prevent further damage and carry out repair works | 6 months | 1) PEC registered AA associate and Kraftkon engaged for detailed assessment of all buildings 2) Factory Will engage approved contractor for remedial work after detailed assessment. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S24 | Loading | Uncontrolled loading | Yarn storage beyond the allowable limit as outlined in the factory's load management plan is observed at the 1st floor level of the 2-Storey Yarn Godown and Greige Godown buildings. Minor hairline shear cracks in the Yarn Godown 1st floor beams were noted which could be associated with the heavy storage. The columns have been checked in this area and have found to have sufficient capacity. | Reduce the load to 105 psf which is reducing the height of yarn bags from 7 to 5. | 1 months | Factory has Rectified the yarn bags heights from 7 to 5 bags. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S25 | Loading | Uncontrolled loading | Yarn storage beyond the allowable limit as outlined in the factory's load management plan is observed at the 1st floor level of the 2-Storey Yarn Godown and Greige Godown buildings. Minor hairline shear cracks in the Yarn Godown 1st floor beams were noted which could be associated with the heavy storage. The columns have been checked in this area and have found to have sufficient capacity. | Building Engineer to ensure that the floor slab is not loaded beyond its capacity. Factory management to actively manage the floor loading. | 6 months | Factory has rectified the shear cracks in yarn godowns 1st floor beams. Storage capacity has been reduced to manage the floor loading capacity. Factory will provide safe load plan for this area and manage load accordingly |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S26 | Structural Documentation | Differs from as-built structure | Structural drawings of the facility need to be updated to include the following discrepancies (non-exhaustive): Weaving building – Structural drawings between the GL A-N/34-50, N-Y/15-51 and Z-Z2/1-51 were not available. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. Regarding the Weaving building, collect and generate a unified structural roof layout instead of multiple fragmented layouts. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S27 | Structural Documentation | Differs from as-built structure | Powerhouse building – structural drawings of the existing building were not available. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S28 | Structural Documentation | Differs from as-built structure | Boiler houser building – structural drawings of the existing building were not available. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S29 | Structural Documentation | Differs from as-built structure | Stitching Bathrobe & Dyeing buildings – Steel frame layouts of both buildings were missing. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S30 | Structural Documentation | Differs from as-built structure | Cross-sections through the buildings were not available. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S31 | Structural Documentation | Differs from as-built structure | Canteen building – structural drawings do not match with the as-built structure | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S32 | Structural Documentation | Differs from as-built structure | RO Plant building – structural drawings do not match with the as-built structure. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S33 | Structural Documentation | Differs from as-built structure | External steel stairs are not indicated on the building’s structural layouts. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built structural layout drafting is in progress. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S34 | Cracking | Non structural | Cracks are observed in some of the non-structural masonry walls infill between the RC frame of the Weaving building. Some of the cracks may have been resulted from shrinkage or lateral movement of the RC frame under wind load or due to excessive deflection of cantilever slab. It is suggested to repair these cracks and tie the walls to the RC frame to prevent potential collapse over time. | Propose the remedial works and once reviewed by Accord, implement the remedial works | 6 months | 1) PEC registered AA associate and Kraftkon engaged for detailed assessment of all affected Columns / Beams. Will engage approved contractor for remedial work after detailed assessment |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1