## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
09-Dec-2024
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Interloop Limited (HD III) - 8 Km Manga Raiwind Road, Manga Mandi, Kasur, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 09-Dec-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-25 | 2025-09-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2 + 3 month | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single-line diagrams (SLDs) for the factory were missing several information. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Update comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 month | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single-line diagrams (SLDs) for the factory were missing several information. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4 + 3 month | 2026-03-19 | 2026-06-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. Fire alarm drawings were available but lacked required information. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 months | 2025-09-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. Fire alarm drawings were available but lacked required information. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6 + 1 month | 2026-05-19 | 2026-06-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards, and signs of burning were also observed in various locations. Here are the few examples where signs of burning were observed: o Gate office near Mosque had sign of burning on switchboard o HFO boiler control DB o HR Department main DB circuit breaker# Q15 Example of these hotspots are mentioned in below: o Suction Hall# 02: 56.4°C o Husk Boiler: 42°C o Knitting 1 A PDB: 49.2°C o Processing DB 2: 61.6°C o 2500 kVA PEL Transformer: 45.9°C | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards, and signs of burning were also observed in various locations. Here are the few examples where signs of burning were observed: o Gate office near Mosque had sign of burning on switchboard o HFO boiler control DB o HR Department main DB circuit breaker# Q15 Example of these hotspots are mentioned in below: o Suction Hall# 02: 56.4°C o Husk Boiler: 42°C o Knitting 1 A PDB: 49.2°C o Processing DB 2: 61.6°C o 2500 kVA PEL Transformer: 45.9°C | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards, and signs of burning were also observed in various locations. Here are the few examples where signs of burning were observed: o Gate office near Mosque had sign of burning on switchboard o HFO boiler control DB o HR Department main DB circuit breaker# Q15 Example of these hotspots are mentioned in below: o Suction Hall# 02: 56.4°C o Husk Boiler: 42°C o Knitting 1 A PDB: 49.2°C o Processing DB 2: 61.6°C o 2500 kVA PEL Transformer: 45.9°C | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | 6 month | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Earthing system | The earthing system was missing in several areas. Many distribution boards lacked proper earth bonding, and the cable trays in the cable cellar were not properly earth-connected. Additionally, the 11kV overhead line within the factory did not have adequate earthing for the metal poles | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | The earth wire was found to be improperly laid directly on the floor. | Re-route the earth wire through designated cable trays or conduits to prevent physical damage, tripping hazards, and ensure safe operation. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | Earthing layout was not available in the facility. | An earthing layout diagram should be developed in accordance with BS 7671 (Regulation 411.3.2.2) to ensure proper documentation of the earthing system and network distribution throughout the facility. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified as listed below: i. The earthing system was missing in several areas. Many distribution boards lacked proper earth bonding, and the cable trays in the cable cellar were not properly earth-connected. Additionally, the 11kV overhead line within the factory did not have adequate earthing for the metal poles. ii. The earth wire was found to be improperly laid directly on the floor. iii. Earthing layout was not available in the facility. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E11 + 2 months | 2026-03-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | In several external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed, particularly circuit breakers installed outside the building walls. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | There were visible signs of damage to panels, cables, and busbars e.g., broken locks, faulty ampere and volt meters. | Inspect and repair or replace all faulty ammeters, voltmeters, damaged panels, cables, and busbars to ensure the integrity of the electrical system, in compliance with Section 522 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical panel lack proper cable dressing in panels in HFO boiler area. | Organize and secure cables in the HFO boiler area using properties, trays, or conduits (BS 7671). Clean and tighten panel connections and install appropriate warning labels and operational tags. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | The visual site inspection included an examination of the electrical panels, cables, and bus bars throughout the facility. i. In several external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed, particularly circuit breakers installed outside the building walls. ii. Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. iii. There were visible signs of damage to panels, cables, and busbars e.g., broken locks, faulty ampere and volt meters. iv. Electrical panel lack proper cable dressing in panels in HFO boiler area. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E15 + 5 months | 2025-12-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multi-looping was observed in several electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each circuit following Section 430 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels, and trunking systems. For example, LT2&3 PFI panel & masjid distribution board. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint following Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels, and trunking systems. For example, LT2&3 PFI panel & masjid distribution board. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E21 + 4 months | 2025-11-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. i. A lightning protection system was provided, however, there was no study available to confirm its adequacy. ii. No test results were provided for the lightning protection system, making it difficult to verify its effectiveness and compliance with relevant standards. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. Perform a thorough inspection of all LPS conductors. Replace any conductors showing signs of corrosion or rust with new components that meet the current standards. Apply protective coatings or use materials resistant to corrosion to prevent future deterioration of LPS components. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. i. A lightning protection system was provided, however, there was no study available to confirm its adequacy. ii. No test results were provided for the lightning protection system, making it difficult to verify its effectiveness and compliance with relevant standards. | If the risk assessment concludes that an LPS is necessary, then hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. Establish a routine maintenance schedule to inspect and maintain the LPS, ensuring ongoing protection against corrosion. | E23 + 4 months | 2025-11-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The following observations were identified with the FADS: a. The addressable Fire Alarm and Detection System lacked centralized communication between fire panels, limiting system coordination and responsiveness. b. The cabling used to complete the installation of the FADS was not fire rated. c. The system demonstrated overall non-compliance with NFPA 72 standards. The following observations were made with regards to the sounders and visual alarms: a. Insufficient audibility was noted in various locations, potentially impacting timely evacuation during emergencies. These discrepancies were observed in the generator room, kitchen canteen store, staircase lobby, meeting room, boiler control room, and offices, where the alarms exhibited low audibility. Conversely, in the training room, the audibility was excessively high, posing a potential risk of hearing damage to workers. The following observations were made with regards to the Manual Call Points: a. The MCP was placed inappropriately at Utility Building. b. The MCP in the HFO control room was found to be non-functional. c. Manual Call Points were not installed at all necessary locations, including along the escape route. The following observations were made regarding the detectors within the facility's Fire Alarm and Detection System (FADS): a. Inadequate fire detection measures were observed in several areas, leading to gaps in fire safety protocols. For instance, no detector was installed above the absorption chiller in the Utility Building and in hallways in Building 1. b. Several detectors were found to be faulty or non-functional. Additionally, the smoke detector in the 1.8-ton boiler control room may require repositioning. | Ensure the functionality and performance of the existing alarm and detection system in all the building. | 1 week | 2025-09-19 | 2025-09-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | i. Submit design documentation for upgrade of existing FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | ii. Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E26 + 1 months | 2025-12-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | iii. Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E27 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | iv. Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E28 +5 months | 2026-05-19 | 2026-10-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | v. Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E29 +3 months | 2026-10-19 | 2027-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | vi. Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E30 + 3 months | 2027-01-19 | 2027-04-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Emergency Lighting | Provided but insufficient | Several areas lack sufficient emergency lighting coverage e.g. engineering office near compressor, LT2 & 3 area and PD washing. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. Submit emergency light design to Pakistan Accord for review. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Emergency Lighting | Provided but insufficient | Multiple emergency luminaires indicate the need for maintenance at Warehouse. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Emergency Lighting | Provided but insufficient | External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations, e.g. assembly area outside production building. | Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s) | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Emergency Lighting | Provided but insufficient | During the inspection the emergency lighting arrangement throughout the facility was assessed. The following observations were made: - Several areas lack sufficient emergency lighting coverage e.g. engineering office near compressor, LT2 & 3 area and PD washing. - Multiple emergency luminaires indicate the need for maintenance at Warehouse. - External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations, e.g. assembly area outside production building. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E32 + 5 months | 2026-01-19 | 2026-06-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Generator, Transformer & Sub-Station Room | Battery | It was observed that battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Generator, Transformer & Sub-Station Room | Battery | It was observed that battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for the cables in the cable cellar of the Utility Building's HFO room; the cables were observed to be hanging on each other. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for the cables in the cable cellar of the Utility Building's HFO room; the cables were observed to be hanging on each other. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | E38 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Cabling & Wiring | Splicing of cables | Few cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. | Install cable lugs on all improperly terminated cables within panels and switchgear to secure connections and prevent breaking strands and loose connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in few locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Cabling & Wiring | Splicing of cables | During the inspection, the cable installation was visually surveyed throughout the facility. The following observations were noted: - Few cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. - PVC tape joints were found in few locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance and provide continuous training for staff on proper jointing techniques. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified specially in finished goods DB. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. Colour coding should be consistent throughout the facility. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified specially in finished goods DB. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations, and ensuring sustained safety and operational efficiency. | E43 + 6 months | 2026-01-19 | 2026-07-19 | AGREE |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
09-Dec-2024
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Interloop Limited (HD III) - 8 Km Manga Raiwind Road, Manga Mandi, Kasur, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 09-Dec-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-25 | 2025-09-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Protection of stairs | S-1 and S-5 are not fire separated from office area, and S-2 is not fire separated from store at ground floor. Fire Load in S-1, S-2 and S-15. | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | 2025-09-19 | 2025-10-03 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Protection of stairs | S-1 and S-5 are not fire separated from office area, and S-2 is not fire separated from store at ground floor. Fire Load in S-1, S-2 and S-15. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect the stairs Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Protection of stairs | S-1 and S-5 are not fire separated from office area, and S-2 is not fire separated from store at ground floor. Fire Load in S-1, S-2 and S-15. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute Fire Doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: All doors into stairs should be fire resisting doors with self-closing mechanisms. Penetrations through doors are not permitted. Doors into stairs should be kept closed (but not locked) at all times. | F3 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Travel distance | Common path of travel (CTD) distances exceeds permitted limits at: a) 39m CTD at Building 1 Accessory Store. b) 24m CTD at Building 1 GBS and PBS area. c) 73m CTD at Building 1 Yarn Store. Alternative Travel Distance (ATD) exceeds permitted limits at: a) 83m of ATD at Building 1 Processing area. b) 69m of ATD at Building 1 Knitting 03 area. c) 85m of ATD at Building 1 knitting 01 area. d) 68m and 115m at Building 2 main store. | Vacate the area temporarily until an alternative exit is provided for areas with common path more than 46 meters. | 2 weeks | 2025-09-19 | 2025-10-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Travel distance | Common path of travel (CTD) distances exceeds permitted limits at: a) 39m CTD at Building 1 Accessory Store. b) 24m CTD at Building 1 GBS and PBS area. c) 73m CTD at Building 1 Yarn Store. Alternative Travel Distance (ATD) exceeds permitted limits at: a) 83m of ATD at Building 1 Processing area. b) 69m of ATD at Building 1 Knitting 03 area. c) 85m of ATD at Building 1 knitting 01 area. d) 68m and 115m at Building 2 main store. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Travel distance | Common path of travel (CTD) distances exceeds permitted limits at: a) 39m CTD at Building 1 Accessory Store. b) 24m CTD at Building 1 GBS and PBS area. c) 73m CTD at Building 1 Yarn Store. Alternative Travel Distance (ATD) exceeds permitted limits at: a) 83m of ATD at Building 1 Processing area. b) 69m of ATD at Building 1 Knitting 03 area. c) 85m of ATD at Building 1 knitting 01 area. d) 68m and 115m at Building 2 main store. | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F6+ 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Exit access | S-5 stair discharges inside the building. | For stairs discharging within the building and those converging to other stairs prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect stair discharge corridors Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Exit access | S-5 stair discharges inside the building. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute Fire Doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All Fire Doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F8+ 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Escape doors | Escape doors are lockable in Building 1 "Common path of travel (CTD) distances exceeds permitted limits at: a) 39m CTD at Building 1 Accessory Store. b) 24m CTD at Building 1 GBS and PBS area. c) 73m CTD at Building 1 Yarn Store. Alternative Travel Distance (ATD) exceeds permitted limits at: a) 83m of ATD at Building 1 Processing area. b) 69m of ATD at Building 1 Knitting 03 area. c) 85m of ATD at Building 1 knitting 01 area. d) 68m and 115m at Building 2 main store." yarn Store, WMC, Left over area and Waste area | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-09-19 | 2025-10-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Escape doors | Escape doors are lockable in Building 1 ground floor yarn Store, WMC, Left Over Area and Waste Area. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. Remove turnstile from the escape route or provide a bypass door from the site next to turnstiles. | 3 month | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Escape doors | Escape doors are lockable in Building 1 ground floor yarn Store, WMC, Left Over Area and Waste Area. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F11 + 3 month | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Exit signage | Missing exit signs in corridor in Building 1. Missing exit signs in circulation area Building 1 and Building 2. Missing exit signs in production areas in Building 1 and Storage area Building 2. Electrically powered exit signs are not a tested and listed system. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the Floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Exit signage | Missing exit signs in corridor in Building 1. Missing exit signs in circulation area Building 1 and Building 2. Missing exit signs in production areas in Building 1 and Storage area Building 2. Electrically powered exit signs are not a tested and listed system. | Ensure that all exit signage is checked periodically and in good working condition. | F13 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Fire Rated Construction | Separation of high-risk areas | LT Room is not fire separated from production in Building 1, Transformer is not fire separated from electrical panels in Building 1, Cable rooms are not fire separated in Building 5, Control room is not fire separated from genset room in Building 5, Electrical room is not fire separated in Building 5 ETP area. Mechanical Plant is not fire separated from knitting in Building 1. Ozone room is not fire separated from production in Building 1. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). Locations of fire rated walls and doors to protect these rooms. Details of proposed fire rated walls and Fire Doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Fire Rated Construction | Separation of high-risk areas | LT Room is not fire separated from production in Building 1, Transformer is not fire separated from electrical panels in Building 1, Cable rooms are not fire separated in Building 5, Control room is not fire separated from genset room in Building 5, Electrical room is not fire separated in Building 5 ETP area. Mechanical Plant is not fire separated from knitting in Building 1. Ozone room is not fire separated from production in Building 1. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F15 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Fire Rated Construction | Separation of shafts | Lift shaft is not separated with fire rated construction in Building 1. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and Fire Doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Fire Rated Construction | Separation of shafts | Lift shaft is not separated with fire rated construction in Building 1. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F17 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Fire Rated Construction | Floor openings | Open voids connecting different levels in Building 2 display area. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Floor openings | Open voids connecting different levels in Building 2 display area. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F19 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Structural fire rating | Steel structure of the Building 2 display area is not fire resistance rated on all floors. | Factory consultant to identify level of fire protection needed for the structure based on the building height, area, provision of sprinklers and frontage space around the building, in accordance with Pakistan Accord Building Standard and reference to NFPA 5000 Section 7.6.2. Submit proposal for level of fire protection required and methods for achieving it to Pakistan Accord for review. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Structural fire rating | Steel structure of the Building 2 display area is not fire resistance rated on all floors. | Implement the proposal for addressing the fire protection of the structure based on proposal reviewed previously, and in accordance with Pakistan Accord Building Standard. | F21+ 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Storage | Storage in GBS area, Accessories store area, finishing area, yarn store area, WMC & left over area and waste store is not fire separated from production in Building 1. Store area is not fire separated from office assortment filling hall in Building 2. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors. Details of fire rated walls and Fire Doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Storage | Storage in GBS area, Accessories store area, finishing area, yarn store area, WMC & left over area and waste store is not fire separated from production in Building 1. Store area is not fire separated from office assortment filling hall in Building 2. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F23 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of occupancies | Daycare area is not fire separated from offices in Building 1, the wall separating the two occupancies is not a fire rated wall (ground floor). | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building. Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Suppression | Separation of occupancies | Daycare area is not fire separated from offices in Building 1, the wall separating the two occupancies is not a fire rated wall (ground floor). | Provide fire rated separation between occupancies by implementing the plan reviewed previously by Pakistan Accord. | F25 + 4 month | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Hazardous Materials | Chemicals storage | Chemical stores are not fire separated from production area in Building 1. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all chemical storage areas . Locations of fire rated walls and doors to protect these rooms. Details of proposed fire rated walls and Fire Doors (e.g. door listing, self-closers, door opening direction). Ventilation provisions to each of these rooms. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Hazardous Materials | Chemicals storage | Chemical stores are not fire separated from production area in Building 1. | Implement the above plan on site. All chemical storage areas to be compliant with the Accord Standard. | F27+ 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Safety Management | Emergency Action Plan | EAP document was not observed on inspection day. | Prepare an Emergency Action Plan report. | 2 month | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Safety Management | Emergency Action Plan | EAP document was not observed on inspection day. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F29 + 2 month | 2025-11-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Safety Management | Records of systems maintenance | No records of maintenance of Fire Extinguishers. No records of maintenance of Fire Doors. | Prepare maintenance schedule for all life safety systems. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Safety Management | Records of systems maintenance | No records of maintenance of Fire Extinguishers. No records of maintenance of Fire Doors. | Prepare a schedule of proposed system maintenance. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Pakistan Accord for review and approval. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Safety Management | Records of systems maintenance | No records of maintenance of Fire Extinguishers. No records of maintenance of Fire Doors. | Ensure all systems are being maintained as per the schedule agreed with Pakistan Accord. Keep maintenance records. | F32 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Safety Management | Records of system testing | No records of testing Fire Extinguishers. No records of testing Fire Doors. | Prepare testing schedule for all life safety systems. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Safety Management | Records of system testing | No records of testing Fire Extinguishers. No records of testing Fire Doors. | Identify how systems will be tested and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Safety Management | Records of system testing | No records of testing Fire Extinguishers. No records of testing Fire Doors. | Ensure all systems are being testing as per the schedule agreed with Pakistan Accord. Keep testing records. | F35 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5
| 3 | 8 |  | 346 | 421 | 6 | 5
| 3 | 8 |  | 349 | 421 | 6 | 5
| 3 | 8 |  | 350 | 421 | 6 | 5
| 3 | 8 |  | 351 | 421 | 6 | 5
| 3 | 8 |  | 352 | 421 | 6 | 5
| 3 | 8 |  | 353 | 421 | 6 | 5
| 3 | 8 |  | 354 | 421 | 6 | 5
| 3 | 8 |  | 355 | 421 | 6 | 5
| 3 | 8 |  | 356 | 421 | 6 | 5
| 3 | 8 |  | 357 | 421 | 6 | 5
| 3 | 8 |  | 358 | 421 | 6 | 5
| 3 | 8 |  | 359 | 421 | 6 | 5
| 3 | 8 |  | 360 | 421 | 6 | 5
| 3 | 8 |  | 361 | 421 | 6 | 5
| 3 | 8 |  | 362 | 421 | 6 | 5
| 3 | 8 |  | 363 | 421 | 6 | 5
| 3 | 8 |  | 364 | 421 | 6 | 5
| 3 | 8 |  | 365 | 421 | 6 | 5
| 3 | 8 |  | 366 | 421 | 6 | 5
| 3 | 8 |  | 367 | 421 | 6 | 5
| 3 | 8 |  | 368 | 421 | 6 | 5
| 3 | 8 |  | 369 | 421 | 6 | 5
| 3 | 8 |  | 370 | 421 | 6 | 5
| 3 | 8 |  | 371 | 421 | 6 | 5
| 3 | 8 |  | 372 | 421 | 6 | 5
| 3 | 8 |  | 373 | 421 | 6 | 5
| 3 | 8 |  | 374 | 421 | 6 | 5
| 3 | 8 |  | 375 | 421 | 6 | 5
| 3 | 8 |  | 376 | 421 | 6 | 5
| 3 | 8 |  | 377 | 421 | 6 | 5
| 3 | 8 |  | 378 | 421 | 6 | 5
| 3 | 8 |  | 379 | 421 | 6 | 5
| 3 | 8 |  | 380 | 421 | 6 | 5
| 3 | 8 |  | 381 | 421 | 6 | 5
| 3 | 8 |  | 382 | 421 | 6 | 5
| 3 | 8 |  | 383 | 421 | 6 | 5
| 3 | 8 |  | 384 | 421 | 6 | 5
| 3 | 8 |  | 385 | 421 | 6 | 5
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
09-Dec-2024
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Interloop Limited (HD III) - 8 Km Manga Raiwind Road, Manga Mandi, Kasur, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 09-Dec-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-25 | 2025-09-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Structural System | Lateral stability system | This issue refers to the Building 1. Building 1 has a flat slab system that requires evaluation for lateral load resistance and deflection control to ensure structural stability. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate. Submit the report to Pakistan Accord for review. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Structural System | Lateral stability system | This issue refers to the Building 1. Building 1 has a flat slab system that requires evaluation for lateral load resistance and deflection control to ensure structural stability. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary. Submit the report to Pakistan Accord for review. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Structural System | Lateral stability system | This issue refers to the Building 1. Building 1 has a flat slab system that requires evaluation for lateral load resistance and deflection control to ensure structural stability. | Propose strengthening works as required and submit the proposal to Pakistan Accord for Review. | S3 + 1 month | 2025-12-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Structural System | Lateral stability system | This issue refers to the Building 1. Building 1 has a flat slab system that requires evaluation for lateral load resistance and deflection control to ensure structural stability. | Carry out reviewed remedial works as required. | S4 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Structural System | Lateral stability system | This issue refers to the Building 2. Lateral stability system may have insufficient capacity. Building 2 was observed to beams in only one direction. A unidirectional moment resisting frame system provides less resistance to lateral loads and may reduce the ability of the structure to satisfy code requirements such as deflection limits. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate. Submit the report to Pakistan Accord for review. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Structural System | Lateral stability system | This issue refers to the Building 2. Lateral stability system may have insufficient capacity. Building 2 was observed to beams in only one direction. A unidirectional moment resisting frame system provides less resistance to lateral loads and may reduce the ability of the structure to satisfy code requirements such as deflection limits. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary. Submit the report to Pakistan Accord for review. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Structural System | Lateral stability system | This issue refers to the Building 2. Lateral stability system may have insufficient capacity. Building 2 was observed to beams in only one direction. A unidirectional moment resisting frame system provides less resistance to lateral loads and may reduce the ability of the structure to satisfy code requirements such as deflection limits. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Propose strengthening works as required and submit the proposal to Pakistan Accord for Review. | S7 + 1 months | 2025-12-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Structural System | Lateral stability system | This issue refers to the Building 2. Lateral stability system may have insufficient capacity Building 2 was observed to beams in only one direction. A unidirectional moment resisting frame system provides less resistance to lateral loads and may reduce the ability of the structure to satisfy code requirements such as deflection limits. Structural stability for a moment frame building is provided by beams and columns acting together. Where the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Carry out reviewed remedial works as required. | S8 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Structural Documentation | Documentation unavailable | The following documents were unavailable. • The drawings for Building 3 include only one floor slab reinforcement plan, while other drawings related to the roof floor and sectional details are missing. • The structural design drawings for buildings 4 and 5 are unavailable. • The stability certificates provided are for the dormitory and are also related to denim units and socks manufacturing. However, no specific building is mentioned in the hosiery division. • The structural drawings for the two-story steel structures and the steel mezzanine floor constructed in Building 2 are unavailable. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. Submit these documents to Pakistan Accord for review. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Structural Documentation | Differs from as-built structure | This issue refers to Building 1 as-built drawings. a. The plans and sections do not provide any details of the double slab. b. The plans do not include drop panels and beam framing details for the ground floor and first floor. c. The actual site condition indicates ceiling heights of 3.8 m and 5.4 m, but no sections provide details showing this height variation. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. Submit these documents to Pakistan Accord for review. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Structural Documentation | Differs from as-built structure | This following issue refers to Building 2 structural and architectural drawings. a. The two columns are not marked at Grid A17. b. There are no beams between Grid A21 and A22. c. There are no stairs opening d. No expansion joint is provided along Grid 20 between Grid A19 and A22. e. No details of steel mezzanine are provided. f. Details of RC duct are missing. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. Submit these documents to Pakistan Accord for review. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Other Damage/Defects | Health and Safety | It concerns with lack of adequate edge protection on the roof of Building 1 which present a risk of potential injury resulting from slip, trip or fall from roof and stair during the access and maintenance of services – Health & Safety concern. | Provide adequate edge protection on the roof and stairs, and on any other part of the factory with the same issue. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Other Damage/Defects | Health and Safety | It concerns with lack of adequate edge protection on the roof of Building 2 which present a risk of potential injury resulting from slip, trip or fall from roof and stair during the access and maintenance of services – Health & Safety concern. | Provide adequate edge protection on the roof and stairs, and on any other part of the factory with the same issue. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixtures
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1