## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
04-Mar-2025
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Interloop Limited Hosiery Division-II - 7Km Khurrianwala Jaranwala Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 04-Mar-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-29 | 2025-09-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | Outdated and mismatched electrical Single Line Diagrams (SLDs) found in multiple locations, including EMB-LDB-31 (Embroidery Hall 1), LT4, LT2, LT3, and various electrical rooms – lacking required updates and necessary detail including cable types (PVC/XLPE), conductor materials (CU/AL), and the earthing system. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Update the existing electrical single-line diagrams for the entire facility following the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | Outdated and mismatched electrical Single Line Diagrams (SLDs) found in multiple locations, including EMB-LDB-31 (Embroidery Hall 1), LT4, LT2, LT3, and various electrical rooms – lacking required updates and necessary detail including cable types (PVC/XLPE), conductor materials (CU/AL), and the earthing system. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Implement a regular review and update process for the single-line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4 + 4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 months | 2025-09-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6+1 month | 2026-05-23 | 2026-06-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | It was observed that several cable and circuit breaker combinations throughout the facility were mismatched, with cables undersized relative to the breaker ratings, posing serious fire and safety risks. For example, in Embroidery Hall 1 (EMB-LDB-31), a 100A incoming breaker was found feeding a 160A outgoing breaker. A 40A breaker was connected to a 4mm² cable, and a 250A breaker was supplied by a 35mm² cable at the Yarn Store Basement Unit 4. In the Knitting 1 Sub Distribution Board, a 630A breaker was connected to 2×95mm² 3.5-core cables. In the Waste Store area, a 50A breaker was found connected to a 6mm² cable, and another 250A breaker was connected to a 35mm² cable. Other discrepancies included a 44A breaker with 4mm² cable, a 70A breaker with 10mm² cable, a 400A breaker with 35mm² cable, and a 160/400A breaker connected to a 25mm² cable at LT4. Additionally, a 400A breaker was connected to 35mm² cable with no adjustability in the LT1 Knitting, and similar findings were noted in the LT Room of HD2. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Circuit breakers | During inspection of LT1 (Low Tension Panel 1), the operating lever of a circuit breaker was found to be broken. The lever is the mechanical handle used to manually switch the circuit breaker ON or OFF. A damaged lever compromises safe manual operation and could pose a safety risk during maintenance, fault isolation, or emergency shutdowns. | Replace the faulty circuit breaker or its damaged operating lever (at LT1) with a compatible and certified component. Verify proper mechanical function after replacement and conduct a safety check to ensure compliance with relevant electrical standards (e.g., BS 7671 and manufacturer guidelines). | 1 month | 2025-09-23 | 2025-10-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | The survey identified several hotspots, including the solar inverter cable in LT Room 1, Knitting 2 LT Room (yellow cable and copper bar), pump RO, RO booster pump (47°C), LT3 solar panel breaker (51°C), and LT4 compressor (43.4°C); signs of burning were observed at Knitting Unit 1 control room (200°C), motor control panel in the Powerhouse LT Room, energy division MCC panel, and multiple points within the workshop distribution board in the Powerhouse new diesel engine hall. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 week | 2025-09-23 | 2025-09-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | The survey identified several hotspots, including the solar inverter cable in LT Room 1, Knitting 2 LT Room (yellow cable and copper bar), pump RO, RO booster pump (47°C), LT3 solar panel breaker (51°C), and LT4 compressor (43.4°C); signs of burning were observed at Knitting Unit 1 control room (200°C), motor control panel in the Powerhouse LT Room, energy division MCC panel, and multiple points within the workshop distribution board in the Powerhouse new diesel engine hall. | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-09-23 | 2025-10-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Hot Spots | It was also found that the thermographic report was not available at the site. Without thermography testing, faults such as overheating components or loose connections may go unnoticed, which increases the risk of fire. Early detection through thermography can prevent fire incidents. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | E11 + 5 months | 2025-10-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | The earthing and equipotential bonding system was found inadequate across the facility. Several distribution boards lacked proper earth bonding, and cable trays, metallic panel covers, solar panel frames, stairs, and other conductive parts were not properly bonded or earth connected, posing potential safety risks. | Install earthing systems where absent, ensuring compliance with BS 7671:2018 + A2 (2022) Chapter 54, and equip all distribution boards with appropriate earthing conductors as per Section 543.1. Additionally, implement equipotential bonding for all cable trays, panel covers, solar frames, metallic stairs, and other exposed conductive parts in accordance with Regulation 411.3.1.2, ensuring all are bonded to the main earthing terminal. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | It was noted that the earth bar was incorrectly connected to the neutral bar in the boiler house electrical panel, indicating improper grounding practices. | Disconnect the earth bars from the neutral bars within the distribution boards and ensure proper separation and connection. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. | Prepare a comprehensive earthing system diagram, including identification of all earthing and neutral system components. | 8 months | 2025-09-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified as listed below: i. The earthing and equipotential bonding system was found inadequate across the facility. Several distribution boards lacked proper earth bonding, and cable trays, metallic panel covers, solar panel frames, stairs, and other conductive parts were not properly bonded or earth connected, posing potential safety risks. ii. It was noted that the earth bar was incorrectly connected to the neutral bar in the boiler house electrical panel, indicating improper grounding practices. iii. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E15 + 4 months | 2026-05-23 | 2026-09-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. The issue was noted outside 1000kVA Transformer Room and Yarn Store DB. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | Several electrical panels and cable trays exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. The issue was noted at sub accessory store, outside blower Knitting Unit 3 and, FYD steamer panel VSF Building. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | Visible signs of damage were observed on panels, cables, and busbars, including damaged insulation, broken locks, and non-functional ammeter and voltmeter displays. The issue was noted at trimming area and at one instance in LT 1, circuit breaker liver was found to be broken. | Inspect and repair or replace all damaged panels, ampere meters, voltmeters, cables, and busbars to ensure the integrity of the electrical system in accordance with BS7671 18th Edition + A2 (2022). | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | Additional concerns included missing phase separators, exposed copper busbars, congested and overcrowded electrical panels, and inadequate cable dressing in most of the distribution boards (DBs). The issue was noted at ETP plant pump 6 and pump 8, Processing-LDB-03 and Office-LDB-23. | Inspect and rectify all distribution boards with missing phase separators, exposed busbars, overcrowded wiring, and poor cable dressing. Ensure proper segregation, insulation, and cable management in compliance with BS 7671:2018 + A2 (2022). | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. The issue was noted outside 1000kVA Transformer Room and Yarn Store DB. ii. Several electrical panels and cable trays exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. The issue was noted at sub accessory store, outside blower Knitting Unit 3 and, FYD steamer panel VSF Building. iii. Visible signs of damage were observed on panels, cables, and busbars, including damaged insulation, broken locks, and non-functional ammeter and voltmeter displays. The issue was noted at trimming area and at one instance in LT 1, circuit breaker liver was found to be broken. iv. Additional concerns included missing phase separators, exposed copper busbars, congested and overcrowded electrical panels, and inadequate cable dressing in most of the distribution boards (DBs). The issue was noted at ETP plant pump 6 and pump 8, Processing-LDB-03 and Office-LDB-23. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Loop Connection | During the inspection loop connections were identified within the electrical panels. The issue was noted at the warehouse area DB, motor control panel in the Power House LT Room (including the loop between MCCBs), and the workshop DB in the new diesel engine hall of the Power House. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022) | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multi-looping was observed in the LT Room 3 Unit 4, boiler house electrical panel and, motor control panel LT Room Powerhouse. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilized to provide each circuit with the required live, neutral, and earth connections. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Openings | Unsealed openings and missing cable glands were observed in several locations, including the ETP area control room, P6 and P8 pump distribution board at the ETP plant, LT panel (photographed from cable cellar in the Powerhouse building), PPC block solar panel DB on the rooftop, assembly area auto lights panel, and the HD2 workshop DB in the new diesel engine hall of the Powerhouse. | Corrective actions are required to seal all openings and replace missing panels covers to restore the integrity and safety of the electrical systems. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Openings | Unsealed openings and missing cable glands were observed in several locations, including the ETP area control room, P6 and P8 pump distribution board at the ETP plant, LT panel (photographed from cable cellar in the Powerhouse building), PPC block solar panel DB on the rooftop, assembly area auto lights panel, and the HD2 workshop DB in the new diesel engine hall of the Powerhouse. | The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Adequate accessibility | In activewear processing hall, the placement of electrical panels adjacent to machines that continuously reject heat has caused the surrounding temperature to exceed ambient levels by several degrees. This temperature rise further increases the temperature of the panels and boards nearby. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in few of the distribution boards, panels and trunking systems. The issue was noted at control room Knitting 1 and, rewinding area LDB 15. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in few of the distribution boards, panels and trunking systems. The issue was noted at control room Knitting 1 and, rewinding area LDB 15. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system (early streamer) was provided, however, there was no study available to confirm its adequacy according to BS EN 62305 (Protection against Lightning). | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | No test results were provided for the lightning protection system, making it difficult to verify its effectiveness and compliance with relevant standards. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance requirements based on BS EN 62305 standard. Submit design calculations for the Pakistan Accord review. | E29 + 2 months | 2025-11-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | The following observations were identified with the current lightning protection system: i. A lightning protection system (early streamer) was provided, however, there was no study available to confirm its adequacy according to BS EN 62305 (Protection against Lightning). ii. No test results were provided for the lightning protection system, making it difficult to verify its effectiveness and compliance with relevant standards. | If the study finds that the current LPS is inadequate or does not comply with BS EN 62305, make the necessary upgrades to bring the system up to standard. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) across the facility was evaluated. The system included multiple addressable fire panels. However, no documentation or certification was available to verify them as listed products. The following observations were identified with the FADS: a. The addressable Fire Alarm and Detection System lacked centralized communication between fire panels, limiting coordination and overall system effectiveness. b. The cabling used for the FADS installation was not fire-rated. c. The system showed overall non-compliance with NFPA 72 standards. The following observations were made regarding the smoke detection system within the facility’s FADS: a. Smoke detectors were missing in multiple areas, including Blower Unit 3 (Ground Floor), Knitting Unit 3, Gas Boiler House Office Area, basement Cable Cellar of the Powerhouse Building, VSF LT Room (Cable Cellar), and the PPC Block Solar Inverter Area (Rooftop). b. Inappropriately located smoke detectors were observed in the Compressor Room (VSF Building) and the Boiler House. c. Broken or faulty detectors were found in the Steamer Room (VSF Building) and the Marketing Department (first floor). d. The Waste Store had inadequate detection coverage, relying solely on beam detectors. The following observations were made with regards to the Manual Call Points (MCPs): a. No MCP was installed at the exit of LT1, representing a serious gap in emergency response readiness. The following observations were made with regards to the sounders and visual alarms: a. Low audibility levels were observed in the FYD Hall, Knitting 3 (Ground Floor and first floor), and Yarn Sampling Area. b. In the Yarn Sampling and FYD Hall, visual alarm coverage was also inadequate. | Ensure the functionality and performance of the existing alarm and detection system in all the building. | 1 week | 2025-09-23 | 2025-09-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) across the facility was evaluated. The system included multiple addressable fire panels. However, no documentation or certification was available to verify them as listed products. The following observations were identified with the FADS: a. The addressable Fire Alarm and Detection System lacked centralized communication between fire panels, limiting coordination and overall system effectiveness. b. The cabling used for the FADS installation was not fire-rated. c. The system showed overall non-compliance with NFPA 72 standards. The following observations were made regarding the smoke detection system within the facility’s FADS: a. Smoke detectors were missing in multiple areas, including Blower Unit 3 (Ground Floor), Knitting Unit 3, Gas Boiler House Office Area, basement Cable Cellar of the Powerhouse Building, VSF LT Room (Cable Cellar), and the PPC Block Solar Inverter Area (Rooftop). b. Inappropriately located smoke detectors were observed in the Compressor Room (VSF Building) and the Boiler House. c. Broken or faulty detectors were found in the Steamer Room (VSF Building) and the Marketing Department (first floor). d. The Waste Store had inadequate detection coverage, relying solely on beam detectors. The following observations were made with regards to the Manual Call Points (MCPs): a. No MCP was installed at the exit of LT1, representing a serious gap in emergency response readiness. The following observations were made with regards to the sounders and visual alarms: a. Low audibility levels were observed in the FYD Hall, Knitting 3 (Ground Floor and first floor), and Yarn Sampling Area. b. In the Yarn Sampling and FYD Hall, visual alarm coverage was also inadequate. | (1) Submit design documentation for upgrading of existing FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E33 + 1 months | 2025-12-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E34 + 4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E35 + 5 months | 2026-05-23 | 2026-10-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E36 +3 months | 2026-10-23 | 2027-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E37 + 3 months | 2027-01-23 | 2027-04-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Emergency Lighting | Provided but non-functional | During the inspection, it was observed that emergency lights were installed but found to be non-functional in several locations. These included the Compressor Rooms of Unit 4 and VSF, where lights failed to operate upon testing. Similar issues were noted in the filament yarn dyeing & air covering area, knitting hall, Knitting 2 (where lights were also installed inappropriately), LT Room HD2, and the trimming area. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. Configure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Emergency Lighting | Provided but non-functional | During the inspection, it was observed that emergency lights were installed but found to be non-functional in several locations. These included the Compressor Rooms of Unit 4 and VSF, where lights failed to operate upon testing. Similar issues were noted in the filament yarn dyeing & air covering area, knitting hall, Knitting 2 (where lights were also installed inappropriately), LT Room HD2, and the trimming area. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E39 + 3 months | 2025-11-23 | 2026-02-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Emergency Lighting | Provided but insufficient | The emergency lighting system had insufficient coverage in several areas, such as Knitting 3, PPC block solar inverter area rooftop, VSF water turbine area, VSF HT room, LT1 and LT3, chemical store area, storage area aisles, activewear HT LT Room, office block first-floor stairs, yarn dyeing area stairs, and process batch store. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Emergency Lighting | Provided but insufficient | Non-illuminated exit signs were found on emergency exit doors without nearby emergency lights. Additionally, no exit directional signs were observed in the processing hall, process batch store, Knitting 2, ETP area, and corridor intersections in the office area. | All emergency exit doors should be equipped with illuminated exit signs or nearby emergency lights and exit directional signs should be provided at all points of divergence, in accordance with the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Emergency Lighting | Provided but insufficient | External emergency lighting was not provided, limiting visibility and hindering safe evacuation during nighttime emergencies—particularly outside Knitting 1. | Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s). | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Emergency Lighting | Provided but insufficient | During the inspection, the emergency lighting arrangement throughout the facility was assessed. The following observations were made: i. The emergency lighting system had insufficient coverage in several areas, such as Knitting 3, PPC block solar inverter area rooftop, VSF water turbine area, VSF HT room, LT1 and LT3, chemical store area, storage area aisles, activewear HT LT Room, office block first-floor stairs, yarn dyeing area stairs, and process batch store. ii. Non-illuminated exit signs were found on emergency exit doors without nearby emergency lights. Additionally, no exit directional signs were observed in the processing hall, process batch store, Knitting 2, ETP area, and corridor intersections in the office area. iii. External emergency lighting was not provided, limiting visibility and hindering safe evacuation during nighttime emergencies—particularly outside Knitting 1. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E41 + 4 month | 2026-03-23 | 2026-07-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E45 + 2 months | 2026-01-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | The ventilation system was found to be inadequate, resulting in insufficient airflow and noticeable heat accumulation—particularly around the transformer areas in Knitting 1 LT Room and LT 3. | Hire a qualified engineer to reassess the existing ventilation system, ensuring that the critical areas around the electrical panels and transformer receive adequate ventilation. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | Several sections of the rooms, including activewear LT Room, LT 4, and LT 3, were poorly illuminated, with light levels falling below the minimum required for safe operation and maintenance tasks. | Add more lighting fixtures in poorly lit areas to ensure even distribution of light throughout the room. Focus on areas that require the highest visibility, such as around equipment and control panels. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | i. The ventilation system was found to be inadequate, resulting in insufficient airflow and noticeable heat accumulation—particularly around the transformer areas in Knitting 1 LT Room and LT 3. ii. Several sections of the rooms, including activewear LT Room, LT 4, and LT 3, were poorly illuminated, with light levels falling below the minimum required for safe operation and maintenance tasks. | Establish regular maintenance and testing of the ventilation system and luminaires within the spaces to ensure adequate performance. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Generator, Transformer & Sub-Station Room | Working clearance | During the inspection, it was observed that the working clearance was inadequate in Powerhouse LT Room. Equipment was placed too close to technician workstation, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. | Reorganize the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Generator, Transformer & Sub-Station Room | Working clearance | During the inspection, it was observed that the working clearance was inadequate in Powerhouse LT Room. Equipment was placed too close to technician workstation, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. | Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Generator, Transformer & Sub-Station Room | Transformer arcing horn | During the inspection, it was observed that the upper portion of the arcing horn near the terminal was missing on the transformer located near the Research and Innovation Department. | Immediate inspection of the transformer near the Research and Innovation Department is required to assess and address the missing upper portion of the arcing horn. Repair or replacement of the affected component should be carried out without delay to maintain equipment safety and reliability. | 1 week | 2025-09-23 | 2025-09-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Generator, Transformer & Sub-Station Room | Transformer arcing horn | During the inspection, it was observed that the upper portion of the arcing horn near the terminal was missing on the transformer located near the Research and Innovation Department. | Replace the corroded and worn arcing horn to prevent further damage and mitigate the risk of electrical faults and fires. Inspect and clean any associated components to ensure proper function and safety. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Generator, Transformer & Sub-Station Room | Transformer arcing horn | During the inspection, it was observed that the upper portion of the arcing horn near the terminal was missing on the transformer located near the Research and Innovation Department. | Establish a routine maintenance schedule for regular inspection and servicing of the arcing horn and related components. Implement measures for early detection of wear and corrosion, such as periodic testing and monitoring, to ensure the arcing horn remains in optimal condition and effectively prevents arcing-related damage. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Generator, Transformer & Sub-Station Room | Room separation | It was observed that the separation between the generator, transformer, and substation areas was inadequate across multiple locations in the facility. Physical barriers between HT, LT, and generator equipment were either missing or insufficient, with noticeable gaps and openings that could facilitate the propagation of fire or electrical faults between sections. In some instances, partitions were constructed using materials that did not comply with required fire resistance standards, further increasing the risk during an incident. These deficiencies were noted at the following locations: HT panel, transformer and LT panel area with no separation, LT Room 2 in Unit 4 ground floor, activewear LT Room where HT and LT equipment shared the same space, Power House HT and LT Room, Power House new diesel engine hall where LT generator, LT panel, and step-up transformer were located in close proximity, LT4 with little gap between LT panel and HT and between LT panels and transformer, LT3 with no separation between LT, HT, and transformer, VSF LT Room, and LT1. | Install temporary fire-resistant barriers and seal any gaps and openings between the generator, transformer, and substation areas to immediately reduce the risk of fire and electrical fault propagation. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Generator, Transformer & Sub-Station Room | Room separation | It was observed that the separation between the generator, transformer, and substation areas was inadequate across multiple locations in the facility. Physical barriers between HT, LT, and generator equipment were either missing or insufficient, with noticeable gaps and openings that could facilitate the propagation of fire or electrical faults between sections. In some instances, partitions were constructed using materials that did not comply with required fire resistance standards, further increasing the risk during an incident. These deficiencies were noted at the following locations: HT panel, transformer and LT panel area with no separation, LT Room 2 in Unit 4 ground floor, activewear LT Room where HT and LT equipment shared the same space, Power House HT and LT Room, Power House new diesel engine hall where LT generator, LT panel, and step-up transformer were located in close proximity, LT4 with little gap between LT panel and HT and between LT panels and transformer, LT3 with no separation between LT, HT, and transformer, VSF LT Room, and LT1. | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Generator, Transformer & Sub-Station Room | Battery | It was observed that in the energy division Generator Room, battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 1 month | 2025-09-23 | 2025-10-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Generator, Transformer & Sub-Station Room | Battery | It was observed that in the energy division Generator Room, battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables, which were found hanging along the walls—particularly in LT1, Activewear LT Room and the cable cellar in the Powerhouse building basement. Inadequate cable support can lead to cable sagging or stress, increasing the risk of damage or failure. Additionally, one cable's insulation was found damaged due to improper laying in the cable tray at the 1000 kVA Transformer Room in the Powerhouse, further raising the risk of electrical hazards. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E60 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables, which were found hanging along the walls—particularly in LT1, Activewear LT Room and the cable cellar in the Powerhouse building basement. Inadequate cable support can lead to cable sagging or stress, increasing the risk of damage or failure. Additionally, one cable's insulation was found damaged due to improper laying in the cable tray at the 1000 kVA Transformer Room in the Powerhouse, further raising the risk of electrical hazards. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | E59 + 3 months | 2025-12-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 370 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Cables support and protection | It was observed that the cable trays in the Powerhouse Transformer Room, LT3, and the Powerhouse cable cellar were inadequately supported and at risk of falling. This presents a significant safety hazard and could potentially damage the electrical system. | Provide adequate support for the cable trays installed in the factory to prevent them from falling and ensure the safety and integrity of the electrical system, in compliance with BS 7671 18th Edition + A2 (2022) Regulation 522.8.5. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E62 | Cabling & Wiring | Cables support and protection | It was observed that the cable trays in the Powerhouse Transformer Room, LT3, and the Powerhouse cable cellar were inadequately supported and at risk of falling. This presents a significant safety hazard and could potentially damage the electrical system. | Securely support all inadequately fixed cable trays in the Powerhouse Transformer Room, LT3, and the cable cellar to eliminate the risk of collapse. Establish a routine inspection schedule to ensure ongoing structural integrity and prevent potential hazards to the electrical system. | E59 + 3 months | 2025-12-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 371 | 421 | 6 | 5 |  | Initial | [11 empty] | E63 | Cabling & Wiring | Cables support and protection | Rusted cable trays were observed. Corroded trays reduce mechanical strength and can eventually fail, potentially leading to exposed cables, short circuits, or electrical hazards. The issue was noted at Powerhouse outside area | Replace all rusted cable trays to maintain the structural integrity of the cable containment system and to prevent eventual collapse or exposure of live conductors. Use corrosion-resistant materials in areas prone to moisture or outdoor exposure. (Reference: BS EN 61537 and BS 7671 18th Edition + A2 (2022) Regulation 522.8.1 for selection of suitable materials). | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E64 | Cabling & Wiring | Cables support and protection | Rusted cable trays were observed. Corroded trays reduce mechanical strength and can eventually fail, potentially leading to exposed cables, short circuits, or electrical hazards. The issue was noted at Powerhouse outside area | Replace all rusted cable trays with corrosion-resistant alternatives and develop a preventive maintenance program to monitor and address early signs of corrosion in susceptible areas. | E59 + 3 months | 2025-12-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E65 | Cabling & Wiring | Cable trench and channel cleanliness | During the facility inspection, it was observed that the cable trunking systems were not adequately maintained in terms of cleanliness. Multiple trunking routes were found to contain a considerable accumulation of fluff and dust, presenting a significant fire hazard. The issue was noted at the server room (Merchandising VSF), Generator Room, cable cellar (Powerhouse building basement), and processing LT Room. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 1 month | 2025-09-23 | 2025-10-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 374 | 421 | 6 | 5 |  | Initial | [11 empty] | E66 | Cabling & Wiring | Cable trench and channel cleanliness | During the facility inspection, it was observed that the cable trunking systems were not adequately maintained in terms of cleanliness. Multiple trunking routes were found to contain a considerable accumulation of fluff and dust, presenting a significant fire hazard. The issue was noted at the server room (Merchandising VSF), Generator Room, cable cellar (Powerhouse building basement), and processing LT Room. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | E65 + 4 months | 2025-10-23 | 2026-02-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 375 | 421 | 6 | 5 |  | Initial | [11 empty] | E67 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at accessory store AS-LDB-28, processing area P-LDB-03, office area OFC-LDB-23, motor control panel Powerhouse LT Room and boiler house control panel. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E68 |  | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at accessory store AS-LDB-28, processing area P-LDB-03, office area OFC-LDB-23, motor control panel Powerhouse LT Room and boiler house control panel. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 376 | 421 | 6 | 5 |  | Initial | [11 empty] | E69 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at new diesel engine hall workshop DB Powerhouse and Knitting 2 distribution board. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 377 | 421 | 6 | 5 |  | Initial | [11 empty] | E70 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at new diesel engine hall workshop DB Powerhouse and Knitting 2 distribution board. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 378 | 421 | 6 | 5 |  | Initial | [11 empty] | E71 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable color coding practices were identified. The issue was noted at Yarn Store distribution board, Knitting 2 LT Room and motor control panel LT Room Power House. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 379 | 421 | 6 | 5 |  | Initial | [11 empty] | E72 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. The issue was noted at Yarn Store distribution board, Knitting 2 LT Room and motor control panel LT Room Power House. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | E71 + 2 months | 2026-01-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 380 | 421 | 6 | 5 |  | Initial | [11 empty] | E73 | Cabling & Wiring | Fixtures | Light fixtures hung by their own cables: This presents a safety hazard as the cable is not designed to bear the weight of the fixture. Over time, this can lead to mechanical stress, damaged insulation, or exposed conductors, increasing the risk of electrical shock or fire. The issue was noted at compressor room VSF Building. | Secure the loose lighting fixtures with appropriate fixed supports to prevent movement and ensure stable connections. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 381 | 421 | 6 | 5 |  | Initial | [11 empty] | E74 | Cabling & Wiring | Fixtures | Light fixtures hung by their own cables: This presents a safety hazard as the cable is not designed to bear the weight of the fixture. Over time, this can lead to mechanical stress, damaged insulation, or exposed conductors, increasing the risk of electrical shock or fire. The issue was noted at compressor room VSF Building. | Implement a regular inspection and maintenance schedule to check and secure all lighting fixtures, ensuring they remain safely and correctly installed. | E73 + 6 months | 2025-12-23 | 2026-06-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 382 | 421 | 6 | 5 |  | Initial | [11 empty] | E75 | Cabling & Wiring | Fixtures | Uncovered or improperly enclosed junction boxes: Exposed or uncovered junction boxes can leave live wires and connections unprotected. This significantly increases the risk of electrical shock, short circuits, and fire, especially in areas with dust, moisture, or physical interference. The issue was noted at Marketing Building ground floor. | Replace or repair broken and exposed junction boxes immediately to restore safe and secure connections. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 383 | 421 | 6 | 5 |  | Initial | [11 empty] | E76 | Cabling & Wiring | Fixtures | Uncovered or improperly enclosed junction boxes: Exposed or uncovered junction boxes can leave live wires and connections unprotected. This significantly increases the risk of electrical shock, short circuits, and fire, especially in areas with dust, moisture, or physical interference. The issue was noted at Marketing Building ground floor. | Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. | E75 + 6 months | 2025-12-23 | 2026-06-23 | AGREE |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
04-Mar-2025
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Interloop Limited Hosiery Division-II - 7Km Khurrianwala Jaranwala Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 04-Mar-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-29 | 2025-09-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | - Escape doors found lockable at various locations across the facility. - Sliding doors/ rolling shutter doors in escape route serving more than 10 occupants found in Mosque area FYD Building, hall 2 Level Ground Knitting 4 Building. - Escape doors in Canteen Building level ground found locked. - Escape door swing against the direction of escape in lab FYD Building. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-09-23 | 2025-10-07 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | - Escape doors found lockable at various locations across the facility. - Sliding doors/ rolling shutter doors in escape route serving more than 10 occupants found in Mosque area FYD Building, hall 2 Level Ground Knitting 4 Building. - Escape doors in Canteen Building level ground found locked. - Escape door swing against the direction of escape in lab FYD Building. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | - Escape doors found lockable at various locations across the facility. - Sliding doors/ rolling shutter doors in escape route serving more than 10 occupants found in mosque area FYD Building, hall 2 level ground Knitting 4 Building. - Escape doors in Canteen Building level ground found locked. - Escape door swing against the direction of escape in lab FYD Building. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3+3 months | 2025-12-23 | 2026-03-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | - Protected stairs S3, S10, S16, S17, S19, S-33, S39, and S43 discharges inside the building at a distance from building exit. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | - Protected stairs S3, S10, S16, S17, S19, S-33, S39, and S43 discharges inside the building at a distance from building exit. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F5+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits in: - Knitting 01 Building level 1 office area with total common path distance of 50.5 m. - Office block Knitting 04 Building with total common path distance of 28 m at two locations. - Processing and Yarn Dyeing Building with total common path distance of 25.6 m. - Admin Building level 1 with total common path distance of 17 m. - Utility Building Unit 4 Basement with total common path distance of 60.6 m. - Travel distance to the nearest of alternative exits exceeds distance limits in - Knitting 04 Building with total alternative path distance of 69 m. - Finishing Building with total alternative path distance of 62 m. | Reduce the common path of travel distance to a maximum of 46 m in the areas with higher common path of travel or vacate the area until the travel distance is reduced. | 2 weeks | 2025-09-23 | 2025-10-07 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits in: - Knitting 01 Building level 1 office area with total common path distance of 50.5 m. - Office block Knitting 04 Building with total common path distance of 28 m at two locations. - Processing and Yarn Dyeing Building with total common path distance of 25.6 m. - Admin Building level 1 with total common path distance of 17 m. - Utility Building Unit 4 Basement with total common path distance of 60.6 m. - Travel distance to the nearest of alternative exits exceeds distance limits in - Knitting 04 Building with total alternative path distance of 69 m. - Finishing Building with total alternative path distance of 62 m. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification work on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits in: - Knitting 01 Building level 1 office area with total common path distance of 50.5 m. - Office block Knitting 04 Building with total common path distance of 28 m at two locations. - Processing and Yarn Dyeing Building with total common path distance of 25.6 m. - Admin Building level 1 with total common path distance of 17 m. - Utility Building Unit 4 Basement with total common path distance of 60.6 m. - Travel distance to the nearest of alternative exits exceeds distance limits in - Knitting 04 Building with total alternative path distance of 69 m. - Finishing Building with total alternative path distance of 62 m. | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | F8+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Protection of stairs | - Missing fire rated enclosure and Fire door at staircase S13, S17, S19, S23, S25, S30, S33, S45. - Unprotected openings into stairs S1, S3, S4, S5, S6, S7, S8, S10, S11, S14, S15, S18, S20, S21, S22, S24, S31, S35, S36, S38, S43, S45 (in form of ventilation fans basement). - Doors are not fire rated doors in most of the stairs except stairs with signage as emergency exits. - Staircase S26 and S29 are not a part of evacuation plan, however it is not enclosed in fire rated construction and missing fire rated door assemblies and is a floor opening between ground and level 1. - Fire load in staircase S13, S26, S27, S33. | Remove fire load from the staircase and keep them clear from obstructions. | 2 weeks | 2025-09-23 | 2025-10-07 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Protection of stairs | - Missing fire rated enclosure and Fire door at staircase S13, S17, S19, S23, S25, S30, S33, S45. - Unprotected openings into stairs S1, S3, S4, S5, S6, S7, S8, S10, S11, S14, S15, S18, S20, S21, S22, S24, S31, S35, S36, S38, S43, S45 (in form of ventilation fans basement). - Doors are not fire rated doors in most of the stairs except stairs with signage as emergency exits. - Staircase S26 and S29 are not a part of evacuation plan, however it is not enclosed in fire rated construction and missing fire rated door assemblies and is a floor opening between ground and level 1. - Fire load in staircase S13, S26, S27, S33. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Protection of stairs | - Missing fire rated enclosure and Fire door at staircase S13, S17, S19, S23, S25, S30, S33, S45. - Unprotected openings into stairs S1, S3, S4, S5, S6, S7, S8, S10, S11, S14, S15, S18, S20, S21, S22, S24, S31, S35, S36, S38, S43, S45 (in form of ventilation fans basement). - Doors are not fire rated doors in most of the stairs except stairs with signage as emergency exits. - Staircase S26 and S29 are not a part of evacuation plan, however it is not enclosed in fire rated construction and missing fire rated door assemblies and is a floor opening between ground and level 1. - Fire load in staircase S13, S26, S27, S33. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F11+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Escape stair condition | There are missing handrails in S21 and S22. | Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Exit discharge | External escape / discharge from Powerhouse is not fire separated from boiler. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes. - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Exit discharge | External escape / discharge from Powerhouse is not fire separated from boiler. | Ensure external escape routes do not pass close to unprotected high risk areas. | F14+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Exit signage | - Missing exit signage for entry into stair S45, S46. - Missing exit signs in production areas at multiple locations across the facility and the Warehouse Building. - Missing exit signs in offices and back of house areas in Knitting 04 Building and VSF Marketing Buildings. - Misleading signage at office block Knitting 4 Building. - Electrically powered exit signs are not a tested and listed system. - Exits signs are not consistent some are red and others green. | Remove misleading directional escape signs. | 2 weeks | 2025-09-23 | 2025-10-07 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Means of Escape | Exit signage | - Missing exit signage for entry into stair S45, S46. - Missing exit signs in production areas at multiple locations across the facility and the Warehouse Building. - Missing exit signs in offices and back of house areas in Knitting 04 Building and VSF Marketing Buildings. - Misleading signage at office block Knitting 4 Building. - Electrically powered exit signs are not a tested and listed system. - Exits signs are not consistent some are red and others green. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Means of Escape | Exit signage | - Missing exit signage for entry into stair S45, S46. - Missing exit signs in production areas at multiple locations across the facility and the Warehouse Building. - Missing exit signs in offices and back of house areas in Knitting 04 Building and VSF Marketing Buildings. - Misleading signage at office block Knitting 4 Building. - Electrically powered exit signs are not a tested and listed system. - Exits signs are not consistent some are red and others green. | Ensure that all exit signage is checked periodically and in good working condition. | F17+3 months | 2025-12-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Fire Rated Construction | Separation of high-risk areas | - RO Plant not separated from Chemical Store in FYD Building. - workshop not separated from Compressor Room in FYD building. - Mechanical plant not fire Separate from knitting area in Activewear Building. - Activewear Building mechanical plant not separated from production. - Battery charging stations for forklifts is not fire separated from storage area/warehouse in Warehouse Building. - Cooking area is not fire separated from dining area in Canteen Building. - Knitting 04 Building IT Room is not fire separated from office area on level 1. - Utility building Unit 02 transformer is not fire separated from HT panels. - Electrical panels/rooms not fire separated from storage in Warehouse Building, from production in Knitting 02 Building. - Compressor areas in all Knitting buildings are not fire separated from production. - Transformer is not fire separated from IT Room in Knitting 03 Building, from LT Utility Building Unit 02, from generators in Powerhouse Building. - Data center is not fire separated from production Knitting 01 Building level 1. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Separation of high-risk areas | - RO Plant not separated from Chemical Store in FYD Building. - workshop not separated from Compressor Room in FYD building. - Mechanical plant not fire Separate from knitting area in Activewear Building. - Activewear Building mechanical plant not separated from production. - Battery charging stations for forklifts is not fire separated from storage area/warehouse in Warehouse Building. - Cooking area is not fire separated from dining area in Canteen Building. - Knitting 04 Building IT Room is not fire separated from office area on level 1. - Utility building Unit 02 transformer is not fire separated from HT panels. - Electrical panels/rooms not fire separated from storage in Warehouse Building, from production in Knitting 02 Building. - Compressor areas in all Knitting buildings are not fire separated from production. - Transformer is not fire separated from IT Room in Knitting 03 Building, from LT Utility Building Unit 02, from generators in Powerhouse Building. - Data center is not fire separated from production Knitting 01 Building level 1. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F19+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Separation of shafts | - Lift shafts across the facility are not separated with fire rated construction. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Separation of shafts | - Lift shafts across the facility are not separated with fire rated construction. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F21+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Floor openings | - Open voids connecting different levels at VSF building connecting level 1 and ground and New Marketing Offices. - Staircase S23, S26 and S29 are not a part of evacuation plan, however it is not enclosed in fire rated construction and missing fire rated door assemblies and is a floor opening between ground and level 1. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Floor openings | - Open voids connecting different levels at VSF building connecting level 1 and ground and New Marketing Offices. - Staircase S23, S26 and S29 are not a part of evacuation plan, however it is not enclosed in fire rated construction and missing fire rated door assemblies and is a floor opening between ground and level 1. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F23+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of occupancies | - Basement is not fire separated from the rest of the building in Utility Building Unit 4. - Large office areas not fire separated from the production areas in Knitting 04 Building office block. - Offices not fire separated from production in Processing and Yarn Dyeing Building. - Warehouse Building IT Room not fire separated from office and storage area is not fire separated from office. - Prayer area is not fire separated from production in VSF Marketing Building. - Marketing offices not fire separated from production in VSF Marketing Building. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification work. The drawings should cover: - Different occupancy types in the building. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Separation of occupancies | - Basement is not fire separated from the rest of the building in Utility Building Unit 4. - Large office areas not fire separated from the production areas in Knitting 04 Building office block. - Offices not fire separated from production in Processing and Yarn Dyeing Building. - Warehouse Building IT Room not fire separated from office and storage area is not fire separated from office. - Prayer area is not fire separated from production in VSF Marketing Building. - Marketing offices not fire separated from production in VSF Marketing Building. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F25+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Storage | Storage areas are not fire separated from: - Winding Store at elastomeric hall FYD Building. - Cooking area Canteen Building,. - Knitting Store VSF Marketing Building. - Store not fire separated from offices New Marketing Offices level 1. - Storage from embroidery in Finishing Building. - Process Batch Store from boarding in Finishing Building. - Yarn Dyeing Store from rewinding and processing and on other side ac plant. room in Processing and Yarn Dyeing Building. - FGS Store not fire Separate in Activewear Building. - AW store at Knitting 03 Building level 1. - FGS Store ground level Knitting 01 Building. - Record room Knitting 01 Building level 1. - Store at Knitting 02 Building level 1. - Store from production ground level Knitting 02 Building. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) including, Knitting 01 Building at ground level and fqc area Finishing Building, | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification work. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Rated Construction | Storage | Storage areas are not fire separated from: - Winding Store at elastomeric hall FYD Building. - Cooking area Canteen Building,. - Knitting Store VSF Marketing Building. - Store not fire separated from offices New Marketing Offices level 1. - Storage from embroidery in Finishing Building. - Process Batch Store from boarding in Finishing Building. - Yarn Dyeing Store from rewinding and processing and on other side ac plant. room in Processing and Yarn Dyeing Building. - FGS Store not fire Separate in Activewear Building. - aw store at Knitting 03 Building level 1, - FGS Store ground level Knitting 01 Building, - Record room Knitting 01 Building level 1 - Store at Knitting 02 Building level 1, - Store from production ground level Knitting 02 Building, - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) including, Knitting 01 Building at ground level and fqc area Finishing Building, | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F27+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Hazardous Materials | Chemicals handling | - Large amounts of chemicals in production areas of Processing and Yarn Dyeing Building. | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Hazardous Materials | Chemicals handling | - Large amounts of chemicals in production areas of Processing and Yarn Dyeing Building. | Implement the chemical handling strategy on site as agreed with Accord. | F29+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room at FYD Building. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of all chemical storage areas . - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. | 4 months | 2025-09-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room at FYD Building. | Implement the above plan on site. All chemical storage areas to be compliant with Pakistan Accord Standard. | F31+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Safety Management | Records of system testing | - Inadequate Record of testing of Fire Doors. | - Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Safety Management | Records of system testing | - Inadequate Record of testing of Fire Doors. | - Ensure all systems are being tested as per the schedule agreed with Accord. - Keep testing records. | F33+3 months | 2025-12-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance for Fire Extinguishers. - Inadequate records of maintenance for Fire Doors. | - Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance for Fire Extinguishers. - Inadequate records of maintenance for Fire Doors. | Ensure all systems are being maintained as per the schedule agreed with Accord . - Keep maintenance records. | F35+3 months | 2025-12-23 | 2026-03-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Safety Management | Emergency Action Plan | - There is an EAP document available however, it does not details the procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-09-23 | 2025-11-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Safety Management | Emergency Action Plan | - There is an EAP document available however, it does not details the procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F37+2 months | 2025-11-23 | 2026-01-23 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5
| 3 | 8 |  | 374 | 421 | 6 | 5
| 3 | 8 |  | 375 | 421 | 6 | 5
| 3 | 8 |  | 376 | 421 | 6 | 5
| 3 | 8 |  | 377 | 421 | 6 | 5
| 3 | 8 |  | 378 | 421 | 6 | 5
| 3 | 8 |  | 379 | 421 | 6 | 5
| 3 | 8 |  | 380 | 421 | 6 | 5
| 3 | 8 |  | 381 | 421 | 6 | 5
| 3 | 8 |  | 382 | 421 | 6 | 5
| 3 | 8 |  | 383 | 421 | 6 | 5
| 3 | 8 |  | 384 | 421 | 6 | 5
| 3 | 8 |  | 385 | 421 | 6 | 5
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
04-Mar-2025
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Interloop Limited Hosiery Division-II - 7Km Khurrianwala Jaranwala Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 04-Mar-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-29 | 2025-09-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Structural System | Lateral stability system | This refers to Knitting 2 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate and submit the report to Pakistan Accord for review. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Structural System | Lateral stability system | This refers to Knitting 2 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Structural System | Lateral stability system | This refers to Knitting 2 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced. | Propose strengthening work if required. | S3+1 month | 2025-12-23 | 2026-01-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Structural System | Lateral stability system | This refers to Knitting 2 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced. | Carry out remedial work as required. | S4+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Structural System | Lateral stability system | This refers to Knitting 3 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate and submit the report to Pakistan Accord for review. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Structural System | Lateral stability system | This refers to Knitting 3 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 3 months | 2025-09-23 | 2025-12-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Structural System | Lateral stability system | This refers to Knitting 3 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced | Propose strengthening work if required. | S7+1 month | 2025-12-23 | 2026-01-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Structural System | Lateral stability system | This refers to Knitting 3 Building (knitting hall area) where structural stability for the building is provided by beams and columns acting together in one direction only, while the beams are omitted in the shorter direction on all floors. As a result, the ability of this system to resist lateral loads in that direction is reduced | Carry out remedial work as required. | S8+4 months | 2026-01-23 | 2026-05-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Other Damage/Defects | Health and Safety | This concerns inadequate edge protection on roof of Finishing, VSF Marketing, Admin Block and R&I buildings where ac outer are placed. This creates a risk of injury resulting from trip or fall – Health & Safety concern. | Provide adequate edge protection on roof. Ensure similar measures are implemented in any other factory areas where these safety concerns exist. | 1 month | 2025-09-23 | 2025-10-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Structural Documentation | Documentation unavailable | This issue refers to all Main buildings of the factory. The structural design drawings of the buildings are unavailable or incomplete. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built structural drawings. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Structural Documentation | Lack of safe load plans | This refers to the building Knitting-01, Knitting-02, Knitting-03, Knitting-04, Processing & Yarn Dyeing, Finishing, Warehouse, VSP Marketing, New Marketing Offices, Admin Block, Canteen, Office Block, Powerhouse and Record Room Building where no safe load plans were posted all over the building. | Building structural engineer to review design documentation to confirm load capacity of the structure. | 6 months | 2025-09-23 | 2026-03-23 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Structural Documentation | Lack of safe load plans | This refers to the building Knitting-01, Knitting-02, Knitting-03, Knitting-04, Processing & Yarn Dyeing, Finishing, Warehouse, VSP Marketing, New Marketing Offices, Admin Block, Canteen, Office Block, Powerhouse and Record Room Building where no safe load plans were posted all over the building. | Factory to post safe load plans on each floor. | S12+1 month | 2026-03-23 | 2026-04-23 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixtures
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1