## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
24-Oct-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Lucky Textile Mills Limited Unit L-12, Plot No. L-3, Block-21, Federal-B Area, Karachi City, Sindh, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 24-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed abnormally high temperatures in multiple locations, among those observed were the following (non-exclusive): - Cargo lift control panel - Main Building on level(s) L03 - Third Floor - Admin/Office on level(s) L00 - Ground Floor - Canteen on level(s) L01 - First Floor | Inspect the electrical panel to identify the source of abnormal temperatures. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components | 1 month | Work is in progress as it is a continuous improvement process. We are rectifying the causes of hot spots as soon as possible. Hotspots removed from mentioned areas, except Admin/Office on level(s) L00 - Ground Floor as work is in progress. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed abnormally high temperatures in multiple locations, among those observed were the following (non-exclusive): - Cargo lift control panel - Main Building on level(s) L03 - Third Floor - Admin/Office on level(s) L00 - Ground Floor - Canteen on level(s) L01 - First Floor | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 6 months. | E1 + 1 month | We conduct thermography on a quarterly basis according to the schedule. Factory will share schedule with Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed abnormally high temperatures in multiple locations, among those observed were the following (non-exclusive): - Cargo lift control panel - Main Building on level(s) L03 - Third Floor - Admin/Office on level(s) L00 - Ground Floor - Canteen on level(s) L01 - First Floor | Carry out independent thermographic surveys as per schedule. | 6 months | We conduct thermography on a quarterly basis according to the schedule. Factory will share thermography report with Pakistan Accord at least every 6 months |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | Breakers installed were observed that did not provide adequate protection for connected cables eg. - Main Building on level(s) L03 - Third Floor, a 6mm2 cable was connected to a 60A breaker | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes. | 3 months | Work is in progress and qualified electrical engineer will be hired in the current month of june-2024. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Circuit breakers | Breakers installed were observed that did not provide adequate protection for connected cables eg. - Main Building on level(s) L03 - Third Floor, a 6mm2 cable was connected to a 60A breaker | Replace cables with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 3 months | Work in progress and qualified electrical engineer will be hired in the current month of june-2024. Factory will replace cables with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. | 3 months | Factory will seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. 80% of opening are sealed and rest 20% work in progress. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | Cabling & Wiring | Cable size | Main Building on level(s) L00 - Ground Floor, some internal fixed wiring was observed at elevated temperatures compared to the incoming wiring | Factory to appoint a qualified electrical engineer to check the cable size for internal wiring for all panels. | 1 month | Work in progress and qualified electrical engineer will be hired in the current month of june-2024. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | Cabling & Wiring | Cable size | Main Building on level(s) L00 - Ground Floor, some internal fixed wiring was observed at elevated temperatures compared to the incoming wiring | Factory to implement advice of the qualified electrical engineer regarding cable size of fixed wiring and replace wiring as necessary | 3 months | Work in progress and qualified electrical engineer will be hired in the current month of june-2024. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | Diagrams & Drawings | Electrical layout drawing | No updated "As built" Electrical Layout Drawings were available at the factory. There were no single line diagrams showing how the overall system is connected. Some drawings are printed at A4 which are too small to be able to read the details. | Provide updated Electrical layout drawing that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation | 8 months | we have floor wise lighting and power layouts as attached for review and further advise. Provide will updated Electrical layout drawings and submit to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. Some of the related issues include: - Incomplete coverage of fire alarm devices in all/some areas - Fire alarm devices not listed including hooters and PA system - Detectors incorrectly installed - Detector devices in disrepair, spray painted over, not installed top of stairs - Unable to confirm if fire alarm panel is listed - Sounders inaudible due to low volume, or without distinctive audible signals | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Factory will submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E10 + 1 month | Factory will submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components that may be required |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E11 + 4 months | Factory will submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, has been inhoused |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E12 + 5 months | Factory will submit full "as-built" documentation of the system to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E14 + 3 months | Factory Will advise Pakistan Accord when FADS installation fully completed and ready for review. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E15 + 3 months | Factory will provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Emergency Lighting | Provided but insufficient | The emergency lighting was observed to be insufficient throughout all buildings, eg. - Approximately half the emergency lights tested did not function in test - Emergency lighting did not operate unless the main breaker for the area was tripped - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs | Test the emergency lighting system on each floor, repeat tests at regular intervals and maintain test records. | 3 months | LTML H.S.E team jointly conduct inspection of emergency lights with Engineering team and update the documentation for records. Factory will share test records with Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Emergency Lighting | Provided but insufficient | The emergency lighting was observed to be insufficient throughout all building sites and/or at exit stairs | Provide additional emergency fixtures to supply adequate illumination along the means of egress, with an emergency lighting system that meets the requirements of the Pakistan Building Code and NFPA 101. Ensure emergency lighting that automatically turns on within 1s of the failure of the normal lighting supply. | 3 months | we have installed emergency lights on every exit stairs as well as on streets for the sufficient illumination as per compliance. Further, work in progress. Factory will ensure emergency lighting that automatically turns on within 1s of the failure of the normal lighting supply. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
24-Oct-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Lucky Textile Mills Limited Unit L-12, Plot No. L-3, Block-21, Federal-B Area, Karachi City, Sindh, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 24-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard | 1 month | All non-compliant locking mechanisms will be removed from egress path doors upon approval of new locking devices, and replaced with compliant ones on a sequential basis, ensuring uninterrupted safety and accessibility. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 2 months | For single Leaf doors panic bar or similar arrangements will ensure inside and cam locks arrangement from outside which gets override upon trigger of panic bar from inside. For double leaf doors same locking arrangement will ensure as in single leaf doors through wicket door provisions. Locking Mechanism specifications link is provided below for ACCORD review & approval: Door Locking Details: https://elocksecurity.com/product/double-cylinders-electromechanical-door-lock-es1073g-2 |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Protection of stairs | Exit stairways not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as needed. | 1 month | HSE team has completed a comprehensive inspection of all fire doors in accordance with NFPA-80. The inspection revealed that all fire doors are properly equipped with automatic door closers and are free from any obstructions or holding materials, ensuring full compliance with the standard. (Inspection Report is attached for perusal - Annexure 'A") |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Exit stairways not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Provide a fire rated separation between the stair and the conduit, duct, etc., or relocate services so that they no longer penetrate the exit enclosure. Close any gaps with listed/approved products with the appropriate fire rating. Remove equipment and services not serving stairway from stairway, or provide construction to separate equipment and service by construction having a fire resistance rating not less than that required for the exit enclosure. Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements | 4 months | All existing openings utilized for ventilation purposes adjacent to exit stairs, currently lacking proper protection, require installation of fire retardant louvers / dampers. We will share the design & technical specifications to Accord for review and approval. HSE conducted survey of the Emergency exit routes to assess the ingress of utilities, services and ducts. There are total 04 emergency exit routes at each floor and all of them are free of any obstructions like “Utilities, services, installations, cable trays & ducts etc.” (Pictorial Evidences & Report is attached - Annexure 'B'). |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Provide fire rated protective enclosure to the staircase in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies Provide all fire doors with self-closing and self-latching devices, and push-bar panic hardware where required in accordance with Pakistan Accord Building Standard. If fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system | F4+4 months | All existing openings utilized for ventilation purposes adjacent to exit stairs, currently lacking proper protection, require installation of fire retardant louvers & dampers. We will submit Design & technical specifications for ACCORD review & Approval. HSE team has completed a comprehensive inspection of all fire doors in accordance with NFPA-80. The inspection revealed that all fire doors are properly equipped with automatic door closers and are free from any obstructions or holding materials, ensuring full compliance with the standard. (Inspection Report is attached for your perusal - Annexure 'A") |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Lift shafts which are not protected by fire and smoke resistant construction in three (3) interior exit stairways connected to lift shafts via the lift machine rooms above Level 4 | Separation of lifts from escape stairs - Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Lifts have been physically segregated from the escape stairs, as evidenced by the civil structure layout & design documentation of the existing structure. Civil Structure Layout & design document is attached lift segregation is shown circled with red for your perusal (Annexure 3) |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Lift shafts which are not protected by fire and smoke resistant construction | Provide fire-rated separation between staircase enclosure and lift shaft in accordance with the Pakistan Accord Building Standard, implementing the previously approved design proposal | F6+4 months | Lift shaft machine rooms will be fitted with fire-resistant doors and equipped with automatic DCP Fire Extinguishers, as part of our fire safety upgrade program. Fire door and automatic DCP Fire Extinguishers technical details are attached for Accord review & Approval. (Annexure 1 & 1A.) |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit discharge | Final exit discharge at ground level not providing safe passage away from the building to a public way | Protect exit route at exterior of the building to allow a safe, free and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standards | 4 months | Emergency exit routes survey has been conducted to assess the ingress of utilities, services and ducts. (Annexure B) Figure-23 & 24 Machines are not installed in discharge pathways. Emergency exit routes are marked on the floor after emergency exit staircase with directional arrows. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit access | Exits discharge through interior building areas on the east side of the main production building which discharges internally into the finishing area on ground level | Provide a fire rated corridor to connect exit stairway discharge on the east side of the main production building directly to the outside | 4 months | In Coordination with Civil dept. a survey of the area was conducted, after structural assessment by a competent civil engineer it is found that discharge directly to the outside is not possible and that the exit stair is acting as a normal stair where evacuating workers have to move to the left for emergency exit door ultimately discharging them to the outside of the building. Additionally, we are engaging a third party civil consultant to obtain expert advice / solution which will be shared with Accord for review and approval. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | Exits discharge through interior building areas on the east side of the main production building | With sprinkler provided ensure all other conditions for internal stairway discharge outlined in the Pakistan Accord Building Standard are met | 4 months | We will discuss the same with civil consultant to obtain expert advice and will share the findings /solutions with Accord for review and approval. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Exits discharge through interior building areas on the east side of the main production building | Provide protected route or alternative exiting arrangements on east side of main production building to outside in accordance with the Pakistan Accord Building Standard | F10 + 4 months | Factory will implement measures to address the internal discharge route in accordance with proposal reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit signage | Exit signage insufficient for guiding occupants to exit locations throughout the facility , and some misleading exit signage | Remove any misleading exit signage and/or floor markings and provide exit signage so access to exits are marked by approved readily visible signs along full length of the escape route | 2 weeks | Emergency exit signages survey has been conducted by HSE across the TMU to identify any misleading signs installed. There were No misleading emergency exit signs found, however, Pakistan Accord team may have mixed there understanding with our internal production floor signs. For ACCORD ease we have plotted leading Emergency Exit signs on a layout drawing for clarity and understanding (Please refer to Annexure 'C'). The Technical details, Specs and pictorial label & references of Emergency Exit Signs installed across TMU are enclosed for your review & approval. (Please refer to Annexure 'D' in attachment) |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit signage | Exit signage insufficient or misleading | Provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | 2 months | Factory will implement any upgrading of the emergency Exit signage if needed, and based on review of proposals submitted earlier, to comply with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit access | Reduced exit capacity due to temporary obstruction with stored goods along means of egress | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 2 weeks | Emergency evacuation routes are blockage free & continual monitoring is being ensured by line management & HSE Dept. (Corrective actions file is attached for your perusal- Annexure 'E) |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit access | Reduced exit capacity due to temporary obstruction along means of egress | Remove obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit capacity | 2 weeks | Emergency evacuation routes are blockage free & continual monitoring is being ensured by line management & HSE Dept. (Corrective actions file is attached for your perusal- Annexure 'E) |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Travel distance | Travel distance in the main production building exceed 60m, and dead-end distance exceeds 15m | Provide alternative exiting arrangements in main production building to reduce the travel distances to be in accordance with the Pakistan Accord Building Standard | 4 months | Factory will propose a plan for addressing the excessive travel distance in the main production building by alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Travel distance | Travel distance in the main production building exceed 60m, and dead-end distance exceeds 15m | Provide alternative exiting arrangements in main production building to reduce the travel distances to be in accordance with the Pakistan Accord Building Standard | F16 + 4 months | Factory will implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Escape doors | Sliding exit doors on escape routes on Ground Floor of the Main Building on the bottom of an interior stairway | Replace sliding door(s) on escape routes with side hung swinging door(s) which swing in the direction of egress travel | 3 months | The following locations have been identified as having sliding doors that needs to be replaced with side-hung swinging doors: • T Block • Fabric Store HSE team in collaboration with Engineering & Civil Department conducted a joint survey and a modification design is agreed to be adopted for all sliding doors. proposed design of the door is attached for Accord review and approval. (Refer to Annexure - 2) For locking mechanism please refer to link given below: Door Locking Details: https://elocksecurity.com/product/double-cylinders-electromechanical-door-lock-es1073g-2 |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Escape doors | Sliding exit doors on escape routes on Ground Floor of the Main Building on the bottom of an interior stairway | Replace sliding door(s) on escape routes with side hung swinging door(s) which swing in the direction of egress travel | 3 months | Factory will implement the plan proposed earlier and reviewed by Pakistan Accord to remove sliding doors on escape routes |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Floor openings | Openings in floors with no fire rated separation - Bridges connecting the east and west sides of Level 1 - Chute connecting Levels 1 and 2. | Maintain fire rated floor separation by sealing penetrations and protecting openings with fire rated enclosures. | 2 months | All connecting bridges will be equipped with fire door at one side of the bridge, preventing the spread of fire from one side of the building to the other. Factory will prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings - Proposed fire separation details (including fire rating of walls and doors) Unprotected openings on the chute connecting levels 1 and 2 will be secured with fire shutters. Fire shutter specs. & design drawing will be shared shortly with ACCORD for review and approval. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Floor openings | Openings in floors with no fire rated separation - Bridges connecting the east and west sides of Level 1 - Chute connecting Levels 1 and 2. | Maintain fire rated floor separation by sealing penetrations and protecting openings with fire rated enclosures. | 4 months | Factory will provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Separation of shafts | Openings in floors with no fire rated separation - Lift machine room built as a mezzanine at Level 4 (north side) | Separate passenger and cargo lift shafts with fire rated opening protective assemblies, in accordance with Accord Pakistan Standard (BCP Table 8.6.3.1) | 4 months | Factory to prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Separation of shafts | Openings in floors with no fire rated separation - Lift machine room built as a mezzanine at Level 4 (north side) | Separate passenger and cargo lift shafts with fire rated opening protective assemblies, in accordance with Accord Pakistan Standard (BCP Table 8.6.3.1) | F22 + 4 months | Factory will provide 2-hour fire rated protection to lift shafts by implementing proposals and documents reviewed by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Storage | Ground level fabric store warehouse is not separated from the production areas and production areas is not separated from the Level 1 storage | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies, incl. Ground level fabric store warehouse, Level 1 storage areas. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated | 4 months | Factory will identify which storage areas can be re-arranged to meet the in-process storage limitations and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) Fire door technical details are attached for Accord review & Approval. (Annexure 1) |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Storage | Ground level fabric store warehouse is not separated from the production areas and production areas is not separated from the Level 1 storage | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies, incl. Ground level fabric store warehouse, Level 1 storage areas. | F24 + 4 months | Factory will implement the plan for separation of storage areas on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Rated Construction | Separation of high-risk areas | Electrical room not separated by fire and smoke resisting construction | Separate electrical room by 2-hr fire rated construction | 4 months | We have identified openings in the Electrical Room and will proceed to enclose them with fire-rated construction materials, ensuring enhanced fire safety. Additionally, the Electrical Room is already equipped with a UL-listed fire door providing 180 minutes of fire resistance. Drawings and submissions outlining the proposed changes will be submitted shortly for Accord review and approval. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Separation of high-risk areas | Electrical room not separated by fire and smoke resisting construction | Separate electrical room by 2-hr fire rated construction | F26 + 4 month | Factory will provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Hazardous Materials | Chemicals handling | Storage of flammable and combustible materials observed on Level 4 | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30 | 1 month | 1. MSDS of Mineral Oil, Machine Oil & Diesel are available. (Copies of MSDS are attached for ACCORD Perusal - Annexure 'L'). |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Hazardous Materials | Diesel storage | Storage of flammable and combustible liquids (diesel) observed in fire pump house | Interior diesel storage (maximum 1265 litres on ground level) is permitted if it is fire separated from other areas by 1-hr fire rated construction and stored in accordance with other requirements of NFPA 30. Diesel storage is permitted within generator rooms and fire pump rooms if adequately stored and that room is separated from adjacent occupancies | 2 months | A total of 120 liters of diesel fuel is stored within the Fire Pump room, which is fully segregated from adjacent occupancies. Additionally, a secondary containment system with a capacity of 120% of the rated capacity has been installed to ensure robust spill containment and prevention. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (1) Submit design documentation for a sprinkler system along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24 | 4 months | Factory will submit design documentation for a new sprinkler system along with required upgrading of the standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F30 + 1 month | If any material needed to be imported Factory will submit documentation to Pakistan Accord showing that an L/C has been opened for import of the components |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F31 + 4 months | Once all necessary material has been inhoused for the SUPS Factory will submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F32 + 3 months | Factory will provide Pakistan Accord with full 'as-built' documentation once installation complete |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F33 + 3 months | Factory will advise Pakistan Accord when SUPS installation fully completed and fully functional. |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F34 + 3 months | Factory will share full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Suppression | Fire pumps | Fire pump and pump control equipment comprising non-listed equipment | Provide listed/approved fire pump, driver and controller, transfer switch equipment and accessories as part of supporting infrastructure for the SUPS and Sprinkler system | 4 months | Factory will provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, demonstrating compliance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Suppression | Fire pumps | Fire pump and pump control equipment comprising non-listed equipment | Provide listed/approved fire pump, driver and controller, transfer switch equipment and accessories as part of supporting infrastructure for the SUPS and Sprinkler system | 18 months | Factory will provide or upgrade electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers as necessary, to comply with NFPA 20 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Suppression | Standpipe system | Insufficient number of standpipe hose connections provided in the current system. | Provide a Class I standpipe system as per NFPA 14 as part of supporting infrastructure for the SUPS and Sprinkler system | 18 months | There are total 14-Hydrants & 24-Hose Reels are installed across the TMU. Aforesaid, system falls under class III Standpipe which does accommodate both 40mm and 65mm dia. hose connections. Factory will provide the design for a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system, and submit to Accord for review Hydrants/ Standpipe System design & layout are attached for ACCORD review and approval. (Annexure 'M'). |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Suppression | Standpipe system | Insufficient number of standpipe hose connections provided in the current system. | Provide a Class I standpipe system as per NFPA 14 as part of supporting infrastructure for the SUPS and Sprinkler system | 18 months | Factory will provide a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2023-10-24
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Lucky Textile Mills Limited Unit L-12, Plot No. L-3, Block-21, Federal-B Area, Karachi City, Sindh, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 24-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | This relates to the Main production building on level(s) L00 - Ground Floor. Potentially overstressed columns on ground floor under overhead water tank. | Building Structural Engineer to review design, loads and columns stresses in area identified in the report. Verify insitu concrete stresses either by 100mm dia. cores or existing cylinder strength data for the identified columns or 100mm dia. cores from 4 columns. Submit concrete strength data to Pakistan Accord for review and and propose remedial works if required. | 3 months | Our Civil Consultant will recheck the design of marked Columns (04 Nos.) and will also share the cube test reports during construction phase of the same. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | This relates to the Main production building on level(s) L00 - Ground Floor. Potentially overstressed columns on ground floor under overhead water tank. | Complete the remedial works as required. | 6 months | After Design check, Design conformance will decide the remedial action, if needed will submit remedial actions, if required. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Beams | This relates to the Main production building on level(s) L04 - Fourth Floor. Beam cracking is visible in a number of locations at underside of 4th floor level and appears to be related to insufficient top steel in the beam. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, in such cases, Building Engineer to investigate cause of cracking and identify appropriate remediation. Investigation shall include confirmation of reinforcement in the beams and design assessment based on the as-constructed building and loading. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | The Beam design is OK, and our Civil Consultant identified that the cracks are shrinkage cracks. However, we will recheck as per the defined methodology and submit confirmation in this regard with the approval of Civil Consultant. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Beams | This relates to the Main production building on level(s) L04 - Fourth Floor. Beam cracking is visible in a number of locations at underside of 4th floor level and appears to be related to insufficient top steel in the beam. | Carry out remediation works as required. | S3+4 months | After Design check, Design conformance will decide the remedial action, if needed will submit remedial actions, if required. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Cracking | Slabs | This relates to the Main production building on level(s) L04 - Fourth Floor. Slab cracking is visible locally at 4th floor level; appears to be flexural and may be associated with coring for electrical services. | Structural Engineer to investigate cause of cracking and identify appropriate remediation. Submit the proposed remedial works to the Pakistan Accord for review. | 2 months | The Slab design is OK, and our Civil Consultant identified that the cracks are shrinkage cracks. However, our Civil Consultant will recheck through site visit and submit confirmation in this regard. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Cracking | Slabs | This relates to the Main production building on level(s) L04 - Fourth Floor. Slab cracking is visible locally at 4th floor level; appears to be flexural and may be associated with coring for electrical services. | Carry out remediation works as required. | S5 + 4 months | After Design check, Design conformance / site visit will decide the remedial action, if needed will submit remedial actions, if required. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural Design | Lack of safe load plans | This relates to the Main production building. No safe load plans posted in the factory | Building Engineer to produce safe loading plans for all floors within the factory giving consideration to floor capacity and column capacity. Safe loading plans to be posted in the factory. | 6 months | We will collect data along with Production team and will prepare Safe Load Plans as per current situation and we will suggest / manage Load pattern as per design limitation with the support of Compliance Team and paste in the floors for implementation. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Other Damage/Defects | Moisture ingress | This relates to the Main production building on level(s) L01 - First Floor. Water damage to structure under washroom area. | Structural Engineer to propose repair to the RC frame in this area and remediate cause of water damage. Submit the proposed remedial works to the Pakistan Accord for review. | 6 months | The moisture stains and paint deterioration were due to leakage / seepage from toilets of above floor and the same earlier repared. However, check and fix / repair the same within specified time. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5
3 | 8 |  | 119 | 421 | 6 | 5
3 | 8 |  | 120 | 421 | 6 | 5
3 | 8 |  | 121 | 421 | 6 | 5
3 | 8 |  | 122 | 421 | 6 | 5
3 | 8 |  | 123 | 421 | 6 | 5
3 | 8 |  | 124 | 421 | 6 | 5
3 | 8 |  | 125 | 421 | 6 | 5
3 | 8 |  | 126 | 421 | 6 | 5
3 | 8 |  | 127 | 421 | 6 | 5
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
anotehr electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1