## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
18-Dec-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Lucky Textile Mills Ltd. No.2, L-3, Block 2, F.B. Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 05-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | This relates to the whole facility: Single Line Diagrams were provided, but were not updated and designed appropriately | Consult a qualified engineer to review and update the entire Single Line Diagrams and rectify design issues. | 3 months | SLD's were already developed for the whole facility, we update the SLD's after modifications due to certain load requirements as needed for new installations and considering the same, we timely update the SLD's of Panels and DB's. Factory will ensure that in-situ electrical layout is matched with SLD |  |  | SLDS are in progress,SLDs should be submitted to Pakistan Accord once completed | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | This relates to the whole facility: As-built Layout drawings were not provided. | Consult a Qualified Engineer complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. | 6 months | Factory will consult a competent engineer to provide an electrical layout drawing,and submit to Accord for review work in progress |  |  | Pending submission | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Hot Spots | Thermographic & Insulation Test Reports were not provided. | Thermographic & Insulation Testing report shall be prepared. | 6 months | We conduct thermography on a quarterly basis according to the schedule. IR report is attached for Accord review and further advise. |  |  | Pending submission | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | Lightning protection system is not installed in the facility. Any document related to LPS assessment was not presented. | Risk assessment for Lightning Protection System should be carried out by qualified engineer. Design LPS system accordingly if required and submit to Pakistan Accord for review. | 2 month | Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review Work in progress |  |  | Pending submission | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | Lightning protection system is not installed in the facility. Any document related to LPS assessment was not presented. | Install Lightning Protection System if required according to Pakistan Accord reviewed documentation.. | 6 months | Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system Work in progress |  |  | Pending submission | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Openings | Unsealed openings within panels having Sharp Edges which can damage insulation of the cables. Unsealed opening could provide a passage for dust, lint and dirt. However, it also provides passage for rodents to enter which could lead to a potential hazard for short circuit. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust, lint and dirt. | 3 months | 70% of of opening are sealed and rest work in progress. |  |  | Work completed partially. | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Panel/cabling/busbar | Unsealed openings within panels having Sharp Edges which can damage insulation of the cables. | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are regularly cleaned, inspected, and free from dust, lint and dirt. | 2 months | We perform cleaning of DB's/ Panels on monthly basis. Rest for the cable trays, we perform cleaning on quarterly basis as per the schedule. |  |  | Work completed partially.,inprogress | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | Abnormal temperatures were recorded in the following locations (non-exhaustive): 1- Main Building on level L01 - 1st Floor on yellow phase termination point of Main Circuit Breaker at SDB 01. 2- Main Building on level L01 - 1st Floor on yellow phase SP breakers in SDB-01. 3- Main Building on level L01 - 1st Floor on SP Circuit Breaker in the DB. 4- Main Building on level L00 - Ground Floor on yellow phase termination point of Main circuit breaker of Holding Machine 11 DB. 5- Main Building on level L01 - 1st Floor in yellow cable from yellow phase outgoing cable SDB-05. 6- Main Building on level L02 - 2nd Floor on termination point on main circuit breaker of SMDB-02. 7- Main Building on level L02 - 2nd Floor on outgoing cable from yellow phase SP breakers which seems overloaded. | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 1 month | Work is in progress as it is a continuous improvement process. We are rectifying the causes of hot spots as soon as possible. |  |  | Initial observation on hotspot have been rectified however thermographic inspection report is required to validate the results. | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Hot Spots | Abnormal temperatures and hot spots identified in the electrical panels and wiring in numerous locations throughout the premises | Carry out independent thermographic survey | 1 month | We conduct thermography on a quarterly basis according to the schedule. |  |  | Thermographic report to be submitted by factory | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Hot Spots | Abnormal temperatures and hot spots identified in the electrical panels and wiring in numerous locations throughout the premises | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 6 months | E9 + 6 months | We conduct thermography on a quarterly basis according to the schedule. Factory will share thermographic schedule and a thermographic report with Accord at least every 6 months |  |  | Thermographic report to be submitted by factory | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Circuit breakers | Undersize cables were found with larger size circuit breakers which is not going to protect the cable. This was a recurring issue in most of the DBs in the Main Building on level(s) L02 - 2nd Floor, including the following (non-exclusive): - SDB 04 Stiching 2nd Floor: Main CB incoming 25mm and outgoing 16mm. - SDB 12 2nd Floor: Same issue found in this DB as well. - Undersize cable (0.75 Sqmm) with 32A SP which cannot provide protection to this cable. | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes | 1 month | Factory will consult a qualified engineer to review the installation and advise on the correct combination of cables and breakers throughout Work is in progress as it is a continuous improvement process. We are rectifying the same as per the compatibility of breakers and cables in the distribution boards and panels. |  |  | Not rectified for all location,work in progress | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Circuit breakers | Undersize cables were found with larger size circuit breakers which is not going to protect the cable. | Replace breakers or cable with correct cable or breaker sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | E11 + 3 months | Factory will replace breakers or cables with components needed to match cables and breaker sizes and ensure that breaker size is less than current carrying capacity |  |  | Not rectified for all location,work in progress | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Cabling & Wiring | Splicing of cables | Inappropriate cable joints found in different DBs in the Main Building on level(s) L01 - 1st Floor. Some of DBs having chattering sound which could be a loose connection, including (non-exclusive): - SDB 06 & SDB 09 - MDB 2 2nd Floor | Check loose connection and rectify as needed | 1 month | work is in progress |  |  | Partially completed.Pending rectification . | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Cabling & Wiring | Splicing of cables | Inappropriate cable joints found in different DBs in the Main Building on level(s) L01 - 1st Floor | PVC Joints must be replaced by copper ferrule or any other appropriate method with proper insulation material. | E13 + 4 months | Factory will ensure joints are replaced as necessary with method using proper insulation material. work is in progress |  |  | Pending Rectification | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | Dedicated neutral cables are missing in DBs in the Main Building on level L00 - Ground Floor, with respect to outgoing circuits, which leads to overload on neutral cables. | In future works, dedicated neutral circuit for each outgoing circuit shall be installed. | 2 months | work is in progress |  |  | Rectified. | Corrected
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | Dedicated neutral cables are missing in DBs in the Main Building on level L00 - Ground Floor | All circuits to have a dedicated neutral on each outgoing circuit. | E15 + 2 months | work is in progress |  |  | Rectified. | Corrected
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Cabling & Wiring | Splicing of cables | Cables termination installed without cable lugs in the Main Building on level L02 - 2nd Floor, which results in strands of the cables breaking and overheating. | All stranded cables terminations shall be provided with proper cable lugs. | 1 month | work is in progress |  |  | Rectified. | Corrected
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Earthing system | In most of the areas, earth bonding of cable tray, metal structures, metal tables etc, found missing. | Connect all metal bodies of electrical panels to the earth terminal within electrical panels. | 6 months | work is in progress |  |  | Work in progress | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Earthing system | In most of the areas, earth bonding of cable tray, metal structures, metal tables etc, found missing. | All other metal structures that (likely to be energized) near electrical installation shall be bound with earth to avoid any hazard. | 6 months | work is in progress |  |  | Work in progress | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Lint & dust inside panel board | DBs and cable trays found with accumulated lint, dust and dirt, particularly: - MDB CBs on level 01- 1st Floor - Main Building on level L02 - 2nd Floor | All DBs must be cleaned and maintained. | 1 month | We perform cleaning of DB's/ Panels on monthly basis. Rest for the cable trays, we perform cleaning on quarterly basis as per the schedule. |  |  | Corrected | Corrected
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Lint & dust inside panel board | DBs and cable trays found with accumulated lint, dust and dirt | Develop a periodic maintenance record of DBs and cable trays. | 1 month | Factory will develop a periodic maintenance schedule and share with Accord for review. We perform cleaning of DB's/ Panels on monthly basis. Rest for the cable trays, we perform cleaning on quarterly basis as per the schedule. |  |  | Corrected | Corrected
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Lint & dust inside panel board | DBs and cable trays found with accumulated lint, dust and dirt | Periodic maintenance shall be done. Ensure that electrical panels are cleaned, inspected and free from Lint, dust and dirt. | 1 month | We perform cleaning of DB's/ Panels on monthly basis. Rest for the cable trays, we perform cleaning on quarterly basis as per the schedule. |  |  | Corrected | Corrected
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Cabling & Wiring | Splicing of cables | In some Distribution Boards, idle or dismantled cables were found, which could pose a potential hazard and ignite a fire. | All cables which are not in use, shall be discarded and dismantled to avoid any hazard. | 3 months | work is in progress |  |  | Corrected | Corrected
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | DBs & Elec Protection Systems | Multiple Connections | In some DBs, multi looping was found on circuit breakers in the Main Building on level L01 - 1st Floor, particularly in the DB Adjacent to Masjid. | Modify the installation so that circuits do not share breakers Avoid looping and bunch of cable at MCCB/MCB or bus bar terminal, use individual circuit and overcurrent device for every incoming and outgoing circuit at the distribution boards. | 3 months | work is in progress |  |  | Pending Rectification | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Emergency Lighting | Provided but insufficient | Emergency lighting throughout all buildings: Emergency lighting provided but did not function in tests | Regularly test the emergency lighting system on each floor. | 3 months | LTML H.S.E team jointly conduct inspection of emergency lights with Engineering team and update the documentation for records. |  |  | Installed emergency lights does not provide adequate backup ,failed to comply with the requirement .further Lighting layout to be submitted by the factory to assess the number of lights on all required location. | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Emergency Lighting | Provided but insufficient | Emergency lighting throughout all buildings: Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs | Provide additional emergency fixtures to supply adequate illumination along the means of egress. | 3 months | We install emergency lights as per the requirements intimated by LTML HSE/Compliance teams. We shall survey with our HSE/Compliance teams to address the same |  |  | Lighting layout to be submitted by the factory to assess the number of lights on all required location. | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Emergency Lighting | Provided but insufficient | Emergency lighting throughout all buildings: No emergency lighting in some rooms / areas | Provide emergency lighting in accordance with Pakistan Building Code and NFPA 101. | E26 + 3 months | Factory will provide emergency lighting system in accordance with Pakistan Building Code and NFPA 101. We install emergency lights as per the requirements intimated by LTML HSE/Compliance teams. |  |  | Lighting layout to be submitted by the factory to assess the number of lights on all required location. | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Fire detection and alarm system is not consistent with acceptable standards. Some of the related issues include (non-exclusive): - Incomplete coverage of fire detection and alarm devices in some areas - Detection devices installed but not functional - Detection devices installed but obstructed - Incomplete coverage of fire alarm devices - Sounders inaudible due to low volume or high ambient noise in metal free packing areas, production areas, maintenance office, laser cutting room - IManual fire alarm box(es) not located near exit doorways | Submit design documentation for upgrading of current system to Pakistan Accord for review. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) and submit to Pakistan Accord for review before purchasing any new equipment |  |  | Pending submission from the factory | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E28 + 1 month | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  | Pending | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E30 + 4 months | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  | Pending | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E30 + 5 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  | Pending | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E31 + 3 months |  |  |  | Pending | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E32 + 3 months |  |  |  | Pending | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 144 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 145 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 146 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 147 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 148 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 149 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 151 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 152 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
18-Dec-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Lucky Textile Mills Ltd. No.2, L-3, Block 2, F.B. Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 05-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed throughout the areas inspected, including (non-exhaustive): - Level 2 - (west central) stair access door; fusing area; special machine room; machine holding area; women’s rest area, metal free packing area) - Level 1 - fusing area and women’s rest area; - Ground Level - mechanic holding area, special machine room area, fusing department, canteen, kitchen | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard | 1 month | All non-compliant locking mechanisms will be removed from egress path doors upon approval of new locking devices, and replaced with compliant ones on a sequential basis, ensuring uninterrupted safety and accessibility. Locking Mechanism specifications link is provided below for ACCORD review & approval: Door Locking Details: https://elocksecurity.com/product/double-cylinders-electromechanical-door-lock-es1073g-2 |  |  | 18-12-24: Non compliant locking mechanisms are not removed yet." | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | For single Leaf doors panic bar or similar arrangements will ensure inside and cam locks arrangement from outside which gets override upon trigger of panic bar from inside. For double leaf doors same locking arrangement will ensure as in single leaf doors through wicket door provisions. Locking Mechanism specifications link is provided below for ACCORD review & approval: Door Locking Details: https://elocksecurity.com/product/double-cylinders-electromechanical-door-lock-es1073g-2 |  |  | 18-12-24: Provided Details of Locking device can be used for offices and other areas where the number of occupants are less than 50, as the provided locking mechanism allows for easy bypass from the inside. For areas with occupants more than 50 factory has to arrange a locking mechanism with a panic/push bar, that can be easily operated from inside even if its locked from the outside. | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Number of exits | Single means of egress is provided, but more than one means of escape is required. This was observed in: - Ground Level canteen and kitchen (also lockable) and metal free packing area - Roof (normally unoccupied) | Propose modifications to means of escape to meet requirements and present to Pakistan Accord for review. | 4 months | Factory will prepare drawings showing proposal for providing the required number of exits from the area and submit to Accord for review prior to the rectification works Both the locations i.e.Ground Level canteen and kitchen and metal free packing area are being removed from the present locations and re-located with plenty of means of escape. |  |  | 18-12-24: Factory will submit the plan to the Pakistan Accord for review. | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Number of exits | Single means of egress is provided, but more than one means of escape is required. | Provide alternative means of egress from the areas identified to ensure there are sufficient number of exits and sufficient exits to accommodate the occupant load and travel distance requirements, in accordance with the Pakistan Accord Building Standard | F3+ 4 months | Adequate exits will be provided from the area, according to proposal previously reviewed by Accord Highlighted Areas (Canteen and Metal free Zone) are being removed from the present locations and relocated with plenty of means of escape. |  |  | 18-12-24: Factory will implement after plan review by Accord. | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected building: - Combustible materials stored in stairway - Automatic door closers are not installed/functioning in several locations - Doors normally required to be kept closed are secured in the open position by being tied open or by obstructions being wedged between the door and door frame. | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as needed. | 2 months | Combustible material stored in stairways have been removed. HSE team has completed a comprehensive inspection of all fire doors in accordance with NFPA-80, report generated & forwarded to Engineering Dept. for necessary repair & Maintenance for automatic door closures. The inspection revealed that all fire doors are properly equipped with automatic door closers and are free from any obstructions or holding materials, ensuring full compliance with the standard. |  |  | 18-12-24: Stored Material Removed from stairways Doors Closer installed however some doors are not easy to open (jammed). No obstruction was observed at the stairs. 24-04-25 Factory provided visuals and is to be verified on site at FUI. | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. | Remove equipment and services not serving stairway from stairway, or provide construction to separate equipment and service by construction having a fire resistance rating not less than that required for the exit enclosure. | 4 months | A Survey with CIVIL team has been conducted, few of the equipments and services will be removed from stairway and relocated and some masonry block construction work will be carried out for the equipments & services which could not be relocated to make enclosure around exit route. |  |  | 18-12-24: Drawings of the proposed solution concluded by Civil Team will be submitted to Accord for review. Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. | Provide a fire rated separation between the stair and the conduit, duct, etc., or relocate services so that they no longer penetrate the exit enclosure. Close any gaps with listed products with the appropriate fire rating. Provide all fire doors with self-closing and self-latching devices, and push-bar panic hardware where required in accordance with Pakistan Accord Building Standard. If fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system. | F6 + 4 months | All the louvre CC mesh and aluminium ventilators openings will be removed and are closed with 6" inch thick block masonary work with plaster on both side. All the fire doors installed across the unit are provided with self closing, self latching devices and push bar panic hardware. |  |  | 18-12-24: The Factory will submit Details to Accord for review. Some doors have been replaced/added however Stairs doors are still not fire doors e.g. North Stair, South Stair. | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected building: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors - Exit stairway exposed to unprotected openings – e.g., southwest exterior exit stairway - Penetrations into/through exit stair protective enclosure | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory will prepare drawings showing proposed fire separating construction and door assemblies to protect stairs and submit to Accord for review prior to the rectification works All the louvre CC mesh and aluminium ventilators openings will be removed and are closed with 6" inch thick block masonary work with plaster on both side. |  |  | 18-12-24: Factory will submit the design to Pakistan Accord for review. | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. | Provide fire rated protective enclosure to the staircase in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F8 + 4 months | Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  | 18-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit capacity | Obstructions along means of egress reducing exit capacity. | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 2 weeks | All the obstruction in escape paths have been removed and path is being continuously maintained free of all obstructions or impediments. Daily inspection of the escape path is being carried out to keep the path free of obstruction & impediments. (Refer to Annexure - "F") |  |  | 18-12-24: Obstructions were removed, however, some obstruction still found at Ground Floor exit. continuously maintain them free of all obstructions or impediments. 24-04-25 Factory provided visuals and is to be verified on site at FUI. | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Travel distance | Travel distances exceed limits in several areas including - travel distance from NE corner Level 2 production area is over 80 meters (due to NE exterior stair closed with ongoing construction - travel distance from SEcorner Level 1 cutting department is over 70 meters (60m limit). - common path of travel from machine holding area on Level 2 is approx 34 meters (23m limit for less than 50 occupants) - common path of travel from NE corner Level 2 production area is approximately 36 meters (NE exterior stair closed with ongoing construction - common path of travel from Finishing Department on Ground Level in excess of 36m (15m limit for 50 occupants or more) - Dead end travel distance exceeds 15m – exterior dead end caused by construction works was observed to be in excess of 90m | Propose alternative exiting arrangements to reduce the travel distances that comply with the Pakistan Accord Building Standard and submit to Pakistan Accord for review. | 4 months | A Joint survey of HSE & Civil team is conducted in LTM - 2 unit to check feasibility of constructing additional means of escape i.e. Exit doors to reduce travel distance at recorded floors. There are 07 Nos. of exit doors provided presently at ground floor, One additional Exit door will be constructed at ground floor as circled in RED in layout plan. At 1st floor there are 03 Nos. of existing Fire exit doors, two more are added to reduce travel distance and are shown in circled RED in Layout plan. At 2nd floor, there are 03 Nos. of existing Fire exit doors, two more are added to reduce travel distance and are shown in circled RED in Layout plan. (Layout Plan showing additional means of escape are attached for Accord review & Approval. (Annexure - B) |  |  | 18-12-24: Ground Floor proposed Plan is approved for execution 1st and 2nd Floor proposed Plan is approved for execution Ensure that there is unobstructed exit access to all emergency stairs | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Travel distance | Travel distances exceed limits in several areas as outlined above | Provide alternative exiting arrangements to reduce the travel distances as per reviewed proposals and in accordance with the Pakistan Accord Building Standard. | F11 + 4 months | Factory will limit travel distances to floor and building exits to within acceptable distances, in accordance with the proposals previously reviewed by Accord. There are 07 Nos. of exit doors provided presently at ground floor, One additional Exit door will be constructed at ground floor as circled in RED in layout plan. At 1st floor there are 03 Nos. of existing Fire exit doors, two more are added to reduce travel distance and are shown in circled RED in Layout plan. At 2nd floor, there are 03 Nos. of existing Fire exit doors, two more are added to reduce travel distance and are shown in circled RED in Layout plan. (Layout Plan showing additional means of escape are attached for Accord review & Approval. (Annexure - B) |  |  | 18-12-24: Factory will implement as per the plan reviewed by Accord. | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior and exterior stairways to public way are exposed to unprotected openings. | Remove combustible exterior storage within 3.05m horizontally and vertically of unprotected openings. | 4 months | Factory will remove combustible exterior storage within 3.05m horizontally and vertically of unprotected openings |  |  | 18-12-24: Combustible storage still exists there. | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior and exterior stairways to public way were observed to be exposed to unprotected openings | Protect exit route at exterior of the building from unprotected openings to allow a safe, free, and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standard. | 4 months | Refer to ACCORD Report Fig. 16, 17, 23, 25 & 26, all the obstructions have been cleared from the exit discharge route and combustible exterior storage removed. (Refer to Annexure - "C") Drinking water cooler vicinity opening shown in Fig. 30 will be closed with block masonry and pipe will be relocated above and near to ceiling. A survey along with Engineering , Civil and a private vendor (M/S Reliant) were conducted, Vendor has submitted a specially designed sand trap / separator grill which is used to block such openings shown in Fig. 18, 19, 20, 21, 22 & 24 and provide separation against fire as well as keep ventilation intake. Grill is made of 14 swg. fire resistance material sheet. (Grill Design is appended as Annexure - "G" for ACCORD Approval & review) Cargo lifts doors shown in Fig 31 & 32 are not creating any obstruction on egress pathways. However, lift shaft will be protected by providing Fire curtains or enclosure. (Fire Curtain design is enclosed as Annexure - "D" for ACCORD review & Approval) Opening shown in Fig. 33 will be closed by installing Fire rated door at LTV Electrical room. (Fire Door shop drawing is appended as Annexure - "H" for ACCORD Review & Approval) Opening of Transformer room shown in Fig. 34 will be addressed by installing 8x6 feet specially designed sand trap / separator gril which act to provide ventilation for dissipating transformer heat as well as Fire separation / protection to the exit route. Grill Design is appended as Annexure - "G" for ACCORD Approval & review). Factory will prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. |  |  | 18-12-24: Obstructions Removed ensure remain clear. Annexure C still shows opening at discharge Route also observed during inspection. Factory will re submit the plan to rectify the issue with full Documentation proof and Certifications for Annexure G, D and H. Factory will implement as per the plan reviewed by Accord. | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Escape doors | Doors on escape routes that swing against direction of travel: Doors on all escape routes, including those leading to outside or away from the building, must swing in the direction of travel to an emergency exit, however, there are several doors along escape routes swinging in the wrong direction (inwards) at the following (non-exclusive) locations: - Level 2 door to north stair. - South (central) stair - Door to south exit (via stair core) | Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard | 1 month | Factory will amend doors to ensure that are side swinging and open in the direction of travel to an exit A survey along with Civil & Engineering team is completed and assessment done at the ground. All the doors shown in Fig. 35, 36, 37 & 39 will be dismantled by in house engineering team and re-designed mechanically to make and install them to swing in the direction of egress travel. |  |  | 18-12-24: Not all opposite swinging doors have been replaced yet. | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit signage | It was observed that there is insufficient exit signage. Exit signs are generally present directly at the location of exits but are not provided throughout the building to lead occupants to the exit locations. | Provide exit signage so access to exits are marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | 4 months | Factory will provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standards And BCP 10.15.1, 10.15.2 and 10.15.3 Emergency exit signage survey has been conducted by HSE across the LTM-2 to quantify the existing signage and assess the requirement of additional ones. Sufficient exit signages are present and installed throughout the building at the location of all exits to access the exit. However, technical details, Specs and pictorial label & references of Emergency Exit Signs installed across LTM-2 are enclosed for your review & approval, if ACCORD is still of the opinion that they are of non-approved status, ACCORD Guidance is solicited. (Annexure - "I" for Emergency Exit signage is appended for ACCORD review and approval) |  |  | 18-12-24: Factory will implement after review by Accord | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Escape doors | Sliding exit doors observed on escape routes where only swinging doors provide an acceptable level of risk. Sliding door(s) on escape routes from administrative/ office areas are acceptable for rooms with a population that does not exceed 10 persons. | Replace sliding door(s) with side hung swinging door(s) which swing in the direction of egress travel in accordance with Pakistan Accord Building Standard | 1 month | In house Civil & Engineering Team are engaged to change the sliding door with those of Swinging Doors. Drawing, design and proposal is developed and shared with Accord for their review & approval. (Annexure - "J" is appended for ACCORD review and approval) |  |  | 18-12-24: Annexure J : Required more Documentation and doors certification if located at escape routes as per observation doors location on drawing for approval. Factory will implement as per the plan reviewed by Accord. | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm observed at - north stair on the roof level (door to the stair is 1830mm and stair is 1930mm) - at the Office Mezzanine above Level 1 (1830mm headroom). | Fix headroom height safety signage and safety padding around underside of lintel where door height is less than 2.05 m on the escape route. | 1 month | Safety Sign & soft padding will be install at highlighted locations and evidence will be shared with ACCORD shortly. |  |  | 18-12-24: Only padding at Roof stair was installed. Provide signages as per Pakistan ACCORD Building Standard. | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm observed at - north stair on the roof level (door to the stair is 1830mm and stair is 1930mm) - at the Office Mezzanine above Level 1 (1830mm headroom). | Propose design modifications to ensure safe passage on all escape route or propose alternative paths that comply with Pakistan Accord Standard and submit to Pakistan Accord for review. | 4 months | In house Civil team has surveyd the location and agreed to increse the Door & roof height shown in Fig. 40 & 42. Modification will be carried out accordingly. Design & Proposal will be submited shortly to Accord for review & approval. Wooden structure shown in Fig. 41 will be removed below staircase and evidences will be submit to Accord for their review & further advice. |  |  | 18-12-24: Factory will submit the design modifications to Accord for review. | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm observed at - north stair on the roof level (door to the stair is 1830mm and stair is 1930mm) - at the Office Mezzanine above Level 1 (1830mm headroom). | Apply design modifications as per proposal reviewed by Pakistan Accord to provide safe heights along all emergency exit routes. | F19 + 4 months | In house Civil team has surveyd the location and agreed to increse the door & roof height shown in Fig. 41. Modification will be carried out accordingly. Design & Proposal will be submited shortly to Accord for review & approval. |  |  | 18-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Suppression | Standpipe system | Hydrant / standpipe system for firefighting operations. The building does not have a Class I standpipe system but requires one because the building is not sprinklered, is more than 2 storeys, and has a floor area greater than 2,325 m2. There is an insufficient number of risers and standpipe hose connections – refer to NFPA 14 for placement requirements (e.g., hose connections required at the main floor landing in exit stairways) | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24 | 4 months | Factory will appoint consultant and submit design documentation for suppression system (SUPS), including standpipe system and supporting infrastructure, to Pakistan Accord for review before purchasing any new equipment There are total 20-Hydrants & 19-Hose Reels are installed across the LTM - 2. Aforesaid, system falls under class III Standpipe which does accommodate both 40mm and 65mm dia. hose connections. Hydrants/ Standpipe System design documents for new equipments & layout are attached for ACCORD review and approval. (Refer to Annexure - "K" for new equipment & Annexure"N" for existing arrangements are appended for ACCORD Review & Approval) |  |  | 18-12-24: Design & technical details are missing. Factory will submit design to Accord for review. Factory at design and development stage (step 1) | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Standpipe system | Hydrant / standpipe system for firefighting operations. The building does not have a Class I standpipe system but requires one | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F21 + 1 month | L/C has been opened for import of New Fire Pump & Accessories required for the SUPS design submitted above. (Annexure - "L" is appended for ACCORD Review & perusal) |  |  | 18-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Standpipe system | Hydrant / standpipe system for firefighting operations. The building does not have a Class I standpipe system but requires one | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F22 + 4 months | All the materials, both imported and locally have been procured, Purchase orders issued to the vendors and material is gradually being transported at site for installation of the SUPS. (Annexure - "M" is appended for ACCORD Review & perusal) |  |  | 18-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Standpipe system | Hydrant / standpipe system for firefighting operations. The building does not have a Class I standpipe system but requires one | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F23 + 3 months | We have noted at our end, After completion of Installation, testing & Commissioning "As - Built" documentation of the system will be submitted to ACCORD. |  |  | 18-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Standpipe system | Hydrant / standpipe system for firefighting operations. The building does not have a Class I standpipe system but requires one | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F24 + 3 months | We will coordinate with ACCORD Pakistan once the installation is complete to conduct verification inspection to ensure the installation fully complies with the reviewed drawings. |  |  | 18-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Standpipe system | Hydrant / standpipe system for firefighting operations. The building does not have a Class I standpipe system but requires one | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F25 + 3 = 18 months | We will Provide testing and commissioning (T&C) certification from the SUPS system supplier onece the installation is complete. We will arrange for provision for attendance of the system installer, factory technical personnel and invite Pakistan Accord technical team to witness a final T&C demonstration verification on site. |  |  | 18-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Fire pumps | Fire pumps and water supply which currently support the hydrant / standpipe system. - This facility is supplied by a private service main with fire pumps and a water supply remote from the site (~1km away in the basement of the Lucky Mall) which also supplies other facilities, including the shopping mall and a 25-story residential building. - Fire pump arrangement is not providing a reliable means to maintain pressure at the inspected building, i.e., 1. A single hose flowing at the building inspected did not draw significant flow and pressure relative to the size and remote nature of the private service main system 2. The electric fire pump was set to turn on when the pressure drops below 7 bar – within seconds of turning on, the electric fire pump would automatically turn itself off because the pressure it produced would cause an over pressurization of the system (pump controller would turn off pump at 13.3 bar to avoid the system exceeding 14 bar which is the maximum rated pressure of the fire pump). This led to cycling of the fire pump turning on and then abruptly shutting itself down, which is not good for the pumping system and introduces reliability issues to the overall system. 3. The diesel fire pump was set to turn on when the pressure drops below 5 bar – though this was out of service and did not turn on when tested | Identify reason for error signals and take an appropriate action to rectify the error so the system is fully functional as part of supporting infrastructure for the SUPS and Sprinkler system. | 4 months | Provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Accord for review New SUPS is being installed dedicatedly to cater the need of LTM - 2, the old one installed in the Lucky One Mall will handed over to the LOM Management. Installing, Testing & Commissioning of New Fire Hydrant system is planned as stated above. Error signal on the pump panel has been rectified, its pressure relief valve changed, now the pump is in running condition. weekly testing and inspections of the pumps are being carried out by the our Engineering dept. |  |  | 18-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Fire pumps | Fire pumps and water supply which currently support the hydrant / standpipe system from a supply on a remote site did not provide adequate flow in the fire suppression system at the facility- | If system cannot be made to function in accordance with the requirements of the Pakistan Accord Building Standard, then submit proposed design modifications to the Pakistan Accord for review, install and commission as part of supporting infrastructure for the SUPS system. | 18 months | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system. New Fire Hydrant System is being installed, proposed design & necessary documents are being submitted to ACCORD Pakistan. (Annexure - "K" is appended for ACCORD Review & Approval) |  |  | 18-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Separation of shafts | Openings in floors created by lift shaft openings where fire rated separations are required. Lift shafts connecting floors not separated by fire and smoke resisting construction and opening protection. | Propose how cargo lift openings will be provided with fire rated floor separation by sealing penetrations or protection of the openings and submit to Pakistan Accord for review | 4 months | Factory will prepare drawings showing proposed fire separating construction to shafts, with details of door assembly, location in relation to escape routes and lift door operation, and submit to Accord for review prior to any rectification works Lift shaft machine rooms will be fitted with fire-resistant doors and equipped with automatic DCP Fire Extinguishers, as part of our fire safety upgrade program. (Fire door and automatic DCP Fire Extinguishers technical details are attached for Accord review & Approval. (Annexure "H" & "1H".) |  |  | 18-12-24: Required Documentation and Certification for all accessories approval. Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Separation of shafts | Openings in floors created by lift shaft openings where fire rated separations are required. Lift shafts connecting floors not separated by fire and smoke resisting construction and opening protection. | Provide fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure in accordance with documentation reviewed previously by Pakistan Accord | F29 + 4 months | Fire rated separation of lift will be completed, including brickwork/ fire rated assemblies and adequate and door operating mechanism, according to proposal previously reviewed by Accord Lift shaft machine rooms will be fitted with fire-resistant doors and equipped with automatic DCP Fire Extinguishers, as part of our fire safety upgrade program. (Fire door and automatic DCP Fire Extinguishers technical details are attached for Accord review & Approval. (Annexure "H" & "1H".) |  |  | 18-12-24: Required full Documentation and Certification for all items for approval. Factory will implement after plan review by Accord Lift Machine Room does not required fire door at roof top. | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Storage | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Where storage does not meet the Pakistan Accord Building Standard requirements for “in-process storage” in production occupancies, then it needs to be separated with fire resisting construction. Storage areas observed to be not separated by fire and smoke resisting construction as follows (non-exhaustive): - Level 2 storage which is not arranged in accordance with limits for in-process storage, open to production floor - Fabric Store not separated from Cutting area | Manage storage in non-storage occupancies so that each pile is less than 2.45 m (8ft) in height and less than 23m2 (250ft2) in any one area, and each pile is separated by a minimum of 3.0 m (10 ft) from other storage piles, and total area of temporary storage less than 10% floor area. (non-sprinklered buildings)- | 1 month | Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review Storage piles in non-storage occupancies have been managed to have less than 8 feet height with minimum 3 m distances at Level 2, excessive storage occupying more than 10% of the floor area has been removed to new extension building. (Evidences of pile management are appended as Annexure "O" for ACCORD review and perusal) |  |  | 18-12-24: -Annexure O : provides information on the in process storage however factory has to resubmit the design to provide details of the in process storage arrangements. -Fabric storage not fire separated from cutting area. | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Storage | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Where storage does not meet the Pakistan Accord Building Standard requirements for “in-process storage” in production occupancies, then it needs to be separated with fire resisting construction. | Propose design and layout showing how storage areas will be rearranged and/or enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review Storage areas are being re-arranged, A New Finished Goods & Fabric Storage facilities has been constructed with Fire rated doors & construction, some of the load of storage area of inspected factory will be shifted to this new location. Design & Layout of the new Finished Goods warehouse & Fabric warehouse Storage areas are appended as Annexure "P" for ACCORD review & approval) |  |  | 18-12-24: Proposed new storage area is suitable as per submitted drawings. Factory has submitted plan to Accord and will implement after plan review by Accord | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Storage | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Where storage does not meet the Pakistan Accord Building Standard requirements for “in-process storage” in production occupancies, then it needs to be separated with fire resisting construction. | Separate storage areas that do not comply with in-process storage limits by 2-hr fire-rated construction with 1.5-hr opening protective assemblies. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | F32 + 4 months | Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord Storage areas are being re-arranged, A New Finished Goods & Fabric Storage facilities has been constructed with Fire rated doors & construction, some of the load of storage area of inspected factory will be shifted to this new location. Design & Layout of the new Finished Goods warehouse & Fabric warehouse Storage areas are appended as Annexure "P" for ACCORD review & approval) |  |  | 18-12-24: Proposed new storage area is suitable as per submitted drawings in Annexure "P". Factory will implement after the design review by Accord. | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Where offices occupy 10% or less of the floor area of a production floor they can be regarded as “incidental” to the main occupancy and do not need to be fire separated from that occupancy. Occupancies observed that may not be incidental and are not separated by fire and smoke resisting construction are as follows (non-exhaustive): - Level 2 offices are not separated from the production floor - Level 1 prayer area is an assembly occupancy and not separated from the production area - Level 1 walls between Offices, Cutting Department and Fabric Store are combustible materials (not fire resisting) - Unsealed penetrations and openings are located in fire-rated separating assemblies. | Propose design and layout showing how different occupancies can be rearranged and/or enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | Factory will prepare drawings showing proposed fire separating construction to high-risk areas and submit to Accord for review prior to the rectification works A New scheme for re-arranging different occupancies has been designed and will be enclosed with fire rated construction & exit assemblies. Layout & plan is prepared and execution is to be carried out shortly. (Lay out for re-arranging occupancies is appended as Annexure "Q" for ACCORD review & Approval.) |  |  | 18-12-24: Factory has submitted Drawings for separation of occupancy. Emergency Stairs and lift shaft should be Fire separated for all floors. Fifth Floor Dining and Pray Area Suitable Fourth Floor Finishing Suitable Second Floor Stitching Suitable First Floor Warehouse Suitable Ground Floor Storage Suitable Basement parking area suitable Inspection for new facility is pending before execution. Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies. | F34 + 4 months | A New scheme for separating different occupancies has been designed and will be enclosed with 2 hrs. fire rated construction & exit assemblies. Layout & plan is prepared and execution is to be carried out shortly. (Lay out for re-arranging occupancies is appended as Annexure "Q" for ACCORD review & Approval.) |  |  | 18-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. | Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | 8 months | Fire rated separation of occupancies will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord Few of the floor openings observed at the fire exit door assemblies have been sealed and lift shaft floor opening sealings are being discussed and carried out soon. (Evidences for fire door floor opening sealings are appended as Annexure "R" for ACCORD review & Perusal.) |  |  | 18-12-24: Annexure R is not suitable evidence for occupancies separation and unsealed penetration. Factory will resubmit plan for Accord review. | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Electrical rooms and transformer room not separated by fire and smoke resisting construction | Separate electrical room by 2-hr fire rated construction. | 4 months | Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord Fire rated door is being installed at electrical room and separation is designed through providing sand trap / separation grills to maintain ventilation for transformer and fire separation. (Fire Door shop drawing is appended as Annexure - "H" & Grill Design as Annexure "G" for ACCORD Review & Approval) |  |  | 18-12-24: Annexure G: Required full documentation and Certifications for all accessories for approval. Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Hazardous Materials | Chemicals storage | Storage, handling, and use of flammable and combustible liquids and/or solids | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and/or providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. | 4 months | Chemical storage has been corrected as per defined in their respective MSDS, all safety measures for storage have been adopted as described in MSDS, MSDS are displayed prominently at the storage areas of respective chemicals. list of compatibility will be developed and ensure the measures accordingly. (MSDS of Chemicals are appended as Annexure - "S" for ACCORD Review & Perusal) Fire rated separation in accordance with the Pakistan Building Code and NFPA 30. will be completed, including brickwork/ fire rated assemblies |  |  | 18-12-24: Annexure S: Factory has submitted local MSDS to Accord for Review. The factory must resubmit the MSDS sheets provided by the supplier/manufacturer for each chemical for Accord review. | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Means of Escape | Exit access | Broken Drainage hole at exit access at Ground Floor | Replace drainage cover | 2 weeks |  |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Means of Escape | Protection of stairs | Fire Load (Aircon outer) at Emergency Stair at Ground Floor | Remove all Fire load from Emergency stairs. | 2 weeks |  |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Means of Escape | Exit access | Obstruction at Roof Exit Access (Solar Girders) at Roof | Place a warning sign and provide padding at sharp edges | 1 month |  |  |  |  | In Progress
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
18-Dec-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Lucky Textile Mills Ltd. No.2, L-3, Block 2, F.B. Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 05-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Cracking | Column | This relates to RC columns and deep beams located along gl.-12 of Ground floor level. These cracks do not display any clear pattern that indicates the cause and they may just be within the plaster finish. | Sections of plaster finish to columns and deep beams to be removed to investigate if cracks are just plaster cracks or whether they penetrate the structural elements. | 2 months | These cracks are in plaster, these columns are already overdesign, and the after removal of plaster, will replaster the same column with in specified time. |  |  | In Progress | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Cracking | Column | This relates to RC columns and deep beams located along gl.-12 of Ground floor level. These cracks do not display any clear | If cracking found to penetrate the structural elements, building Engineer to carry out design check on beams to confirm whether structural repair and/or additional load limitations should be applied. Submit proposal for any remedial works if necessary to Pakistan Accord for review. Building Engineer to prepare Safe load plans based on outcome of assessment. | S1 + 4 months | After removal of plaster inspection to be done with Civl Consultant and than will decide the remedial action, if needed will submit remedial actions, if required. (Otherwise plaster repairing will be done as per the above timeline). Factory will share assessment report of Civil Consultant with Accord for review |  |  | In Progress | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Column | A vertical crack in the RC column is observed at GL 14/G of ground floor. No heavy storage at superstructural levels was observed at this location. | Sections of plaster finish to columns to be removed to investigate if cracks penetrate the building structure. Submit the site investigation results to Pakistan Accord for review. | 2 months | To check after removal of plaster of the same, and will replaster the same column with in specified time/ Factory will share assessment report of Civil Consultant with Accord for review |  |  | This column was repainted, without investigation of the crack. The factory will check if the crack is on render only or is propagating in column as well. In Progress | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Column | A vertical crack in the RC column is observed at GL 14/G of ground floor. | If cracking found to penetrate the structural elements, then the Building Structural Engineer to determine the cause of cracking and design appropriate remedial measures. Submit proposal for any remedial works if necessary to Pakistan Accord for review. | S3 + 4 months | After removal of plaster inspection to be done with Civl Consultant and than will decide the remedial action, if needed will submit remedial actions, if required. (Otherwise plaster repairing will be done as per the above timeline. Factory will implement remedial measures if necessary, in accordance with report previously reviewed by Accord |  |  | In Progress | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Structural System | Lateral stability system | No apparent lateral stability system observed at 1st Floor level where a flat slab form of construction is used; it is not clear how the lateral forces are resisted at the this level. RCC lift shafts provide some assistance to resist the lateral loads but the zone between gl. 5a to 9a does not have any lift shafts, so the lateral stability support system is not obvious. | Structural Engineer to carry out building stability analysis against the lateral loads and propose additional stability system if required. Submit results of stability analysis and any proposed remediation measures (if required) to Pakistan Accord for review before undertaking the works. | 3 months | This structure is properly designed and design check also done at the time of renovation, also we involved third party for integrity testing and as advised our Civil Consultant will check accordingly one module of this building and submit test results accordingly. Factory will share assessment report of Civil Consultant with Accord for review |  |  | In Progress | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural System | Lateral stability system | No apparent lateral stability system observed at 1st Floor level where a flat slab form of construction is used; it is not clear how the lateral forces are resisted at the this level. | Implement remediation measures (if required) in accordance with Pakistan Accord Building Standard. | S5 + 4 months | After Design check, Design conformance will decide the remedial action, if needed will submit remedial actions, if required. |  |  | In Progress | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural System | Vertical load path | RC column is located off grid, while RC beams are located on the grid. | Building Structural Engineer to verify the shear capacity of the RC beam as-built. Submit proposal for any remedial works if necessary to Pakistan Accord for review if excessive shear stresses found in the beams. | 3 months | The primary Beams are designed for Secondary beam point load - We will share the design reports of Ferro Scanning of subject beams after verification of Civil Consultant |  |  | In Progress | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural System | Vertical load path | RC column is located off grid, while RC beams are located on the grid. | Carry out any remedial works to address excessive shear forces if found necessary. | S7 + 4 months | After Design check, Design conformance will decide the remedial action, if needed will submit remedial actions, if required. |  |  | In Progress | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Loading | Uncontrolled loading | Excessive loading of fabric storage at 1st floor level. | Building Engineer to consider temporary reduction/removal of storage until an assessment on the load capacity of the as-constructed suspended slab is completed. | 1 month | We will collect data along with Production team and will prepare Safe Load Plans as per current situation and we will suggest / manage Load pattern as per design limitation with the support of Compliance Team and paste in the floors for implementation. |  |  | In Progress | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Loading | Uncontrolled loading | No safe load plans were posted anywhere in the factory | Building Engineer to produce loading plans for all floors within the factory. Loading to be actively managed by Factory Management. | 6 months | Safe Load Plans will pasted on the floor with the support of Compliance team |  |  | In Progress | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Structural Design | Drawings differ from as-built | Discrepancies were observed between the structural drawings and the as-built condition on site. | Building Engineer to survey the building and produce accurate and complete as-built documentation. | 6 months | We will in the process of updation of Building As Built Drawing and after verification of Civil Consultant, we will share the same with Accord |  |  | The drawings are not prepared yet, the factory will share the drawing with Accord. In progress | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Other Damage/Defects | Moisture ingress | Water ingress and leakage is potentially causing corrosion of reinforcement, leading to cracking and lasting damage to RC structural elements at - overhang slabs around the perimeter. - RC beams at 2nd floor and Roof levels. . | Building Engineer to remove sections of plaster finish from the structural elements to investigate if the cracks penetrate through the RC structure. If they do, then submit a proposal for any remedial works to the Pakistan Accord for review. The proposed remedial works could involve: - Removal of damaged concrete, cleaning of the corroded layout of the reinforcement bars, and reinstatement of adequate steel reinforcement cover. - Eliminate any means of water ingress that could further affect the reinforcement. | 6 months | The moisture stains and paint deterioration were due to leakage / seepage from toilets / AC Drainage of above floor in different locations and the same to be repaired as per the methodology specified and submit the confirmance after repairing the same with in specified time. |  |  | In Progress | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Other Damage/Defects | Column impact damage | The column on grid A-19 the second floor was damaged by impact of trolley. | Repair damage to column corners and external faces | 3 months |  |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Other Damage/Defects | Column impact damage | The column on grid A-19 the second floor was damaged by impact of trolley. | Install protective measures to prevent damage recurring | S13 + 3 months |  |  |  |  | In Progress
[8 empty] | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Cracking | Beams | The beam on grid F11 to F 13a was cracked. The cause of cracking can be overloading during installation of solar panels on roof. | Building Engineer to carry out condition survey of the RC beams to investigate cause and impact of these cracks on the capacity of the beams. | 2 months |  |  |  |  | In Progress
[8 empty] | Follow Up | [10 empty] | S16 | Cracking | Beams | The beam on grid F11 to F 13a was cracked. The cause of cracking can be overloading during installation of solar panels on roof. | Propose the remedial works if necessary to Pakistan Accord in situation if the RC beams are not in line with the design requirements. Once reviewed, implement the remedial works. Continue monitoring them on an on-going basis. | S15 + 4 months |  |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Other Damage/Defects | Damaged strucutral element | On the 1st floor of the building at multiple location there were voids in the structural beams and columns. The voids were because of extraction of core and they were not filled after core extraction | The factory need to fill in the core holes with high strength grout. | 3 months |  |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Damaged structural element

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1