## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
26-Feb-2025
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Magna Processing Industries (Pvt) Ltd - Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 26-Feb-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
[9 empty] | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | INSPECTION TYPE | REFERENCE NUMBER | CAP ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | [18 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-25 | 2025-09-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were not available. | Developed comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [11 empty] | E3 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were not available. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Electrical layout drawing | It was noted that the factory has not available electrical layout drawings, including power layouts, lighting layouts, fire alarm layouts, earthing layouts and containment layouts. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Electrical layout drawing | It was noted that the factory has not available electrical layout drawings, including power layouts, lighting layouts, fire alarm layouts, earthing layouts and containment layouts. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E4 + 3 months | 2026-03-19 | 2026-06-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | It was also found that the multiple circuit breakers had ratings that were not appropriate for the connected cable sizes such as: - Ground floor distribution board 100A circuit breaker with 6mm² cable. - Second floor distribution board 150A circuit breaker with 2x6mm² cable. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E7 | DBs & Elec Protection Systems | Circuit breakers | It was also found at multiple locations, such as the ground floor Canteen area distribution boards, that single-phase outgoing from three pole Breaker. Using a single phase of a three-pole breaker can lead to unbalanced load conditions. | Remove the single-phase from the three-pole breaker and use a single-pole breaker for single-phase connection out as per standard cable current carrying capacity. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | It was observed that the circuit breakers were installed in the facility without fixing supports and protective enclosures. Observed at basement office and third floor lift distribution board. | Fix all circuit breakers that are loosely installed throughout the facility with concealed metallic enclosures to ensure safety and compliance with standards BS 7671 Section 416. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Hot Spots | During the inspection, it was found that hot spot within the distribution boards. Observed at ground, first and second floor distribution boards. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | During the inspection, it was found that hot spot within the distribution boards. | Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring the safe and reliable operation of the electrical systems. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | It was also found that the thermographic test report was not available at the site. | Carry out an independent thermographic survey of the entire electrical system on a bi-annual basis. Submit the thermographic test report to the Pakistan Accord for information. | E10 + 6 months | 2025-12-19 | 2026-06-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | It was found that the earth circuits distribution was missing in multiple distribution boards and power plugs. Observed at such as: basement, ground and second floor distribution boards. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. Submit the earthing system design to the Pakistan Accord for information. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | It was found that the earth circuits distribution and bonding were missing in multiple distribution boards and power plugs. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E12 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | It was found that the equipotential bonding for the distribution board front doors, cable trays, machines body and metallic panel covers were missing. Observed at such as: basement and ground floor distribution boards and cable trays. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | It was found that the earth testing record was not available at the site. | Develop and submit the earth testing record to the Pakistan Accord for information. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was also found that there was loose wiring and insufficient working space inside the distribution boards for operation and maintenance. | Install wire ducts to organize and route wires neatly, remove loose cables, and ensure that no cables are attached to the bus bars. This may mean the addition of new distribution boards with proper accessibility for cables incoming and outgoing, bus-bar alignment. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was found that the basement, ground and second floor distribution boards lack a dedicated neutral connection for outgoing power circuits. | Conduct a thorough inspection of the existing wiring to identify circuits sharing a neutral wire. Provide dedicated neutral wires for each circuit, ensuring that each circuit's return path is properly isolated in accordance with BS 7671 (18th Edition) regulation 314.4. | E16 + 3 months | 2025-11-19 | 2026-02-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was observed that the front door of the ground floor water pump distribution board was not opening properly and was getting stuck halfway. | Check if the door is misaligned. Adjust the hinges or mounting to ensure it opens fully without obstruction. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was also found that there was loose wiring and insufficient working space inside the distribution boards for operation and maintenance, a lack of dedicated neutral connections, and panel door was stuck. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Loop Connection | loop connections were identified within the electrical distribution boards. In these loop connections, one circuit breaker is energized by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. Observed at, basement, ground, first and third floor distribution board. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multi looping was observed in a number of electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. Observed at, basement, ground, first and second floor distribution boards, | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022) | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Openings | It was found that many distribution boards have openings, which may cause potential hazards due to environmental factors. In the future avoid any unnecessary openings from distribution boards, and cable trays. Observed at ground, first and third floor distribution boards. | Examine the entire facility panels to identify all openings, holes, and gaps that need to be sealed. Seal the openings, holes of panels, cable trays and trenches with metallic enclosures, fire-resistant sealants, gaskets, or fillers, use cable glands for cable entry. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Openings | It was found that many distribution boards have openings, which may cause potential hazards due to environmental factors. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | E22 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Adequate accessibility | At multiple locations, it was found that the electrical distribution boards and breaker box do not possess the required space for inspection or easy access to the panels and their components. Observed at first floor cutting office and third floor lift distribution board (The lift distribution board had an out of order tag, but power was still present inside the panel). | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards. Observed at ground floor Canteen area, the distribution board. | All electrical panels and distribution boards shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and distribution boards. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E25 + 3 months | 2025-10-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was found that no lightning protection system was installed throughout the facility also any LPS risk assessment was not available. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment for each building. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was found that the surge arrestor system was found which was serving as an LPS. however, there was no risk assessment available to confirm its adequacy. | If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). | E27 + 6 months | 2025-11-19 | 2026-05-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E29 | Fire Alarm & Detection System (FADS) | No FADS | It was also observed that the basement area was not connected to the main fire alarm panel. Additionally, a separate hooter system was installed for the basement, which failed to operate during testing. | Connect the basement area to the main fire alarm panel to ensure centralized monitoring and control. Replace or repair the faulty hooter system to ensure proper alarm activation during emergencies. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that conventional and not listed fire alarm system was installed for the facility. However, several deficiencies were noted, including the absence of fire alarm devices in offices, utility rooms, the use of non-listed devices, insufficient audibility, and the lack of visual alarms, detectors were installed not at the highest point. Additionally, non fire rated cable used throughout all systems. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that a conventional and non-listed fire alarm system was installed for the facility. | (i) Submit design documentation for existing system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that a conventional and non-listed fire alarm system was installed for the facility. | (ii) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E31 + 1 month | 2025-12-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that a conventional and non-listed fire alarm system was installed for the facility. | (iii) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E32 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that a conventional and non-listed fire alarm system was installed for the facility. | (iv) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | E33 + 5 months | 2026-05-19 | 2026-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that a conventional and non-listed fire alarm system was installed for the facility. | (v) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E34 + 3 months | 2026-10-19 | 2027-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that a conventional and non-listed fire alarm system was installed for the facility. | (vi) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E35 + 3 months | 2027-01-19 | 2027-04-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Routine testing of the Fire Alarm and Detection System (FADS) has not been performed consistently. | Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E38 | Emergency Lighting | Provided but insufficient | It was found that the non-compliant emergency lights provided in the facility were insufficient to cover the entire facility. The emergency lighting did not provide adequate illumination levels, leading to dark or poorly lit areas during power outages. This inadequate coverage may cause incidents during emergencies. - Observed at basement and first floor emergency exit and production areas. | Submit the emergency lighting system design to the Pakistan Accord for information. Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional compliant emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E39 | Emergency Lighting | Provided but insufficient | It was found that the non-compliant emergency lights provided in the facility were insufficient to cover the entire facility. The emergency lighting did not provide adequate illumination levels, leading to dark or poorly lit areas during power outages. This inadequate coverage may cause incidents during emergencies. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E38 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E40 | Emergency Lighting | Provided but insufficient | External emergency lighting was not provided. | Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s). | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E41 | Emergency Lighting | Independent power source | it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Observed at each floor of buildings. Proper circuitry is crucial to ensure that emergency lighting is automatically activated when general lighting fails. This automatic activation is essential for maintaining sufficient illumination, allowing for the safe evacuation of occupants and preventing panic during power outages. Further the emergency lights and exit signs be reconfigured to be connected on a dedicated single circuit, which must not include any other load except for the emergency lighting system According to the Building Code of Pakistan Fire Safety Provisions 2016, emergency lighting systems must be designed to provide immediate illumination in the event of power loss to ensure a clear and safe path for evacuation. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E42 | Emergency Lighting | Independent power source | it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E41 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E43 | Emergency Lighting | General Lighting | Many general lights were fixed by cable ties, ropes with cable trays and many lights were found to have no hanging supports, which posing a risk of equipment damage or incidents due to instability and potential for falling. Observed at first and second floor production area. | Ensure all general lights are properly mounted using appropriate fixtures instead of cable ties or ropes. Install secure hanging supports to prevent instability and potential falling hazards. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E44 | Emergency Lighting | General Lighting | it was found that the insufficient lighting coverage to cover the entire second floor i.e. main distribution board. | Conduct a thorough assessment of lighting throughout the facility to find areas with insufficient illumination. Install additional lighting fixtures in these spots to ensure adequate brightness. Ensure the new lighting design meets safety and efficiency guidelines to provide clear visibility for all tasks and emergency situations. | E43 + 3 months | 2025-11-19 | 2026-02-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E45 | Emergency Lighting | General Lighting | it was found that the insufficient lighting coverage to cover the entire second floor i.e. main distribution board. | Regularly inspect and maintain light fixtures to ensure safety and compliance. | E44 + 2 months | 2026-02-19 | 2026-04-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E46 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | The ventilation system was inadequate, with insufficient air flow leading to heat accumulation in the HT Room. | Hire a qualified engineer to check whether ventilation requirement is sufficient or not and implement it, also share with Pakistan Accord as well. Redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the HT Room receive adequate ventilation. This might involve repositioning vents or adding ductwork. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E47 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | Several sections of the HT Room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | Add more lighting fixtures in poorly lit areas to ensure even distribution of light throughout the room. Focus on areas that require the highest visibility, such as around equipment and control panels. | E46 + 3 months | 2025-11-19 | 2026-02-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E48 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | Several sections of the HT Room were poorly lit, along with insufficient ventilation. | Establish regular maintenance and testing of the ventilation and illumination system within the spaces to ensure adequate performance. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E49 | Cabling & Wiring | Cables support and protection | It was found that at different locations the cables were running without cable containment, such as cable trays, conduits, or ducting. cables were laid directly over the floor. Inadequate cable containment and support results in sagging or stress on cables, which can lead to damage or failure. Observed at, ground floor, first floor and third floor production areas and office rooms. | Secure cables with appropriate containment and supports to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E50 | Cabling & Wiring | Cables support and protection | It was found that at different locations the cables were running without cable containment, such as cable trays, conduits, or ducting. cables were laid directly over the floor. Inadequate cable containment and support results in sagging or stress on cables, which can lead to damage or failure. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices. | E49 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E51 | Cabling & Wiring | Cable trench and channel cleanliness | It was found that the numerous cable trays were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. Observed at the second floor cable trays. | Clean cable trays and all cable trenches to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E52 | Cabling & Wiring | Cable trench and channel cleanliness | It was found that the numerous cable trays were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable containments to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | E51 + 3 months | 2025-10-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E53 | Cabling & Wiring | Splicing of cables | It was found that the cable terminations were installed without cable lugs, which resulted in breaking strands, and loose connections This presents a significant fire risk due to the potential for electrical arcing and overheating. Observed at the first, second and third floor distribution board. | Install cable lugs on all improperly terminated cables within the distribution boards to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E54 | Cabling & Wiring | Splicing of cables | It was found that the cable terminations were installed without cable lugs. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | E53 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E55 | Cabling & Wiring | Splicing of cables | PVC tape joints were found at ground floor distribution boards, second floor stitching machine cables. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E56 | Cabling & Wiring | Splicing of cables | PVC tape joints were found at ground floor distribution boards, second floor stitching machine cables. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices | E55 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E57 | Cabling & Wiring | Splicing of cables | It was noted that the insulation of cutting machine cables was damaged at first floor of cutting tables and second floor main distribution board. | Repair or replace the damaged cable insulation in the distribution boards to restore proper insulation, in compliance with BS 7671, Regulation 526.1, which requires all connections to be electrically sound and insulated to prevent accidental contact. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E58 | Cabling & Wiring | Colour coding | During the inspection of multiple distribution boards, deviations from standard cable colour coding practices were identified. Observed at ground, first and second floor production area distribution boards. (In the second floor main distribution board bus bars need to be repainted with the respective colour codes or insulation). | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E59 | Cabling & Wiring | Colour coding | During the inspection of multiple distribution boards, deviations from standard cable colour coding practices were identified. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | E58 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E60 | Cabling & Wiring | Fixture | Wooden switchboards were found at the ground floor HT Room, along with a wooden piece inside a distribution board and electrical connections wrapped with plastic sheets observed at the basement and ground floor area. | Replace the wooden Switchboard with a non-combustible enclosure designed for electrical installations. Remove wooden and plastic materials from distribution boards and appliances. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E61 | Cabling & Wiring | Fixture | Wooden switchboards were found at the ground floor HT Room. | Establish a facility-wide standard to use only non-combustible materials for mounting electrical components, and conduct regular audits for compliance. | E60 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E62 | Cabling & Wiring | Fixture | It was also observed that the power receptacle was installed in an unsuitable location outside the ground floor outdoor area. | Relocate power receptacles in compliant locations with proper fixing. If relocation is not possible, ensure the receptacle is installed in a weatherproof enclosure rated for outdoor use. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E63 | Cabling & Wiring | Fixture | It was also observed that the power receptacle was installed in an unsuitable location outside the ground floor outdoor area. | Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed. | E62 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
26-Feb-2025
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Magna Processing Industries (Pvt) Ltd - Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 26-Feb-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-25 | 2025-09-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | - Escape doors are lockable at other Buildings (HR office & Corton store) , Main Building (roof) & main facility exit door. - Main door of facility swing against the direction of escape. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-09-19 | 2025-10-03 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | - Escape doors are lockable at other Buildings (HR office & Corton store) , Main Building (roof) & main facility exit door . - Main door of facility swing against the direction of escape. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Pakistan Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | - Escape doors are lockable at other Buildings (HR office & Corton store) , Main Building (roof) & main facility exit door. - Main door of facility swing against the direction of escape. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | - Obstructions and trip hazards on escape route at Main Building (roof & Basement floor (Storage area)). | Remove obstructions/trip hazards on escape routes and keep them clear for escape. | 2 weeks | 2025-09-19 | 2025-10-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | - Obstructions and trip hazards on escape route at Main Building (roof & basement floor (storage area)). | Ensure that all escape routes are kept free from obstructions and trip hazards. | 2 weeks | 2025-09-19 | 2025-10-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Protection of stairs | - Unprotected openings into stair S2(all floors) - Door not fire door in stair S1 & s2 (all floors). - Fire load in/under stair S1 (all floors). | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | 2025-09-19 | 2025-10-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Protection of stairs | - Unprotected openings into stair S2(all floors) - Door not fire door in stair S1 & s2 (all floors). - Fire load in/under stair S1 (all floors). | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Protection of stairs | - Unprotected openings into stair S2(all floors). - Door not fire door in stair S1 & s2 (all floors). - Fire load in/under stair S1 (all floors). | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating. construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Doors into stairs should be kept closed (but not locked) at all times. | F8 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs at Main Building (roof). - Missing exit signs at stair discharge routes Main Building (Ground floor). - Missing exit signs in corridors and circulation areas Main Building (all floors). - Missing exit signs at roof of Main Building. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs at Main Building (roof). - Missing exit signs at stair discharge routes Main Building (Ground floor). - Missing exit signs in corridors and circulation areas Main Building (all floors). - Missing exit signs at roof of Main Building. | Ensure that all exit signage is checked periodically and in good working condition. | F10 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Fire Rated Construction | Separation of high-risk areas | - Electrical rooms are not fire separated from labor entry corridor with fire rated construction at other Buildings. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Fire Rated Construction | Separation of high-risk areas | - Electrical rooms are not fire separated from labor entry corridor with fire rated construction at other Buildings. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F12 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Fire Rated Construction | Separation of shafts | - Lift shafts is not separated with fire rated construction at Main Building (all floors). | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Fire Rated Construction | Separation of shafts | - Lift shafts is not separated with fire rated construction at Main Building (all floors). | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F14 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Fire Rated Construction | Floor openings | - Open void (Spiral stair- which is considered that it's not a part of escape plan) connecting different floors at Main Building (all floors). | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Fire Rated Construction | Floor openings | - Open void (Spiral stair- which is considered that it's not a part of escape plan) connecting different floors at Main Building (all floors). | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F16 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Fire Rated Construction | Separation of occupancies | - Canteen not separated from production at Main Building (ground floor). | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors) | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Fire Rated Construction | Separation of occupancies | - Canteen not separated from production at Main Building (ground floor). | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F18 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Storage | - Storage areas are not fire separated from the rest of the building at Main Building (1st, 2nd & basement floor ). | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Storage | - Storage areas are not fire separated from the rest of the building at Main Building (1st, 2nd & basement floor ). | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F20 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Safety Management | Fire drills | - No regular fire drills. - Fire drill documentation is of poor standard. - Not all staff are involved in fire drills. - Not all staff know what to do in the event of fire. | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Safety Management | Fire drills | - No regular fire drills. - Fire drill documentation is of poor standard. - Not all staff are involved in fire drills. - Not all staff know what to do in the event of fire. | Ensure fire drills are performed a minimum 2 times per year. | F22 + 2 months | 2025-11-19 | 2026-01-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Safety Management | Records of system testing | - Inadequate records of testing of Fire Extinguishers. | - Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Safety Management | Records of system testing | - Inadequate records of testing of Fire Extinguishers. | - Ensure all systems are being tested as per the schedule agreed with Pakistan Accord . - Keep testing records. | F24+ 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Fire Extinguishers. | - Set up a maintenance schedule for all life safety systems. - Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Fire Extinguishers. | - Ensure all systems are being maintained as per the schedule agreed with Accord . - Keep maintenance records. | F26+ 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Prepare an Emergency Action Plan report. | 2 months | 2025-09-19 | 2025-11-19 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F28 + 2 months | 2025-11-19 | 2026-01-19 | AGREE |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
26-Feb-2025
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Magna Processing Industries (Pvt.) Ltd. - Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 26-Feb-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-07-25 | 2025-09-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns or existing cylinder or cube strength data and submit results to Accord. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | Factory Engineer to review design, loads and columns stresses in area identified and submit to Pakistan Accord for review. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building , in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 2 months | 2025-07-25 | 2025-09-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review. | S4 + 3 months | 2025-09-25 | 2025-12-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths along with safe load plans reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan. | S5 + 4 months | 2025-12-25 | 2026-04-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | (4) Submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review | S6 + 4 months | 2026-04-25 | 2026-08-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord | S7 + 6 months | 2026-08-25 | 2027-02-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete. | S8 + 1 month | 2027-02-25 | 2027-03-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal basement floor columns highlighted in plan appear to be over stressed for the observed load. The size of column and number of floors could be the reason for these highly stressed columns. | Continue to implement load plan. | S9 + 1 month | 2027-03-25 | 2027-04-25 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Structural System | Lack of local stability | Poor connection details and lack of local stability in supporting mechanism of circular staircase has been observed in Main Building. | Building Engineer to review the design of staircase and propose any strengthening measures as required. Submit the proposal to Pakistan Accord for approval. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Structural System | Lack of local stability | Poor connection details and lack of local stability in supporting mechanism of circular staircase has been observed in Main Building. | Implement the remediation as required. | S11+3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Structural System | Lateral stability system | This relates to the structural stability system in the lateral direction of structure (Basement to roof) which is observed to be beam in one direction only. In a moment frame building the structural stability is provided by beams and columns acting together, whereas if the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Structural System | Lateral stability system | This relates to the structural stability system in the lateral direction of structure (Basement to roof) which is observed to be beam in one direction only. In a moment frame building the structural stability is provided by beams and columns acting together, whereas if the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary. Also submit the proposed line of action to Pakistan Accord for approval. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Structural System | Lateral stability system | This relates to the structural stability system in the lateral direction of structure (Basement to roof) which is observed to be beam in one direction only. In a moment frame building the structural stability is provided by beams and columns acting together, whereas if the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Propose strengthening works as required. | S14 + 1 month | 2025-12-19 | 2026-01-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Structural System | Lateral stability system | This relates to the structural stability system in the lateral direction of structure (Basement to roof) which is observed to be beam in one direction only. In a moment frame building the structural stability is provided by beams and columns acting together, whereas if the beams are omitted in one or both directions on one or more floors the ability of this system to resist lateral loads is reduced. | Carry out remedial works as required. | S15 + 4 months | 2026-01-19 | 2026-05-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Other Damage/Defects | Moisture ingress | Water ingress and leakage is potentially causing damage to RC beams and slabs. Improper drainage of the roof slab, particularly due to the presence of rainwater, also affects RC beams and slabs. Similarly, moisture ingress has been observed in basement wall and the presence of high water table at site could be the reason for this moisture ingress. It might cause corrosion in reinforcement and concrete spalling, which can result in injuries | Identify the source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Other Damage/Defects | Moisture ingress | Water ingress and leakage is potentially causing damage to RC beams and slabs. Improper drainage of the roof slab, particularly due to the presence of rainwater, also affects RC beams and slabs. Similarly, moisture ingress has been observed in basement wall and the presence of high water table at site could be the reason for this moisture ingress. It might cause corrosion in reinforcement and concrete spalling, which can result in injuries | Inspect damage to the slab and beam and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-09-19 | 2025-12-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Other Damage/Defects | Moisture ingress | Water ingress and leakage is potentially causing damage to RC beams and slabs. Improper drainage of the roof slab, particularly due to the presence of rainwater, also affects RC beams and slabs. Similarly, moisture ingress has been observed in basement wall and the presence of high water table at site could be the reason for this moisture ingress. It might cause corrosion in reinforcement and concrete spalling, which can result in injuries | Implement remedial work. | S18 + 3 months | 2025-12-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Other Damage/Defects | Moisture ingress | Water ingress and leakage is potentially causing damage to RC beams and slabs. Improper drainage of the roof slab, particularly due to the presence of rainwater, also affects RC beams and slabs. Similarly, moisture ingress has been observed in basement wall and the presence of high water table at site could be the reason for this moisture ingress. It might cause corrosion in reinforcement and concrete spalling, which can result in injuries | Continue to monitor for future signs of water ingress. | S19 + 3 months | 2026-03-19 | 2026-06-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Other Damage/Defects | Health and Safety | No adequate edge protection is provided to the roof. This can cause a risk of potential injury resulting from slip, trip, or fall from the roof during the access and maintenance of the roof. | Provide an appropriate roof edge protection to all accessible roofs. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Other Damage/Defects | Health and Safety | No adequate safety protection is provided to the staircase ground to roof as highlighted in plan. This can cause a risk of potential injury resulting from slip, trip, or fall from the staircase during the movement from one floor to other. | Provide an appropriate edge protection to all staircases. | 1 month | 2025-09-19 | 2025-10-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Structural Documentation | Documentation unavailable | Documentations such as geotechnical report and structural drawings were missing. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Structural Documentation | Lack of safe load plans | Floor wise safe load plans were missing. | Building structural engineer to review design documentation to confirm load capacity of the structure. | 6 months | 2025-09-19 | 2026-03-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Structural Documentation | Lack of safe load plans | Floor wise safe load plans were missing. | Factory to post safe load plans on each floor. | S24 + 1 month | 2026-03-19 | 2026-04-19 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1