## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
2025-05-20
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Maheen Textile Mills (Pvt.) Ltd. - 28 Km Sheikhupura Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2025-05-20
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-09-04 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | This section refers to the electrical rooms within the facility. During the inspection conducted, it was observed that there were no electrical room layout drawings available for the factory. There are no visible indications of electrical equipment locations or pathways for maintenance and emergency access. | Develop detailed electrical room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | This section refers to the electrical rooms within the facility. During the inspection conducted, it was observed that there were no electrical room layout drawings available for the factory. There are no visible indications of electrical equipment locations or pathways for maintenance and emergency access. | Regularly update and review the electrical room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2 + 6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | This section refers to the entire facility. It was found that the electrical single line diagrams (SLDs) for the factory were missing. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | This section refers to the entire facility. It was found that the electrical single line diagrams (SLDs) for the factory were missing. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4 + 6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | This section refers to the entire facility. During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | This section refers to the entire facility. During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6 + 6 months | 2025-12-30 | 2026-06-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | This section refers to the entire facility. During the survey, the circuit breakers installed throughout the facility inside the electrical panels and distribution boards were inspected. It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. - In the Cutting Hall electrical panel, a 16 sq.mm cable was connected to a 125A circuit breaker. - On the ground floor of Production Building B3, a 16 sq.mm cable was connected to a 100A circuit breaker. - In the Warehouse area of Production Building B2 (Ground Floor), a 10 sq.mm cable was connected to a 200A circuit breaker. - At Packing 2 in Production Building B2 (Ground Floor), a 10 sq.mm cable was connected to a 63A circuit breaker. - On the 1st floor of Production Building B2, a 10 sq.mm cable was connected to a 100A circuit breaker. - In the Solar Distribution Panel, a 400 sq.mm cable was protected by a 1000A circuit breaker. - On the 1st floor of Production Building 3, a 16 sq.mm cable was connected to a 100A circuit breaker. - In the Head Office main panel, a 95 sq.mm cable was connected to a 630A circuit breaker. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Hot Spots | This relates to the entire facility. During the inspection, Thermographic surveys were conducted on the electrical boards. The survey identified numerous hot spots within panels and distribution boards. Here are the location of the hotspots: a) Main ACB Incoming, Powerhouse. b) LT Panel. c) Solar Inverter Room. d) Compressor DB, Utilities 2. e) Canteen DB. f) Production Building 1. g) Production Building 3, 1st Floor. h) Production Building 2, Ground Floor (Packing Department). i) Production Building 2, 2nd Floor. j) Head Office Main Panel. k) Gate Office Electrical Panel (Sign of Burning). l) Admin Block 2, Outer DB. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 week | 2025-10-30 | 2025-11-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | This relates to the entire facility. During the inspection, Thermographic surveys were conducted on the electrical boards. The survey identified numerous hot spots within panels and distribution boards. Here are the location of the hotspots: a) Main ACB Incoming, Powerhouse. b) LT Panel. c) Solar Inverter Room. d) Compressor DB, Utilities 2. e) Canteen DB. f) Production Building 1. g) Production Building 3, 1st Floor. h) Production Building 2, Ground Floor (Packing Department). i) Production Building 2, 2nd Floor. j) Head Office Main Panel. k) Gate Office Electrical Panel (Sign of Burning). l) Admin Block 2, Outer DB. | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | Previous thermographic scan reports were not available at the time of inspection. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | E10 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | i. The earth pits were inaccessible and unsuitably located (e.g., production building 3 – inaccessible earth pit). | i. Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | ii. The earthing cables were not appropriately sized according to the relevant earthing standards. | ii. Replace all earthing cables with appropriately sized cables as per the requirements of BS 7671 18th Edition + A2 (2022) Appendix 4, Section 5. Verify that all earthing conductors meet the minimum cross-sectional area specified. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | iii. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections (e.g., compressor room DB in Utilities 2 Building; Production Building B2 electrical panel; cutting hall DB; Production B2 1st floor electrical panel; LT panel; lamination department in utilities 2; Production Building 1 fabric store; production building 3 1st floor DB; knitting main panel). | iii. Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | iv. It was noted that the earth bar was incorrectly connected to the neutral bar, indicating improper grounding practices (e.g., LT panel in generator room; warehouse – Production Building B2 ground floor; Packing 2 – Production Building B2 ground floor). | iv. Disconnect the earth bars from the neutral bars with the distribution boards and ensure proper separation and connection | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | v. Equipotential bonding for the cable trays and metallic panel covers was missing (e.g., Production B3 ground floor electrical panel; Packing 2 – Production Building B2 ground floor). | v. Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Earthing system | vi. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. | vi. Prepare a comprehensive earthing system diagram, including identification of all earthing and neutral system components. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. The earth pits were inaccessible and unsuitably located (e.g., production building 3 – inaccessible earth pit). ii. The earthing cables were not appropriately sized according to the relevant earthing standards. iii. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections (e.g., compressor room DB in Utilities 2 Building; Production Building B2 electrical panel; cutting hall DB; Production B2 1st floor electrical panel; LT panel; lamination department in utilities 2; Production Building 1 fabric store; production building 3 1st floor DB; knitting main panel). iv. It was noted that the earth bar was incorrectly connected to the neutral bar, indicating improper grounding practices (e.g., LT panel in generator room; warehouse – Production Building B2 ground floor; Packing 2 – Production Building B2 ground floor). v. Equipotential bonding for the cable trays and metallic panel covers was missing (e.g., Production B3 ground floor electrical panel; Packing 2 – Production Building B2 ground floor). vi. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. |  | 2025-10-30 | Invalid | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | i. In a number of external areas, it was observed that electrical components were not suitable for the environmental conditions in which they were installed (e.g., outside the admin building; outside production building 3; production building 3 outer area). | i. Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | ii. Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. | ii. Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | iii. There were visible signs of damage to panels, cables, and busbars (e.g., broken or uninsulated busbar base in admin block; faulty indication lights in canteen kitchen ground floor of Utilities 2 Building; faulty voltage meter and phase indicator lights at gate office electrical panel). | iii. Inspect and repair or replace all damaged panels, cables, and busbars to ensure the integrity of the electrical system in accordance with Section 522 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Panel/cabling/busbar | iv. Additional concerns included missing phase separators, exposed copper busbars, and inadequate cable dressing in most of the distribution boards (DBs) (e.g., head office main panel – missing phase separators; kitchen canteen ground floor – cable dressing and uninsulated busbar issue in Utilities 2 Building; improper cable dressing in Production B3 ground floor and first floor electrical panels; Packing 1 and 2 in Production Building B2 ground floor; cutting DB in Production Building 1). | iv. Identify and replace unfixed and inadequately installed electrical components to ensure the integrity of the electrical system in accordance with Section 522 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the entire facility. The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas, it was observed that electrical components were not suitable for the environmental conditions in which they were installed (e.g., outside the admin building; outside production building 3; production building 3 outer area). ii. Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. iii. There were visible signs of damage to panels, cables, and busbars (e.g., broken or uninsulated busbar base in admin block; faulty indication lights in canteen kitchen ground floor of Utilities 2 Building; faulty voltage meter and phase indicator lights at gate office electrical panel). iv. Additional concerns included missing phase separators, exposed copper busbars, and inadequate cable dressing in most of the distribution boards (DBs) (e.g., head office main panel – missing phase separators; kitchen canteen ground floor – cable dressing and uninsulated busbar issue in Utilities 2 Building; improper cable dressing in Production B3 ground floor and first floor electrical panels; packing 1 and 2 in Production Building B2 ground floor; cutting DB in Production Building 1). | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E21 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Loop Connection | This relates to the entire facility. During the inspection loop connections were identified within the electrical panels. In these loop connections, one circuit breaker is energized by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. The issue was note at Packing 2 Production Building 2 ground floor. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilized to provide each circuit with the required live, neutral, and earth connections. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Multiple Connections | This relates to the whole facility. During our inspection, multilooping was observed in a number of electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. The issue was noted at packing 1 Production Building B2 ground floor, Lamination Department Utilities 2 and Production Building 2 ground floor packing area. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Openings | This relates to the entire facility of the factory. During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements. Unsealed openings were discovered in the panels and distribution boards at multiple locations, including Production B2, Packing 2 (ground floor), Power house (1st floor solar area), main LT panel, cutting area (Production B1), Production B3, Production B2 warehouse (ground floor), and the Knitting Building. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Openings | This relates to the entire facility of the factory. During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements. Unsealed openings were discovered in the panels and distribution boards at multiple locations, including Production B2, Packing 2 (ground floor), Power house (1st floor solar area), main LT panel, cutting area (Production B1), Production B3, Production B2 warehouse (ground floor), and the Knitting Building. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | E26 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Adequate accessibility | This relates to the entire facility. During the visit, the electrical panels and distribution boards were examined for adequate accessibility. At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. The issue was noted at Lamination Department Utility 2, Production Building 2 ground floor packing 1 and 2, and Production Building 3. In several instances, the placement of electrical panels adjacent to machines that continuously reject heat has caused the surrounding temperature to exceed ambient levels by several degrees. This temperature rise further increases the temperature of the panels and boards nearby. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | DBs & Elec Protection Systems | Lint & dust inside panel board | This relates to the entire facility. During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. The issue was noted at multiple locations, including lint and dust accumulation inside cable trays in the cutting hall (ground floor) and Packing 2 (Production Building B2, ground floor), as well as general cleanliness issues in the lamination department (utilities 2), admin block DB, Production Building 3, head office main panel, and the Knitting Building. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | DBs & Elec Protection Systems | Lint & dust inside panel board | This relates to the entire facility. During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. The issue was noted at multiple locations, including lint and dust accumulation inside cable trays in the cutting hall (ground floor) and Packing 2 (Production Building B2, ground floor), as well as general cleanliness issues in the Lamination Department (Utilities 2), Admin Block DB, Production Building 3, Head Office main panel, and the Knitting Building. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E29 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system was provided, however, there was no study available to confirm its adequacy. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system was provided, however, there was no study available to confirm its adequacy. | If the risk assessment concludes that an LPS is necessary then hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standards such as BS EN 62305 (Protection against Lightning). | E31 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. The factory has installed an independent or conventional fire panel for its facility. The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and manual call point coverage, faulty or non-functional detectors, use of non-fire rated cables, low audibility in various areas, and overall non-compliance with NFPA 72 standards. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 2 weeks | 2025-10-30 | 2025-11-13 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. The factory has installed an independent or conventional fire panel for its facility. The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and manual call point coverage, faulty or non-functional detectors, use of non-fire rated cables, low audibility in various areas, and overall non-compliance with NFPA 72 standards. | i. Submit design documentation for new FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. The factory has installed an independent or conventional fire panel for its facility. The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and manual call point coverage, faulty or non-functional detectors, use of non-fire rated cables, low audibility in various areas, and overall non-compliance with NFPA 72 standards. | ii. Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E37 + 1 months | 2026-08-30 | 2026-09-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. The factory has installed an independent or conventional fire panel for its facility. The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and manual call point coverage, faulty or non-functional detectors, use of non-fire rated cables, low audibility in various areas, and overall non-compliance with NFPA 72 standards. | iii. Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E38 + 4 months | 2026-07-30 | 2026-11-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. The factory has installed an independent or conventional fire panel for its facility. The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and manual call point coverage, faulty or non-functional detectors, use of non-fire rated cables, low audibility in various areas, and overall non-compliance with NFPA 72 standards. | iv. Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E39 + 5 months | 2026-03-30 | 2026-08-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. The factory has installed an independent or conventional fire panel for its facility. The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and manual call point coverage, faulty or non-functional detectors, use of non-fire rated cables, low audibility in various areas, and overall non-compliance with NFPA 72 standards. | v. Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E40 + 3 months | 2026-04-30 | 2026-07-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. The factory has installed an independent or conventional fire panel for its facility. The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and manual call point coverage, faulty or non-functional detectors, use of non-fire rated cables, low audibility in various areas, and overall non-compliance with NFPA 72 standards. | vi. Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E41 + 3 months | 2025-12-30 | 2026-03-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Fire Alarm & Detection System (FADS) | Maintenance records | This section refers to the entire facility. During the inspection, the testing and maintenance records for the FADS were reviewed. The following observations were made with regards to testing and maintenance: i. Routine testing of the Fire Alarm and Detection System (FADS) has not been performed consistently. ii. The testing and maintenance of the Fire Alarm and Detection System (FADS) have not been conducted in accordance with the requirements specified in Chapter 14 of NFPA 72. | Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | 6 months | 2025-10-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | i. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer areas. | i. Redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the generator and transformer receive adequate ventilation. This might involve repositioning vents or adding ductwork. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | ii. Several sections of the room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | ii. Add more lighting fixtures in poorly lit areas to ensure even distribution of light throughout the room. Focus on areas that require the highest visibility, such as around equipment and control panels. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | This sections refers to the electrical switch rooms and generator room. An assessment of the existing ventilation system was conducted, alongside an evaluation of the lighting setup in various parts of the room, to determine their compliance with recommended standards. The following observations were made: i. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer areas. ii. Several sections of the room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | Establish regular maintenance and testing of the ventilation system and luminaires within the spaces to ensure adequate performance. | E41 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Generator, Transformer & Sub-Station Room | Working clearance | This sections refers to the electrical switch rooms and Generator Room. During our inspection an the working clearances surrounding key electrical equipment was assessed. During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. The issue was noted at in Generator and LT Rooms in Utility 2, Building 10, Solar Inverter Room and Head Office Building, Electrical Room. | Reorganize the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | Generator, Transformer & Sub-Station Room | Working clearance | This sections refers to the electrical switch rooms and Generator Room. During our inspection an the working clearances surrounding key electrical equipment was assessed. During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. The issue was noted at in Generator and LT Rooms in Utility 2, Building 10, Solar Inverter Room and Head Office Building, Electrical Room. | Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. | E44 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Generator, Transformer & Sub-Station Room | Room separation | During the inspection of the generator, and substation rooms, the physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. It was observed that the separation between the generator, and LT panels was inadequate. The barriers between these sections were either non-existent or insufficient, with gaps and openings that could facilitate the spread of fire or electrical faults from one area to another. | Install temporary fire-resistant barriers and seal any gaps and openings between the generator, and LT panel areas to immediately reduce the risk of fire and electrical fault propagation. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Generator, Transformer & Sub-Station Room | Room separation | During the inspection of the generator, and substation rooms, the physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. It was observed that the separation between the generator, and LT panels was inadequate. The barriers between these sections were either non-existent or insufficient, with gaps and openings that could facilitate the spread of fire or electrical faults from one area to another. | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. | E46 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Cabling & Wiring | Cables support and protection | This section refers to the entire facility. During the inspection of the entire facility, a visual survey of the cable containment system was conducted. Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. The issue was noted at waste area, Solar Inverter Room, Mezzanine floor, Building 10, Utilities 2. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Cabling & Wiring | Cables support and protection | This section refers to the entire facility. During the inspection of the entire facility, a visual survey of the cable containment system was conducted. Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. The issue was noted at waste area, solar inverter room mezzanine floor Building 10 Utilities 2. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | E48 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Cabling & Wiring | Cable trench and channel cleanliness | This related to the whole facility. During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. The issue was noted at generator area LT Room Utilities 2. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Cabling & Wiring | Cable trench and channel cleanliness | This related to the whole facility. During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. The issue was noted at generator area LT Room Utilities 2. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | E50 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Cabling & Wiring | Splicing of cables | i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at multiple locations in the facility, especially in the Power house Production Buildings 1, 2 and 3, Utilities 2, Head Office and Admin Block. | i. install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Cabling & Wiring | Splicing of cables | ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at cutting hall ground floor and the Production Building Packing 2 ground floor. | ii. Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Cabling & Wiring | Splicing of cables | iii. PVC connectors were used, which may pose a potential short circuit hazard due to poor insulation and lack of mechanical strength. The issue was noted at cutting hall cable tray. | iii. Replace PVC connectors in critical areas with proper insulated lugs or terminals to eliminate immediate short circuit risks. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Cabling & Wiring | Splicing of cables | i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at multiple locations in the facility, specially Power house Production Buildings 1, 2 and 3, Utilities 2, Head Office and Admin Block. | i. Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | E52 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Cabling & Wiring | Splicing of cables | ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at cutting hall ground floor and Production Building Packing 2 ground floor. | ii. Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | E53 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Cabling & Wiring | Splicing of cables | iii. PVC connectors were used, which may pose a potential short circuit hazard due to poor insulation and lack of mechanical strength. The issue was noted at cutting hall cable tray. | iii. Ensure complete replacement of all PVC connectors with compliant terminations as per BS 7671 / NFPA 70 and train staff on approved practices. | E54 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Cabling & Wiring | Colour coding | This relates to the whole facility. During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. The issue was noted at Production Building 1 and Admin Block 2. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Colour coding | This relates to the whole facility. During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. The issue was noted at Production Building 1 and Admin Block 2. | Develop and enforce a strict protocol for cable colour coding to be followed in all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | E58 + 4 months | 2025-12-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 370 | 421 | 6 | 5 |  | Initial | [11 empty] | E60 | Cabling & Wiring | Fixtures | This relates to the whole facility. During the inspection, the electrical fixtures throughout the facility were visually surveyed. Broken and exposed power receptacles and switchboards: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. The issue was noted at lamination department, kitchen Canteen ground floor Utility 2, Maintenance Workshop and Electrical Room Head Office Building. | Replace or repair broken and exposed power receptacles and switchboards immediately to restore safe and secure connections. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 371 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Fixtures | This relates to the whole facility. During the inspection, the electrical fixtures throughout the facility were visually surveyed. Broken and exposed power receptacles and switchboards: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. The issue was noted at lamination department, kitchen Canteen ground floor Utility 2, Maintenance Workshop and Electrical Room Head Office Building. | Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
2025-05-20
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Maheen Textile Mills (Pvt.) Ltd. - 28 Km Sheikhupura Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2025-05-20
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-09-04 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | Escape doors are lockable/locked at Production 2 (ground floor), Head Offices (all floors). - Sliding & lockable doors serve for escape from areas with more than 10 occupants at stair S6 discharge, Utilities (ground floor) , Production 1. (ground floor) and Production 4 (ground floor). | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-10-30 | 2025-11-13 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | Escape doors are lockable/locked at Production 2 (ground floor), Head Offices (all floors). - Sliding & lockable doors serve for escape from areas with more than 10 occupants at stair S6 discharge, Utilities (ground floor), Production 1 (ground floor) and Production 4 (ground floor). | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | Escape doors are lockable/locked at Production 2 (ground floor), Head Offices (all floors). - Sliding & lockable doors serve for escape from areas with more than 10 occupants at stair S6 discharge, Utilities (ground floor), Production 1 (ground floor) and Production 4 (ground floor). | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | Obstructions on escape route at Production 2(roof), Utilities (ground floor & roof), store of Production 4 (ground floor). - Protected stair S1, S5, S6, S9, S12 and S14, discharges inside the building at a distance from building exit. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) at S14 (1st floor) found 1.89m. | Remove obstructions on escape routes and keep them clear for escape. Provide warning signs where headroom height is less than 2.05 m on escape routes. | 2 weeks | 2025-10-30 | 2025-11-13 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | Obstructions on escape route at Production 2(roof), Utilities (ground floor & roof), store of Production 4 (ground floor). - Protected stair S1, S5, S6, S9, S12 and S14, discharges inside the building at a distance from building exit. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) at S14 (1st floor) found 1.89m. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Exit access | Obstructions on escape route at Production 2(roof), Utilities (ground floor & roof), store of Production 4 (ground floor). - Protected stair S1, S5, S6, S9, S12 and S14, discharges inside the building at a distance from building exit. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) at S14 (1st floor) found 1.89m. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. Implement measures to ensure adequate clear head height is achieved along all escape routes. | F6 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits at Head Office (ground floor) found 36 m, Production 2 (ground floor) found 35 m & 25m. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits at Head Office (ground floor) found 36 m, Production 2 (ground floor) found 35 m & 25m. | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | F8+ 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Number of exits | Single exit from occupied floor at Head Office (2nd floor). - There are areas with over 50 occupants that are served by only 1 exit at Head Office (ground floor ). | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Number of exits | Single exit from occupied floor at Head Office (2nd floor). - There are areas with over 50 occupants that are served by only 1 exit at Head Office (ground floor ). | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Standard. | F10 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Protection of stairs | Unprotected openings (windows/ open to production floor) into stairs at S3 (1st & 2nd floor), S1, S6 , S7 & S12 (all floors), S8, S9 , S13 & S14 (1st floor). - Doors not fire doors at S3 (1st & 2nd floor). - Fire load in/under stairs at S1(ground & 1st floor) , at S9, S13 & S14 (ground floor). - Services passing through or within stairs at S13 (1st floor). | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | 2025-10-30 | 2025-11-13 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Protection of stairs | Unprotected openings (windows/ open to production floor) into stairs at S3 (1st & 2nd floor), S1, S6 , S7 & S12 (all floors), S8, S9 , S13 & S14 (1st floor). - Doors not fire doors at S3 (1st & 2nd floor). - Fire load in/under stairs at S1(ground & 1st floor) , at S9, S13 & S14 (ground floor). - Services passing through or within stairs at S13 (1st floor). | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers. door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Protection of stairs | Unprotected openings (windows/ open to production floor) into stairs at S3 (1st & 2nd floor), S1, S6 , S7 & S12 (all floors), S8, S9 , S13 & S14 (1st floor). - Doors not fire doors at S3 (1st & 2nd floor). - Fire load in/under stairs at S1(ground & 1st floor) , at S9, S13 & S14 (ground floor). - Services passing through or within stairs at S13 (1st floor). | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F13 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Escape stair condition | Obstacles (obstructed with door) in stairs at S3 (2nd floor) & S8 (1st floor). - Stair width is less than minimum stair width at S15 (found 0.63 m). - Stair S9 is not structurally safe connecting 2nd floor to roof. | Remove all obstructions from stairs. | 2 weeks | 2025-10-30 | 2025-11-13 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Escape stair condition | Obstacles (obstructed with door) in stairs at S3 (2nd floor) & S8 (1st floor). - Stair width is less than minimum stair width at S15 (found 0.63 m). - Stair S9 is not structurally safe connecting 2nd floor to roof. | Ensure the following are provided: - Stair structure (width) to be fixed so that stairs are safe for escape. - Fire Inspection. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Means of Escape | Exit discharge | Stair discharge route of S7 not fire separated from the rest of the building at Utilities (ground floor). | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes Provide additional exits from site. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Means of Escape | Exit discharge | Stair discharge route of S7 not fire separated from the rest of the building at Utilities (ground floor). | Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high risk areas. | F17 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs at all over the facility. - Missing exit signs at stair discharge routes at all over the facility. - Missing exit signs in production areas at all over the facility. - Missing exit signs at roof at all over the facility. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs at all over the facility. - Missing exit signs at stair discharge routes at all over the facility. - Missing exit signs in production areas at all over the facility. - Missing exit signs at roof at all over the facility. | Ensure that all exit signage is checked periodically and in good working condition. | F19 + 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Separation of high-risk areas | Steam generators are not enclosed in minimum 3m high sturdy construction to separate them from occupied areas at Production 2 (ground & 1st floor). - Steam generator door is not a sturdy door at Production 2 (ground & 1st floor) | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Separation to electric steam generator up to 3 m above the finished floor level. This should be achieved using reinforced concrete / masonry walls with a solid steel doors. - The door must have a self-closer and a positive latch. - Blast vent should be provided to outside the building. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Separation of high-risk areas | Steam generators are not enclosed in minimum 3m high sturdy construction to separate them from occupied areas at Production 2 (ground & 1st floor). - Steam generator door is not a sturdy door at Production 2 (ground & 1st floor). | Implement the above plan on site. All buildings to be compliant with Pakistan Accord Standard. | F21 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Separation of high-risk areas | Electrical room & Solar inverter rooms are not fire separated at Utilities (ground floor & mezzanine floor). - Generator room is not fire separated at Utilities (ground floor). - Mechanical plant areas are not fire separated at Utilities (ground floor). | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Separation of high-risk areas | Electrical room & Solar inverter rooms are not fire separated at Utilities (ground floor & mezzanine floor). - Generator room is not fire separated at Utilities (ground floor). - Mechanical plant areas are not fire separated at Utilities (ground floor). | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F23 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction at all floors of Production 2 , Utilities, Head Office (lift shaft closed with wooden sheets) and Production 4. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction at all floors of Production 2 , Utilities, Head Office (lift shaft closed with wooden sheets) and Production 4. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F25 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Separation of occupancies | Locking devices on doors do not allow for free escape under all circumstances at Utilities (2nd floor). - No adequate automatic fire detection and alarm system at Utilities (2nd floor). - Above ground levels lack an alternative escape route at Utilities (2nd floor). - Cooking facilities and/or kitchens not adequately fire separated at Utilities (2nd floor). - Lack of fire rated separation between the dormitory and other occupancy types at Utilities (2nd floor). | The dormitory is not to be used until minimum requirements for sleeping occupancies have been provided. Alternative arrangements must be sought immediately for the dormitory as continuing the use of the building for this purpose is not appropriate. Dormitory not to be re-occupied until the minimum requirements have been implemented. | 2 weeks | 2025-10-30 | 2025-11-13 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Rated Construction | Separation of occupancies | Locking devices on doors do not allow for free escape under all circumstances at Utilities (2nd floor). - No adequate automatic fire detection and alarm system at Utilities (2nd floor). - Above ground levels lack an alternative escape route at Utilities (2nd floor). - Cooking facilities and/or kitchens not adequately fire separated at Utilities (2nd floor). - Lack of fire rated separation between the dormitory and other occupancy types at Utilities (2nd floor). | Document proposals for design of remedial measures to ensure compliance with all fire safety requirements for sleeping occupancies to comply with Pakistan Accord Standard. Submit proposals to Pakistan Accord for review. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Rated Construction | Separation of occupancies | Locking devices on doors do not allow for free escape under all circumstances at Utilities (2nd floor). - No adequate automatic fire detection and alarm system at Utilities (2nd floor). - Above ground levels lack an alternative escape route at Utilities (2nd floor). - Cooking facilities and/or kitchens not adequately fire separated at Utilities (2nd floor). - Lack of fire rated separation between the dormitory and other occupancy types at Utilities (2nd floor). | Implement remediation measures to ensure full compliance with dormitory requirements of Pakistan Accord Standard and Pakistan Building Code in accordance with previously reviewed design. | F28 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building at Production 2 (ground floor), Production 1 (ground floor), Online store at Utilities (ground floor), record room & samples stores at Head Office (ground & 1st floor) and accessories store & waste store at Production 4. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) at Production 1. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building at Production 2 (ground floor), Production 1 (ground floor), Online store at Utilities (ground floor), record room & samples stores at Head Office (ground & 1st floor) and accessories store & waste store at Production 4. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) at Production 1. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F30+ 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Fire extinguishers | Poor condition of fire extinguishers (broken seals found on site) at multiple location over the facility. | Ensure that all building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Suppression | Fire extinguishers | Poor condition of fire extinguishers (broken seals found on site) at multiple location over the facility. | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Hazardous Materials | Diesel storage | Diesel storage is not separated from rest of the building at Utilities. - Inadequate bunding below diesel storage tank at Utilities. | Prepare drawings showing the proposed diesel storage arrangements to comply with NFPA 30. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of the proposed diesel storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. - Bunding details. | 4 months | 2025-10-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Hazardous Materials | Diesel storage | Diesel storage is not separated from rest of the building at Utilities. - Inadequate bunding below diesel storage tank at Utilities. | Implement the above plan on site. All diesel storage areas to be compliant with Pakistan Accord Standard. | F34 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Safety Management | Fire drills | No regular fire drills. | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Safety Management | Fire drills | No regular fire drills. | Ensure fire drills are performed a minimum 2 times per year. | F36 + 2 months | 2025-12-30 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Extinguishers. | Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Extinguishers. | Ensure all systems are being tested as per the schedule agreed with Pakistan Accord. - Keep testing records. | F38+ 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Extinguishers. | Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Extinguishers. | Ensure all systems are being maintained as per the schedule agreed with Pakistan Accord. - Keep maintenance records. | F40 + 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Fire Safety Management | Emergency Action Plan | - There was an EAP document but it does not details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-10-30 | 2025-12-30 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Fire Safety Management | Emergency Action Plan | - There was an EAP document but it does not details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F42+ 2 months | 2025-12-30 | 2026-02-28 | AGREE |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
2025-05-20
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Maheen Textile Mills (Pvt.) Ltd. - 28 Km Sheikhupura Road, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2025-05-20
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-09-04 | 2025-10-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Other Damage/Defects | Corrosion of reinforcement | In Production 4, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Identify the cause of the damage and propose measures to prevent further water damage. | 1 month | 2025-10-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Other Damage/Defects | Corrosion of reinforcement | In Production 4, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Inspect damage to the columns and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Other Damage/Defects | Corrosion of reinforcement | In Production 4, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Implement work. | S3 + 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Other Damage/Defects | Corrosion of reinforcement | In Production 4, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Continue to monitor for future signs of water ingress/damage. | S4 + 3 months | 2026-04-30 | 2026-07-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Other Damage/Defects | Corrosion of reinforcement | In Head Office, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Identify the cause of the damage and propose measures to prevent further water damage. | 1 month | 2025-10-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Other Damage/Defects | Corrosion of reinforcement | In Head Office, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Inspect damage to the columns and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Other Damage/Defects | Corrosion of reinforcement | In Head Office, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Implement work. | S7 + 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Other Damage/Defects | Corrosion of reinforcement | In Head Office, exposed and corroded rebars were observed at the roof, posing a significant risk of further deterioration due to prolonged exposure to weathering. If left unaddressed, this corrosion is likely to propagate, potentially compromising the structural integrity of other parts of the building over time. | Continue to monitor for future signs of water ingress/damage. | S8 + 3 months | 2026-04-30 | 2026-07-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Other Damage/Defects | Column impact damage | This relates to Utilities 2 Building with RC MRF slab at ground floor. Impact damage was observed in a few internal RC columns , which will impact the load bearing capacity of the columns if remain unprotected. | Repair damage to column corners and external faces. | 1 month | 2025-10-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Other Damage/Defects | Column impact damage | This relates to Utilities 2 Building with RC MRF slab at ground floor. Impact damage was observed in a few internal RC columns , which will impact the load bearing capacity of the columns if remain unprotected. | Install protective measures to prevent damage recurring. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Other Damage/Defects | Column impact damage | This relates to Utilities 2 Building with RC MRF slab at ground floor. Impact damage was observed in a few internal RC columns , which will impact the load bearing capacity of the columns if remain unprotected. | Continue to monitor condition of columns in highly trafficked areas. | S11 + 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Other Damage/Defects | Column impact damage | This relates to Production 1 Building at ground floor. Impact damage was observed in a few internal RC columns , which will impact the load bearing capacity of the columns if remain unprotected. | Repair damage to column corners and external faces. | 1 month | 2025-10-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Other Damage/Defects | Column impact damage | This relates to Production 1 Building at ground floor. Impact damage was observed in a few internal RC columns , which will impact the load bearing capacity of the columns if remain unprotected. | Install protective measures to prevent damage recurring. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Other Damage/Defects | Column impact damage | This relates to Production 1 Building at ground floor. Impact damage was observed in a few internal RC columns , which will impact the load bearing capacity of the columns if remain unprotected. | Continue to monitor condition of columns in highly trafficked areas. | S14 + 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Other Damage/Defects | Moisture ingress | In Building Utilities 1, signs of moisture ingress were observed in the canteen area on the 1st floor slab. The dampness appears to have initiated concrete spalling in the slab, indicating potential deterioration of the structural element if not addressed promptly. | Identify the cause of the damage / source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-10-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Other Damage/Defects | Moisture ingress | In Building Utilities 1, signs of moisture ingress were observed in the canteen area on the 1st floor slab. The dampness appears to have initiated concrete spalling in the slab, indicating potential deterioration of the structural element if not addressed promptly. | Inspect damage to the slab and propose repairs to structure. Submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Other Damage/Defects | Moisture ingress | In Building Utilities 1, signs of moisture ingress were observed in the canteen area on the 1st floor slab. The dampness appears to have initiated concrete spalling in the slab, indicating potential deterioration of the structural element if not addressed promptly. | Implement work. | S17 + 3 months | 2026-01-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Other Damage/Defects | Moisture ingress | In Building Utilities 1, signs of moisture ingress were observed in the canteen area on the 1st floor slab. The dampness appears to have initiated concrete spalling in the slab, indicating potential deterioration of the structural element if not addressed promptly. | Continue to monitor for future signs of water ingress/damage. | S18 + 3 months | 2026-04-30 | 2026-07-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Other Damage/Defects | Health and Safety | This concerns inadequate edge protection on buildings Admin Block 1, Utilities 1, Utilities 2, Production 1, Production 2, Production 3, Production 4, Head Office's roof where no edge protection was provided at the end of the roof where solar panels are installed on these buildings as well. Furthermore, The provide edge protection at stairs in all building is observed to be inadequate as the provided height is not what is required. i.e. 1032 mm. This creates a risk of injury resulting from trip or fall – Health & Safety concern. | Provide adequate edge protection on the roofs and stairs of all these buildings, and on any other part of the factory with the same issue. | 1 month | 2025-10-30 | 2025-11-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Structural Documentation | Documentation unavailable | The structural drawings for all buildings were unavailable and need to be prepared. The only existing document was a master layout, structural drawings of Head office buildings (original part before expansion) which differs from as-builts at few extents such as shape of columns, and structural framing plan of Admin Block 1 building. Additionally, soil report was also not available for the factory. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation | 6 months | 2025-10-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Structural Documentation | Non-engineered structure | In Building Production 4, a portion of the structure comprises of steel sheets supported by a steel truss system. This portion appears to be non-engineered possessing undersized members, lacking evidence of proper structural design or approval. Additionally, no documentation or structural drawings were available for this shed at the time of inspection. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Structural Documentation | Non-engineered structure | In Building Production 4, a portion of the structure comprises of steel sheets supported by a steel truss system. This portion appears to be non-engineered possessing undersized members, lacking evidence of proper structural design or approval. Additionally, no documentation or structural drawings were available for this shed at the time of inspection. | Propose strengthening work as required and submit to Pakistan Accord for approval. | S22 + 1 month | 2026-01-30 | 2026-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Structural Documentation | Non-engineered structure | In Building Production 4, a portion of the structure comprises of steel sheets supported by a steel truss system. This portion appears to be non-engineered possessing undersized members, lacking evidence of proper structural design or approval. Additionally, no documentation or structural drawings were available for this shed at the time of inspection. | Implement strengthening work as required. | S23 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Structural Documentation | Non-engineered structure | In Building Production 2, a part of the structure comprises steel sheets supported by a steel truss system. This portion appears to be non-engineered, lacking evidence of proper structural design. Additionally, no documentation or structural drawings were available for this shed at the time of inspection. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 3 months | 2025-10-30 | 2026-01-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S26 | Structural Documentation | Non-engineered structure | In Building Production 2, a part of the structure comprises steel sheets supported by a steel truss system. This portion appears to be non-engineered, lacking evidence of proper structural design. Additionally, no documentation or structural drawings were available for this shed at the time of inspection. | Propose strengthening work as required and submit to Pakistan Accord for approval. | S25 + 1 month | 2026-01-30 | 2026-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S27 | Structural Documentation | Non-engineered structure | In Building Production 2, a part of the structure comprises steel sheets supported by a steel truss system. This portion appears to be non-engineered, lacking evidence of proper structural design. Additionally, no documentation or structural drawings were available for this shed at the time of inspection. | Implement strengthening work as required. | S26 + 4 months | 2026-02-28 | 2026-06-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S28 | Structural Documentation | Lack of safe load plans | Safe load plans were not available and posted in any of the building in the factory. | Building structural engineer to review design documentation to confirm load capacity of the structure. Develop safe load plans and submit to Pakistan Accord for review. | 6 months | 2025-10-30 | 2026-04-30 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S29 | Structural Documentation | Lack of safe load plans | Safe load plans were not available and posted in any of the building in the factory. | Factory to post safe load plans on each floor. | S28 + 1 month | 2026-04-30 | 2026-05-30 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixtures
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1