## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
2025-04-28
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | MK Sons (Pvt.) Ltd. - 2 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2025-04-28
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-09-03 | 2025-10-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no sub-station room layout drawings available for the factory. There were no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no sub-station room layout drawings available for the factory. There were no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2 + 3 months | 2025-11-29 | 2026-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but were incomplete, mismatches with on-site installations, not provided for the whole facility and missing necessary technical details like busbar/cable size, breaker size, breaker short circuit current rating, connected load and mechanical interlocking scheme. | Update and develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but were incomplete, mismatches with on-site installations, not provided for the whole facility and missing necessary technical details like busbar/cable size, breaker size, breaker short circuit current rating, connected load and mechanical interlocking scheme. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4 + 3 months | 2025-12-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-10-29 | 2026-04-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6 + 3 months | 2026-04-29 | 2026-07-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. Specifically, some circuit breakers had higher ratings than the cables could safely handle, which poses a significant risk of overheating and potential fire hazards. Conversely, other circuit breakers had lower ratings than necessary, resulting in frequent and unnecessary tripping. To ensure both safety and operational efficiency, corrective action is required to align the circuit breaker ratings with the cable capacities. This adjustment will mitigate the risks associated with overheating and improve the reliability of the electrical system. This issue was observed at main LT panel sub-station room Processing Building, folding areaProcessing Building, first floor Stitching Building and AC Plant panel room Weaving Building. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. Some example of these hotspots are mentioned in below: - Hotspot of 134°C found in distribution board at control room of Boiler House. - Hotspot of 121°C found in PFI panel at sub-station room Processing Building. - Hotspot of 106°C found in panel at control room of Boiler House. - Hotspot of 96.6°C found in distribution board at ETP. - Hotspot of 94.7°C found on cable connector at folding area Processing Building. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. Some example of these hotspots are mentioned in below: - Hotspot of 134°C found in distribution board at control room of Boiler House. - Hotspot of 121°C found in PFI panel at sub-station room Processing Building. - Hotspot of 106°C found in panel at control room of Boiler House. - Hotspot of 96.6°C found in distribution board at ETP. - Hotspot of 94.7°C found on cable connector at folding area Processing Building. | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | During the inspection, it was also found that the factory does not have any thermographic survey report available for electrical panels and components. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. It is recommended to perform thermographic surveys of electrical panels and distribution boards after every 6 months. | E10 + 5 months | 2025-11-29 | 2026-04-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations such as generator hall Powerhouse, machine panels Processing Building, first & second floor Stitching Building and ETP area . Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. | Design and evaluate the earthing system installation throughout the facility. Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | It was noted that the earthing cables and neutral cables were connected on the same busbar, indicating improper grounding practices. This was observed specifically at printing hall first floor Processing Building and Greige Godown. | Separate earthing cables from neutral cables that are on the same busbar and use dedicated busbars for earthing cables within the distribution boards and ensure proper separation and connection. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | Equipotential bonding for the cable trays and metallic panel covers was missing. This was observed at Powerhouse, Processing Building, Stitching Building, Greige Godown, Office Building and ETP area. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | No proper earthing layouts & earth pits maintenance records were available on site. | Provide earthing layouts and maintain earth pit maintenance records on-site. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. The earthing system was absent in multiple locations such as generator hall Powerhouse, machine panels Processing Building, first & second floor Stitching Building and ETP area . Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. ii. It was noted that the earthing cables and neutral cables were connected on the same busbar, indicating improper grounding practices. This was observed specifically at printing hall first floor Processing Building and Greige Godown. iii. Equipotential bonding for the cable trays and metallic panel covers was missing. This was observed at Powerhouse, Processing Building, Stitching Building, Greige Godown, Office Building and ETP Area. iv. No proper earthing layouts & earth pits maintenance records were available on site. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E15 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed outside Processing Building. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. This was specifically observed at the backside of Weaving Building. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | There were visible signs of damage to panels and cables. This issue was observed at sub-station room Processing Building and sizing hall Weaving Building. | Inspect and repair or replace all damaged panels, cables, and busbars to ensure the integrity of the electrical system in accordance with Section 522 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | In some panels, electrical components were hanging freely & fixed without any proper support. This was observed at Powerhouse, Processing Building, AC Plant Panel Room,Weaving Building, and IT Server Room Office Building. | Inspect and fix all panels with improperly fixed & hanging components to ensure the integrity of the electrical system. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | A few panels were found to have prayer mats, cardboards and instruction manuals placed inside them. The presence of flammable materials such as prayer mats and cardboard within electrical panels poses a fire and safety hazard. This was specifically observed at IT Server Room Office Building, sizing hall Weaving Building and dyeing machine panel at Processing Building. | Remove prayer mats, cardboards, instruction manuals and any flammable material from panels and distribution boards. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Panel/cabling/busbar | The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This issue was specifically observed outside Processing Building. ii. Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. This was specifically observed at the backside of Weaving Building. iii. There were visible signs of damage to panels and cables. This issue was observed at sub-station room Processing Building and sizing hall Weaving Building., iv. In some panels, electrical components were hanging freely & fixed without any proper support. This was observed at Powerhouse, Processing Building, AC plant panel room, Weaving Building,and IT Server Room Office Building. v. A few panels were found to have prayer mats, cardboards and instruction manuals placed inside them. The presence of flammable materials such as prayer mats and cardboard within electrical panels poses a fire and safety hazard. This was specifically observed at IT Server Room Office Building, sizing hall Weaving Building and dyeing machine panel at Processing Building. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E18 + 3 months | 2025-12-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Loop Connection | In these loop connections, one circuit breaker is energized by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. This was observed at control room Boiler House, LT panel Processing Building, folding hall Processing Building and at pasting panel Processing Building. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilized to provide each circuit with the required live, neutral, and earth connections. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed in a number of electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. This was observed at dyeing panel Processing Building, first floor Stitching Building, Greige Godown and sizing hall Weaving Building. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Openings | Unsealed openings were discovered in the panels and distribution boards. This was observed at control room Boiler House, sub-station room Processing Building, Stitching Building and AC plant panel room Weaving Building. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Openings | Unsealed openings were discovered in the panels and distribution boards. This was observed at control room Boiler House, sub-station room Processing Building, Stitching Building and AC plant panel room Weaving Building. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | E25 + 2 months | 2025-12-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Adequate accessibility | At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. This was observed at cable cellar Powerhouse, dyeing area Processing Building, printing area Processing Building and sizing hall Weaving Building. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This was observed at Boiler House panels, Powerhouse, Processing Building and ETP area panels. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This was observed at Boiler House panels, Powerhouse, Processing Building and ETP area panels. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E28 + 3 months | 2025-11-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system was provided, however, there was no study available to confirm its adequacy. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment.Also, adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards as per BS EN 62305. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system was provided, however, there was no study available to confirm its adequacy. | If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard as per BS EN 62305. | E30 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were conventional panels installed inside the facility in Processing Building, Stitching Building, Greige Godown, Weaving Building, Main Store and Office Building. The conventional Fire Alarm and Detection System was non-listed and exhibited several deficiencies, including inadequate detection and manual call point (MCP) coverage, incorrectly installed detectors and manual call points (MCP), non-fire rated cables, low audibility in various areas, inadequate visual coverage, no internal battery backup, faulty sounders, no layout drawings and overall non-compliance with NFPA 72 standards. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were conventional panels installed inside the facility in Processing Building, Stitching Building, Greige Godown, Weaving Building, Main Store and Office Building. The conventional Fire Alarm and Detection System was non-listed and exhibited several deficiencies, including inadequate detection and manual call point (MCP) coverage, incorrectly installed detectors and manual call points (MCP), non-fire rated cables, low audibility in various areas, inadequate visual coverage, no internal battery backup, faulty sounders, no layout drawings and overall non-compliance with NFPA 72 standards. | (1) Submit design documentation for new replacement of FADS to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | E32 + 3 months | 2025-11-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were conventional panels installed inside the facility in Processing Building, Stitching Building, Greige Godown, Weaving Building, Main Store and Office Building. The conventional Fire Alarm and Detection System was non-listed and exhibited several deficiencies, including inadequate detection and manual call point (MCP) coverage, incorrectly installed detectors and manual call points (MCP), non-fire rated cables, low audibility in various areas, inadequate visual coverage, no internal battery backup, faulty sounders, no layout drawings and overall non-compliance with NFPA 72 standards. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for the import of any components required for the FADS design submitted earlier. | E33 + 1 month | 2026-02-28 | 2026-03-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were conventional panels installed inside the facility in Processing Building, Stitching Building, Greige Godown, Weaving Building, Main Store and Office Building. The conventional Fire Alarm and Detection System was non-listed and exhibited several deficiencies, including inadequate detection and manual call point (MCP) coverage, incorrectly installed detectors and manual call points (MCP), non-fire rated cables, low audibility in various areas, inadequate visual coverage, no internal battery backup, faulty sounders, no layout drawings and overall non-compliance with NFPA 72 standards. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E34 + 4 months | 2026-03-28 | 2026-07-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were conventional panels installed inside the facility in Processing Building, Stitching Building, Greige Godown, Weaving Building, Main Store and Office Building. The conventional Fire Alarm and Detection System was non-listed and exhibited several deficiencies, including inadequate detection and manual call point (MCP) coverage, incorrectly installed detectors and manual call points (MCP), non-fire rated cables, low audibility in various areas, inadequate visual coverage, no internal battery backup, faulty sounders, no layout drawings and overall non-compliance with NFPA 72 standards. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E35 + 5 months | 2026-07-28 | 2026-12-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were conventional panels installed inside the facility in Processing Building, Stitching Building, Greige Godown, Weaving Building, Main Store and Office Building. The conventional Fire Alarm and Detection System was non-listed and exhibited several deficiencies, including inadequate detection and manual call point (MCP) coverage, incorrectly installed detectors and manual call points (MCP), non-fire rated cables, low audibility in various areas, inadequate visual coverage, no internal battery backup, faulty sounders, no layout drawings and overall non-compliance with NFPA 72 standards. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E36 + 3 months | 2026-12-28 | 2027-03-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were conventional panels installed inside the facility in Processing Building, Stitching Building, Greige Godown, Weaving Building, Main Store and Office Building. The conventional Fire Alarm and Detection System was non-listed and exhibited several deficiencies, including inadequate detection and manual call point (MCP) coverage, incorrectly installed detectors and manual call points (MCP), non-fire rated cables, low audibility in various areas, inadequate visual coverage, no internal battery backup, faulty sounders, no layout drawings and overall non-compliance with NFPA 72 standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and the Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E37 + 3 months | 2027-03-28 | 2027-06-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations. This issue was observed at control room Boiler House, raising section Processing Building, ground floor Stitching Building and Greige Godown. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations. This issue was observed at control room Boiler House, raising section Processing Building, ground floor Stitching Building and Greige Godown. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E39 + 3 months | 2025-11-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Emergency Lighting | Provided but insufficient | Several areas lacked sufficient emergency and directional exit lighting coverage: a) LT room Powerhouse b) Several areas of Processing Building. c) Several areas of Stitching Building. d) Greige Godown. e) Several areas of Weaving Building . f) Office Building. g) Waste Godown. | Conduct a comprehensive survey to identify areas lacking adequate emergency and directional exit lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. Submit emergency lighting layout to Pakistan Accord for review. | 4 months | 2025-10-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Emergency Lighting | Provided but insufficient | Multiple emergency luminaires indicated the need for maintenance. This was observed at generator hall Powerhouse and roof of Stitching Building. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Emergency Lighting | Provided but insufficient | Installed emergency lights were too dim to provide adequate illumination. This issue was observed at control room Powerhouse and Processing Building. | Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Emergency Lighting | Provided but insufficient | The backup power supply to the emergency luminaires is insufficient. | Upgrade the backup power supply to ensure it can adequately support all emergency luminaires during a power failure. This includes installing additional battery packs or generators as necessary to comply with the Building Code of Pakistan Fire Safety Provisions 2016. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | Emergency Lighting | Provided but insufficient | Several exit signs were non-illuminated and misleading. This issue was observed specifically at first floor Stitching Building, Greige Godown and Waste Godown. | Ensure all exit signs are properly illuminated and replace or reposition misleading exit signs to ensure clear and accurate egress guidance. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Emergency Lighting | Provided but insufficient | During the inspection the emergency lighting arrangement throughout the facility was assessed. The following observations were made: i. Several areas lacked sufficient emergency and directional exit lighting coverage: a) LT Room Power House. b) Several areas of Processing Building. c) Several areas of Stitching Building. d) Greige Godown. e) Several areas of Weaving Building. f) Office Building. g) Waste Godown. ii. Multiple emergency luminaires indicated the need for maintenance. This was observed at Generator Hall Powerhouse and roof of Stitching Building. iii. Installed emergency lights were too dim to provide adequate illumination. This issue was observed at control room Powerhouse and Processing Building. iv. The backup power supply to the emergency luminaires was insufficient. v. Several exit signs were non-illuminated and misleading. This issue was observed specifically at first floor Stitching Building, Greige Godown, and Waste Godown. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E41 + 3 months | 2026-02-28 | 2026-05-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E47 + 3 months | 2025-12-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | i. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the HT panel and transformer areas. ii. Several sections of the room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. This issue was specifically observed at the sub-station room in the Processing Building. | i. Hire a qualified engineer to reassess the ventilation system to ensure it meets safety and performance standards. If the assessment concludes that the current system is inadequate redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the HT panel and transformer receive adequate ventilation.This may involve repositioning vents or adding ductwork as necessary. Submit the ventilation assessment report and the proposed design to Pakistan Accord for review. ii. Add more lighting fixtures in poorly lit areas to ensure even distribution of light throughout the room. Focus on areas that require the highest visibility, such as around equipment and control panels. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | i. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the HT panel and transformer areas. ii. Several sections of the room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. This issue was specifically observed at the Sub-station Room in the Processing Building. | Establish regular maintenance and testing of the ventilation system and luminaires within the spaces to ensure adequate performance. | E49 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Generator, Transformer & Sub-Station Room | Working clearance | During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. This issue was specifically observed at Sub-station room in Processing Building and Transformer Room in the Weaving Building. | Reorganize the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Generator, Transformer & Sub-Station Room | Working clearance | During the inspection, it was observed that the working clearance was inadequate in multiple areas. Equipment was placed too close to walls or other machines, making it difficult for personnel to access for routine maintenance or emergency interventions. Additionally, some pathways were obstructed, restricting movement and potentially delaying response times during an emergency. This issue was specifically observed at Sub-station room in Processing Building and Transformer Room in the Weaving Building. | Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. | E51 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Generator, Transformer & Sub-Station Room | Room separation | It was observed that the separation between the transformer and LT panels was inadequate. The barriers between these sections were either non-existent or insufficient, with gaps and openings that could facilitate the spread of fire or electrical faults from one area to another. Additionally, some partitions were constructed from materials that did not meet fire resistance standards, posing a significant risk in the event of an incident. This was observed specifically in the transformer room in the Weaving Building. | Install temporary fire-resistant barriers and seal any gaps and openings between the transformer and HT panel to immediately reduce the risk of fire and electrical fault propagation. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Generator, Transformer & Sub-Station Room | Room separation | It was observed that the separation between the transformer and LT panels was inadequate. The barriers between these sections were either non-existent or insufficient, with gaps and openings that could facilitate the spread of fire or electrical faults from one area to another. Additionally, some partitions were constructed from materials that did not meet fire resistance standards, posing a significant risk in the event of an incident. This was observed specifically in the transformer room in the Weaving Building. | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. | E53 + 4 months | 2025-12-29 | 2026-04-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Generator, Transformer & Sub-Station Room | Battery | Noticeable spills of battery fluid were observed, which can lead to corrosion and pose a chemical hazard. This issues were specifically observed at generator hall Powerhouse and IT Server Room Office Building. | Clean any battery fluid spills using appropriate neutralizing agents and safety equipment to prevent corrosion and chemical hazards. Inspect and repair any affected battery cells or enclosures to prevent further leakage. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Generator, Transformer & Sub-Station Room | Battery | Noticeable spills of battery fluid were observed, which can lead to corrosion and pose a chemical hazard. This issues were specifically observed at generator hall Powerhouse and IT Server Room Office Building. | Implement a regular maintenance schedule to monitor and address potential leaks, ensuring that any spills are promptly managed. | E55 + 2 months | 2025-11-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 370 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Generator, Transformer & Sub-Station Room | Battery | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. This issues were specifically observed at generator hall Powerhouse and IT Server Room Office Building. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 371 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Generator, Transformer & Sub-Station Room | Battery | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. This issues were specifically observed at generator hall Powerhouse and IT Server Room Office Building. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | E57 + 2 months | 2025-11-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. This issue was observed at cable cellar Powerhouse, Boiler House, outside and on roof of Weaving Building, ETP area and outside Stitching Building. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E60 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. This issue was observed at cable cellar Powerhouse, Boiler House, outside and on roof of Weaving Building, ETP area and outside Stitching Building. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | E59 + 2 months | 2025-12-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Cables support and protection | Numerous loose connections were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections and the practice of inserting exposed wires directly into sockets to prevent electrical hazards. This issue was observed specifically at Boiler House. | Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E62 | Cabling & Wiring | Cables support and protection | Numerous loose connections were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections and the practice of inserting exposed wires directly into sockets to prevent electrical hazards. This issue was observed specifically at the Boiler House. | Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices. | E61 + 2 months | 2025-11-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E63 | Cabling & Wiring | Cables support and protection | Proper mechanical support was not provided for cable trays and it was found to be damaged. This issue was specifically observed outside the Griege Godown. | Provide adequate mechanical support and repair or replace the damaged cable trays to ensure safe installation. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E64 | Cabling & Wiring | Cables support and protection | Proper mechanical support was not provided for cable trays and it was found to be damaged. This issue was specifically observed outside the Griege Godown. | Establish and enforce a routine maintenance schedule for inspecting cable trays, ensuring prompt rectification of any damage or misalignment. | E63 + 2 months | 2025-11-29 | 2026-01-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 374 | 421 | 6 | 5 |  | Initial | [11 empty] | E65 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that: i. The cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was observed at theProcessing Building. ii. At some locations, cable trays were found to be rusted. This issue was observed outside the Greige Godown. | i. Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. ii. Replace or treat rusted cable trays with corrosion-resistant materials and apply protective coatings to prevent future deterioration. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 375 | 421 | 6 | 5 |  | Initial | [11 empty] | E66 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that: i. The cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was observed at theProcessing Building. ii. At some locations, cable trays were found to be rusted. This issue was observed outside the Greige Godown. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards.. | E65 + 2 months | 2025-12-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 376 | 421 | 6 | 5 |  | Initial | [11 empty] | E67 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was observed in the Stitching Building first and second floors and Processing Building. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 377 | 421 | 6 | 5 |  | Initial | [11 empty] | E68 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was observed in the Stitching Building first and second floors and Processing Building. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | E67 + 2 months | 2025-12-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 378 | 421 | 6 | 5 |  | Initial | [11 empty] | E69 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was observed in the Boiler House, Processing Building,, Stitching Building, and Office Building. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 379 | 421 | 6 | 5 |  | Initial | [11 empty] | E70 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was observed in the Boiler House, Processing Building,, Stitching Building, and Office Building. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | E69 + 2 months | 2025-12-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 378 | 421 | 6 | 5 |  | Initial | [11 empty] | E71 | Cabling & Wiring | Splicing of cables | PVC connectors used in distribution boards which could be hazard of potential short circuit due to its poor insulation. This issue was specifically observed ain the sub-station room of the Processing Building. | Replace the PVC connector with a secure, compliant electrical connection such as a terminal block. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 379 | 421 | 6 | 5 |  | Initial | [11 empty] | E72 | Cabling & Wiring | Splicing of cables | PVC connectors used in distribution boards which could be hazard of potential short circuit due to its poor insulation. This issue was specifically observed ain the sub-station room of the Processing Building. | Establish a plan to replace all PVC connectors with compliant electrical terminal blocks and integrate this into regular maintenance to ensure ongoing safety and compliance. | E71 + 2 months | 2025-12-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 380 | 421 | 6 | 5 |  | Initial | [11 empty] | E73 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was observed in the control room of the Boiler House and the folding area in the Processing Building. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 381 | 421 | 6 | 5 |  | Initial | [11 empty] | E74 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was observed in the control room of the Boiler House and the folding area in the Processing Building. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | E73 + 2 months | 2025-12-29 | 2026-02-28 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 382 | 421 | 6 | 5 |  | Initial | [11 empty] | E75 | Cabling & Wiring | Fixtures | During the inspection, the electrical fixtures throughout the facility were visually surveyed. The following observations were noted: i. Power receptacles installed in inappropriate locations: Receptacles placed in unsuitable locations, such as non-IP rated sockets installed outdoors or exposed to the elements, are at higher risk of moisture ingress and corrosion. This can lead to electrical short circuits or fires, posing a severe safety hazard. This issue was observed at Boiler House. ii. Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was observed at Powerhouse, Processing Building, and ETP Lab area. iii. Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. This issue was observed in the Boiler House and Processing Building. | i. Relocate power receptacles from inappropriate locations to more suitable, protected areas to prevent exposure to environmental elements. For external receptacles utilize suitably rated IP fixtures. ii. Replace combustible wooden ply backings with non-combustible materials to reduce fire risk. iii. Replace or repair broken and exposed power receptacles immediately to restore safe and secure connections. | 2 months | 2025-10-29 | 2025-12-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 383 | 421 | 6 | 5 |  | Initial | [11 empty] | E76 | Cabling & Wiring | Fixtures | During the inspection, the electrical fixtures throughout the facility were visually surveyed. The following observations were noted: i. Power receptacles installed in inappropriate locations: Receptacles placed in unsuitable locations, such as non-IP rated sockets installed outdoors or exposed to the elements, are at higher risk of moisture ingress and corrosion. This can lead to electrical short circuits or fires, posing a severe safety hazard. This issue was observed at Boiler House. ii. Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was observed at Powerhouse, Processing Building, and ETP Lab area. iii. Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. This issue was observed in the Boiler House and Processing Building. | i. Develop installation guidelines and training for personnel to ensure future power receptacles are installed in compliant and safe locations. ii. Establish a facility-wide standard to use only non-combustible materials for mounting electrical components, and conduct regular audits for compliance. iii. Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. | E75 + 3 months | 2025-12-29 | 2026-03-29 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 384 | 421 | 6 | 5
| 3 | 8 |  | 385 | 421 | 6 | 5
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
28-Apr-2025
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | MK Sons (Pvt.) Ltd. - 2 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 28-Apr-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-09-03 | 2025-10-29 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | Escape doors are lockable, the following examples were observed; - Ground floor in the Processing Building. - First floor Canteen areas in Processing Building. - Second Floor in the Processing Building. - Ground floor in the Stitching Building. - Exit gate from Second Floor in the Stitching Building. - Exit gate from Roof Level on the Stitching Building. - Exit door from ground floor in the Griege Building. - Exit doors from ground floor in the Weaving Building. - Exit door from Generator room in the Power House Building. - Frst floor of the Head Office Building. - Canteen Area in Head Office Building. Escape door does not allow for easy opening (e.g. ground floor exit from Store Building is stuck and difficult to open). Sliding doors serve for escape from areas with more than 10 occupants (ground floor Weaving Building). Doors into stairs swing against the direction of escape (e.g. Door into Stair 2 serving the Process Building roof). Escape door locked (e.g. first floor of the Head Office Building). | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-10-29 | 2025-11-12 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | Escape doors are lockable, the following examples were observed; - Ground floor in the Processing Building. - First floor Canteen areas in Processing Building. - Second Floor in the Processing Building. - Ground floor in the Stitching Building. - Exit gate from Second Floor in the Stitching Building. - Exit gate from Roof Level on the Stitching Building. - Exit door from ground floor in the Griege Building. - Exit doors from ground floor in the Weaving Building. - Exit door from Generator room in the Power House Building. - Frst floor of the Head Office Building. - Canteen Area in Head Office Building. Escape door does not allow for easy opening (e.g. ground floor exit from Store Building is stuck and difficult to open). Sliding doors serve for escape from areas with more than 10 occupants (ground floor Weaving Building). Doors into stairs swing against the direction of escape (e.g. Door into Stair 2 serving the Process Building roof). Escape door locked (e.g. first floor of the Head Office Building). | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | Escape doors are lockable, the following examples were observed; - Ground floor in the Processing Building. - First floor Canteen areas in Processing Building. - Second Floor in the Processing Building. - Ground floor in the Stitching Building. - Exit gate from Second Floor in the Stitching Building. - Exit gate from Roof Level on the Stitching Building. - Exit door from ground floor in the Griege Building. - Exit doors from ground floor in the Weaving Building. - Exit door from Generator room in the Power House Building. - Frst floor of the Head Office Building. - Canteen Area in Head Office Building. Escape door does not allow for easy opening (e.g. ground floor exit from Store Building is stuck and difficult to open). Sliding doors serve for escape from areas with more than 10 occupants (ground floor Weaving Building). Doors into stairs swing against the direction of escape (e.g. Door into Stair 2 serving the Process Building roof). Escape door locked (e.g. first floor of the Head Office Building). | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3 + 3 months | 2026-01-29 | 2026-04-29 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | The discharge routes from the stairs are not fire separated from the floor occupancy: e.g.: - Processing Building Stair 1, Stair 2, Stair 4, Stair 5, Stair 7, Stair 8 and Stair 9 discharge routes are not fire separated from the floor occupancy. - Stitching Building Stair 1 and Stair 2 discharge routes are not fire separated from the floor occupancy. - Head Office Building Stair 1 discharge route is not fire separated. Obstructions on escape route (e.g. storage on exit route on first floor of the Head Office Building). Trip hazards on escape route (e.g. Stair 4 from first floor Stitching Building). Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) (e.g. Stair 2 from Roof of Processing Building). | Remove obstructions on escape routes and keep them clear for escape. Cover uneven areas in escape routes. Provide warning signs where headroom height is less than 2.05 m on escape routes. | 2 weeks | 2025-10-29 | 2025-11-12 |  |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | The discharge routes from the stairs are not fire separated from the floor occupancy: e.g.: - Processing Building Stair 1, Stair 2, Stair 4, Stair 5, Stair 7, Stair 8 and Stair 9 discharge routes are not fire separated from the floor occupancy. - Stitching Building Stair 1 and Stair 2 discharge routes are not fire separated from the floor occupancy. - Head Office Building Stair 1 discharge route is not fire separated. Obstructions on escape route (e.g. storage on exit route on first floor of the Head Office Building). Trip hazards on escape route (e.g. Stair 4 from first floor Stitching Building). Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) (e.g. Stair 2 from Roof of Processing Building). | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Exit access | The discharge routes from the stairs are not fire separated from the floor occupancy: e.g.: - Processing Building Stair 1, Stair 2, Stair 4, Stair 5, Stair 7, Stair 8 and Stair 9 discharge routes are not fire separated from the floor occupancy. - Stitching Building Stair 1 and Stair 2 discharge routes are not fire separated from the floor occupancy. - Head Office Building Stair 1 discharge route is not fire separated. Obstructions on escape route (e.g. storage on exit route on first floor of the Head Office Building). Trip hazards on escape route (e.g. Stair 4 from first floor Stitching Building). Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) (e.g. Stair 2 from Roof of Processing Building). | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. Implement measures to ensure adequate clear head height is achieved along all escape routes. | F6 + 4 months | 2026-02-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Travel distance | Extended common path travel distance measured in the following locations: - Ground floor Storage area in the Weaving Building, measured at 35m. - First floor office in the Head Office Building, measured 27m and 29m to the exit stairs. - Generator Room of the Power House Building, measured at 30m to the exit. - Basement of the Store Building is a high hazard area due chemical storage, measured at >25m. - Processing Building ground floor Plant Room, measured at >25m. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Travel distance | Extended common path travel distance measured in the following locations: - Ground floor Storage area in the Weaving Building, measured at 35m. - First floor office in the Head Office Building, measured 27m and 29m to the exit stairs. - Generator Room of the Power House Building, measured at 30m to the exit. - Basement of the Store Building is a high hazard area due chemical storage, measured at >25m. - Processing Building ground floor Plant Room, measured at >25m. | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | F8 + 4 months | 2026-02-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Protection of stairs | Unprotected exit stairs: e.g. - Processing Building Stair 1, Stair 2, Stair 4, Stair 5, Stair 7, Stair 8 and Stair 9 are not fire separated from the occupancy on all floors. - Stitching Building Stair 1, Stair 2 and Stair 5 are not fire separated from the occupancy on all floors. - Store Building Stair 1 and Stair 2 are not fire separated on all floors. - Power Plant Building Stair 1 is not provided with fire doors on all floors. - Head Office Building Stair 1 is not fire separated from the occupancy on all floors. Unprotected openings to external stairs: e.g. - Stair 3 from first floor of the Processing Building, - Stair 1 from first floor of the Greige Building. - Stair 3 from first floor of the Stitching Building. Fire load observed within the stair: e.g. - Stitching Building Stair 2 has fire load stored under the stair on ground floor level. | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | 2025-10-29 | 2025-11-12 |  |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Protection of stairs | Unprotected exit stairs: e.g. - Processing Building Stair 1, Stair 2, Stair 4, Stair 5, Stair 7, Stair 8 and Stair 9 are not fire separated from the occupancy on all floors. - Stitching Building Stair 1, Stair 2 and Stair 5 are not fire separated from the occupancy on all floors. - Store Building Stair 1 and Stair 2 are not fire separated on all floors. - Power Plant Building Stair 1 is not provided with fire doors on all floors. - Head Office Building Stair 1 is not fire separated from the occupancy on all floors. Unprotected openings to external stairs: e.g. - Stair 3 from first floor of the Processing Building, - Stair 1 from first floor of the Greige Building. - Stair 3 from first floor of the Stitching Building. Fire load observed within the stair: e.g. - Stitching Building Stair 2 has fire load stored under the stair on ground floor level. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Protection of stairs | Unprotected exit stairs: e.g. - Processing Building Stair 1, Stair 2, Stair 4, Stair 5, Stair 7, Stair 8 and Stair 9 are not fire separated from the occupancy on all floors. - Stitching Building Stair 1, Stair 2 and Stair 5 are not fire separated from the occupancy on all floors. - Store Building Stair 1 and Stair 2 are not fire separated on all floors. - Power Plant Building Stair 1 is not provided with fire doors on all floors. - Head Office Building Stair 1 is not fire separated from the occupancy on all floors. Unprotected openings to external stairs: e.g. - Stair 3 from first floor of the Processing Building, - Stair 1 from first floor of the Greige Building. - Stair 3 from first floor of the Stitching Building. Fire load observed within the stair: e.g. - Stitching Building Stair 2 has fire load stored under the stair on ground floor level. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F11 + 4 months | 2026-02-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Escape stair condition | - Handrails are not provided on both sides of the stairs (e.g. Stair 2 Processing Building). | Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs (e.g. Stair 5 Stitching Building, Stair 2 Processing Building) . - Missing exit signs in corridors and circulation areas (e.g. Exit signage missing to final exit door on ground floor of the Head Office Building) . - Exit signs in production areas (e.g. Processing Building ground floor, Basement Level in the Stitching Building, ground floor in the Store Building.) - Missing exit signs in offices and back of house areas (e.g. Roof Plant Level on the Power House Building). - Exit signs are not uniform throughout the factory. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs (e.g. Stair 5 Stitching Building, Stair 2 Processing Building) . - Missing exit signs in corridors and circulation areas (e.g. Exit signage missing to final exit door on ground floor of the Head Office Building) . - Exit signs in production areas (e.g. Processing Building ground floor, Basement Level in the Stitching Building, ground floor in the Store Building.) - Missing exit signs in offices and back of house areas (e.g. Roof Plant Level on the Power House Building). - Exit signs are not uniform throughout the factory. | Ensure that all exit signage is checked periodically and in good working condition. | F14 + 3 months | 2026-01-29 | 2026-04-29 |  |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Fire Rated Construction | Separation of high-risk areas | - Compressor Room not fire separated on ground floor of Processing Building, from the main processing area. - Chemical Store Room is not fire separated on first floor of Processing Building, from the main processing area. - No fire separation of the Kitchen Area on first floor Processing Building, from the main processing area. - Water treatment Plant in the open factory floor on the first floor of the Processing Building, from the dying area. - No fire separation of Kitchen Area on third floor Stitching Building, from the main Canteen area. - Electrical Room is not fire separated on the ground floor of the Weaving Building, from the main processing area. - No fire separation of the Kitchen area ground floor of the Weaving Building, from main Canteen area. - Generators are not fire separated from the control room in the Power House Building. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Fire Rated Construction | Separation of high-risk areas | - Compressor Room not fire separated on ground floor of Processing Building, from the main processing area. - Chemical Store Room is not fire separated on first floor of Processing Building, from the main processing area. - No fire separation of the Kitchen Area on first floor Processing Building, from the main processing area. - Water treatment Plant in the open factory floor on the first floor of the Processing Building, from the dying area. - No fire separation of Kitchen Area on third floor Stitching Building, from the main Canteen area. - Electrical Room is not fire separated on the ground floor of the Weaving Building, from the main processing area. - No fire separation of the Kitchen area ground floor of the Weaving Building, from main Canteen area. - Generators are not fire separated from the control room in the Power House Building. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F16 + 4 months | 2026-02-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Fire Rated Construction | Separation of occupancies | - The Stitching Building and Greige Down Buildings are connected on the first floor via two bridges between occupancies, there is no fire separation provided between the two occupancies. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Fire Rated Construction | Separation of occupancies | - The Stitching Building and Greige Down Buildings are connected on the first floor via two bridges between occupancies, there is no fire separation provided between the two occupancies. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F18 + 4 months | 2026-02-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Storage | - Storage area not fire separated from processing area (e.g. ground floor of Processing Building, ground floor in Storage Building, first floor of Stitching Building, ground floor of Weaving Building, first floor of Head Office Building). - In process storage area exceeding allowable limits (e.g. ground floor of Processing Building, ground floor Process Area of Storage Building, first floor of Stitching Building, first floor of Greige Building). | Identify all designated storage areas. - Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification work. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Storage | - Storage area not fire separated from processing area (e.g. ground floor of Processing Building, ground floor in Storage Building, first floor of Stitching Building, ground floor of Weaving Building, first floor of Head Office Building). - In process storage area exceeding allowable limits (e.g. ground floor of Processing Building, ground floor Process Area of Storage Building, first floor of Stitching Building, first floor of Greige Building) | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F20 + 4 months | 2026-02-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Suppression | Standpipe system | - Connection points are not compliant (observed throughout the Processing Building and Stitching Building). - Missing standpipe outlets in stairs (observed throughout the Processing Building and Stitching Building). | Replace any damaged equipment and ensure the current system is fully operational. | 2 weeks | 2025-10-29 | 2025-11-12 |  |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Suppression | Standpipe system | - Connection points are not compliant (observed throughout the Processing Building and Stitching Building). - Missing standpipe outlets in stairs (observed throughout the Processing Building and Stitching Building). | (1) Submit design documentation for the required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the system with NFPA 14, 20, 22, and 24. | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Suppression | Standpipe system | - Connection points are not compliant (observed throughout the Processing Building and Stitching Building). - Missing standpipe outlets in stairs (observed throughout the Processing Building and Stitching Building). | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the system design submitted earlier. | F23 + 1 month | 2026-02-28 | 2026-03-28 |  |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Suppression | Standpipe system | - Connection points are not compliant (observed throughout the Processing Building and Stitching Building). - Missing standpipe outlets in stairs (observed throughout the Processing Building and Stitching Building). | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the system. | F24 + 3 months | 2026-03-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Suppression | Standpipe system | - Connection points are not compliant (observed throughout the Processing Building and Stitching Building). - Missing standpipe outlets in stairs (observed throughout the Processing Building and Stitching Building). | (4) Once installation of the system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F25 + 3 months | 2026-06-28 | 2026-09-28 |  |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Suppression | Standpipe system | - Connection points are not compliant (observed throughout the Processing Building and Stitching Building). - Missing standpipe outlets in stairs (observed throughout the Processing Building and Stitching Building). | (5) Factory to advise Pakistan Accord when system installation is fully completed and the system is fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | F26 + 3 months | 2026-09-28 | 2026-12-28 |  |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Suppression | Standpipe system | - Connection points are not compliant (observed throughout the Processing Building and Stitching Building). - Missing standpipe outlets in stairs (observed throughout the Processing Building and Stitching Building). | (6) Provide full testing and commissioning (T&C) certification from the system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the system will be complete. | F27 + 4 months | 2026-12-28 | 2027-04-28 |  |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Suppression | Fire pumps | - Fire pump set is not listed. | Provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system as per steps (1) t (6) mentioned in standpipe system. | 18 months | 2025-10-29 | 2027-04-29 |  |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Suppression | Fire extinguishers | - Poor condition of fire extinguishers (e.g. Fire Extinguisher without valves on ground floor in Processing Building). | Inspection of all fire extinguishers within the facility and ensure all fire extinguishers are charged. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Suppression | Fire extinguishers | - Poor condition of fire extinguishers (e.g. Fire Extinguisher without valves on ground floor in Processing Building). | Ensure that all building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Fire extinguishers | - Poor condition of fire extinguishers (e.g. Fire Extinguisher without valves on ground floor in Processing Building). | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | F31 + 3 months | 2026-01-29 | 2026-04-29 |  |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Hazardous Materials | Chemicals storage | Flammable materials are not stored in a fire separated room: - Chemicals stored in the processing area on ground floor of Processing Building. - Chemical mixing area not fire separated from Processing area in Weaving Building. | It is recommended for the immediate removal of chemicals stored in the processing area. | 2 weeks | 2025-10-29 | 2025-11-12 |  |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Hazardous Materials | Chemicals storage | Flammable materials are not stored in a fire separated room: - Chemicals stored in the processing area on ground floor of Processing Building. - Chemical mixing area not fire separated from Processing area in Weaving Building. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to the Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction.) - Ventilation provisions to each of these rooms. | 4 months | 2025-10-29 | 2026-02-28 |  |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Hazardous Materials | Chemicals storage | Flammable materials are not stored in a fire separated room: - Chemicals stored in the processing area on ground floor of Processing Building. - Chemical mixing area not fire separated from Processing area in Weaving Building. | Implement the above plan on site. All chemical storage areas to be compliant with Pakistan Accord Standard. | F34 + 4 months | 2026-02-28 | 2026-06-28 |  |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Safety Management | Fire drills | - No regular fire drills (e.g. no evidence of regular fire drills have been provided). | Conduct a fire drill and make records, including findings and recommended future improvements. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Safety Management | Fire drills | - No regular fire drills (e.g. no evidence of regular fire drills have been provided). | Ensure fire drills are performed a minimum 2 times per year. | F36 + 3 months | 2026-01-29 | 2026-04-29 |  |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Safety Management | Records of system testing | - Inadequate records of testing of Standpipes. - Inadequate records of testing of Fire Extinguishers. | - Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule is to be submitted to the Accord for review and approval. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Safety Management | Records of system testing | - Inadequate records of testing of Standpipes. - Inadequate records of testing of Fire Extinguishers. | - Ensure all systems are being tested as per the schedule agreed with Accord . - Keep testing records. | F38 + 3 months | 2026-01-29 | 2026-04-29 |  |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Standpipes. - Inadequate records of maintenance of Fire Extinguisher. | - Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. - The schedule is to be submitted to the Accord for review and approval. | 3 months | 2025-10-29 | 2026-01-29 |  |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Standpipes. - Inadequate records of maintenance of Fire Extinguisher. | - Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. | F40 + 3 months | 2026-01-29 | 2026-04-29 |  |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Fire Safety Management | Emergency Action Plan | - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-10-29 | 2025-12-29 |  |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Fire Safety Management | Emergency Action Plan | - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F42 + 2 months | 2025-12-29 | 2026-02-28 |  |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
2025-04-28
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | MK Sons (Pvt.) Ltd. - 2 Km Jaranwala Road, Khurrianwala, Faisalabad, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 2025-04-28
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | PROPOSED | PROPOSED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-09-03 | 2025-10-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Unit at the basement level appear to be highly stressed for the observed load. | Verify in-situ concrete stresses either by 100mm dia. cores or existing cylinder strength data for columns or 100mm dia. cores from 4 columns and submit results to Pakistan Accord for review | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Unit at the basement level appear to be highly stressed for the observed load. | Factory Engineer to review design, loads and column stresses. | S2 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal RC columns of the Stitching Unit at the basement level appear to be highly stressed for the observed load. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S3 + 3 months | 2026-04-29 | 2026-07-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Cracking | Beams | This issue is related to the Stitching Unit. A crack is observed at a soffit of an RC beam of Stitching Unit at the 1st floor level. The crack appears to be due to separation of plaster from the RC beam surface. | Building Engineer to carry out condition survey of the RC beams to investigate cause and impact of these cracks on the capacity of the beams. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Cracking | Beams | This issue is related to the Stitching Unit. A crack is observed at a soffit of an RC beam of Stitching Unit at the 1st floor level. The crack appears to be due to separation of plaster from the RC beam surface. | Propose measures to prevent future damage and to repair the existing damage / strengthen the beam as required and submit to Pakistan Accord for approval. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Cracking | Beams | This issue is related to the Stitching Unit. A crack is observed at a soffit of an RC beam of Stitching Unit at the 1st floor level. The crack appears to be due to separation of plaster from the RC beam surface. | Once reviewed, implement the remedial work. Continue monitoring them on an on-going basis | S6 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Cracking | Beams | This issue is related to the Grey Godown extension. A diagonal crack is observed in an RC beam of the Grey Godown extension. Heavy load is not observed at the roof level. Plaster was removed from the crack location during the inspection, and it appears that the crack penetrates through the RC beam. | Building Engineer to carry out condition survey of the RC beams to investigate cause and impact of these cracks on the capacity of the beams. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Cracking | Beams | This issue is related to the Grey Godown extension. A diagonal crack is observed in an RC beam of the Grey Godown extension. Heavy load is not observed at the roof level. Plaster was removed from the crack location during the inspection, and it appears that the crack penetrates through the RC beam. | Propose measures to prevent future damage and to repair the existing damage / strengthen the beam as required and submit to Pakistan Accord for approval. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Cracking | Beams | This issue is related to the Grey Godown extension. A diagonal crack is observed in an RC beam of the Grey Godown extension. Heavy load is not observed at the roof level. Plaster was removed from the crack location during the inspection, and it appears that the crack penetrates through the RC beam. | Once reviewed, implement the remedial work. Continue monitoring them on an on-going basis. | S9 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Cracking | Walls | This relates to the load bearing masonry walls of the Stitching Unit’s Canteen. Cracks are observed in the walls at locations where precast roof beams bears on the walls. These cracks may be attributed to bearing stress failure of the masonry wall beneath the precast beams or insufficient capacity of the lintels above the window openings | One of the window lintel appears to have a limited bearing length on the masonry wall. The wall supports a precast roof beam. Building Engineer to remove the plaster from the wall and verify the bearing length of the lintel. Should a short bearing length be confirmed, replace the lintel with one that provides an adequate bearing length. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Cracking | Walls | This relates to the load bearing masonry walls of the Stitching Unit’s Canteen. Cracks are observed in the walls at locations where precast roof beams bears on the walls. These cracks may be attributed to bearing stress failure of the masonry wall beneath the precast beams or insufficient capacity of the lintels above the window openings | Building Structural Engineer to propose the remedial work to Pakistan Accord. | S11 + 1 month | 2026-01-29 | 2026-02-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Cracking | Walls | This relates to the load bearing masonry walls of the Stitching Unit’s Canteen. Cracks are observed in the walls at locations where precast roof beams bears on the walls. These cracks may be attributed to bearing stress failure of the masonry wall beneath the precast beams or insufficient capacity of the lintels above the window openings | Once reviewed, implement the remedial work. | S12 + 3 months | 2026-02-28 | 2026-05-28 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Cracking | Material interface | This relates to the Greige Godown Building. Non-structural masonry wall cracking locally due to no soft joint provided between RC beam and masonry wall. | Building Structural Engineer to monitor cracking in these locations and propose remedial details as required, including isolation of the wall from RC beam | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Power House building. The exposed reinforcement in the Power House building present a significant risk of corrosion to the reinforcement, which may subsequently result in concrete cracking and spalling | Building Engineer to inspect the area and propose measures to cover up the exposed reinforcing bars. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Power House Building. The exposed reinforcement in the Power House building present a significant risk of corrosion to the reinforcement, which may subsequently result in concrete cracking and spalling. | Implement the remedial work. | S15 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Stitching Unit. The exposed reinforcement in the Stitching Unit building presents a significant risk of corrosion to the reinforcement, which may subsequently result in concrete cracking and spalling. | Building Engineer to inspect the area and propose measures to cover up the exposed reinforcing bars. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Stitching Unit. The exposed reinforcement in the Stitching Unit building presents a significant risk of corrosion to the reinforcement, which may subsequently result in concrete cracking and spalling. | Implement the remedial work. | S17 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Processing Unit. The exposed reinforcement in the Processing Unit building presents a significant risk of corrosion to the reinforcement, which may subsequently result in concrete cracking and spalling. | Building Engineer to inspect the area and propose measures to cover up the exposed reinforcing bars. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Processing Unit. The exposed reinforcement in the Processing Unit building presents a significant risk of corrosion to the reinforcement, which may subsequently result in concrete cracking and spalling. | Implement the remedial work. | S19 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Other Damage/Defects | Spalling concrete | This issue relates to Canteen of Stitching Unit. Vertical cracks are observed in some of the RC columns of Canteen over the Stitching Unit. Heavy load is not observed above the columns. The cracks in the column appear to be related to the in-sufficient reinforcement cover to column reinforcement | Building Engineer to inspect the areas and confirm the source of the damage. Propose repairs to structure and submit to Pakistan Accord for review. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Other Damage/Defects | Spalling concrete | This issue relates to Canteen of Stitching Unit. Vertical cracks are observed in some of the RC columns of Canteen over the Stitching Unit. Heavy load is not observed above the columns. The cracks in the column appear to be related to the in-sufficient reinforcement cover to column reinforcement. | Implement remedial work. | S21 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Other Damage/Defects | Spalling concrete | This issue relates to Canteen of Stitching Unit. Vertical cracks are observed in some of the RC columns of Canteen over the Stitching Unit. Heavy load is not observed above the columns. The cracks in the column appear to be related to the in-sufficient reinforcement cover to column reinforcement. | Continue to monitor for future signs of water ingress/damage. | S22 + 3 months | 2026-04-29 | 2026-07-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Other Damage/Defects | Spalling concrete | This issue relates to Power House. Cracks are observed in the inverted beams of the Power House roof. The cracks appear to be related to the corrosion of beam reinforcement. | Building Engineer to inspect the areas and confirm the source of the damage. Propose repairs to structure and submit to Pakistan Accord for review. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Other Damage/Defects | Spalling concrete | This issue relates to Power House. Cracks are observed in the inverted beams of the Power House roof. The cracks appear to be related to the corrosion of beam reinforcement. | Implement remedial work. | S24 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S26 | Other Damage/Defects | Spalling concrete | This issue relates to Power House. Cracks are observed in the inverted beams of the Power House roof. The cracks appear to be related to the corrosion of beam reinforcement | Continue to monitor for future signs of water ingress/damage. | S25 + 3 months | 2026-04-29 | 2026-07-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S27 | Other Damage/Defects | Spalling concrete | This issue relates to Grey Godown. Vertical cracks are observed in some of the RC columns of Grey Godown at Ground floor level. The column cracks appear to be related to the insufficient reinforcement cover to column reinforcement. | Building Engineer to inspect the areas and confirm the source of the damage. Propose repairs to structure and submit to Pakistan Accord for review. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S28 | Other Damage/Defects | Spalling concrete | This issue relates to Grey Godown. Vertical cracks are observed in some of the RC columns of Grey Godown at Ground floor level. The column cracks appear to be related to the insufficient reinforcement cover to column reinforcement. | Implement remedial work. | S27 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S29 | Other Damage/Defects | Spalling concrete | This issue relates to Grey Godown. Vertical cracks are observed in some of the RC columns of Grey Godown at Ground floor level. The column cracks appear to be related to the insufficient reinforcement cover to column reinforcement. | Continue to monitor for future signs of water ingress/damage. | S28 + 3 months | 2026-04-29 | 2026-07-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S30 | Other Damage/Defects | Moisture ingress | This issue refers to the Processing Unit. Uncontrolled drainage, which may contain chemicals, poses a risk to the reinforced concrete (RC) columns. Over time, moisture can infiltrate the RC columns, potentially leading to the corrosion of the column reinforcement, which may ultimately result in the formation of cracks. | Building Engineer to inspect area and provide adequate drainage. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S31 | Other Damage/Defects | Brickwork instability | This refers to the non-load masonry wall around the perimeter of the Power House building. The southwest and northwest masonry walls are separating out from the RC columns and are unrestrained. The large span of the masonry wall may collapse due to lateral movement. | Building Engineer to inspect the area and propose repairs to structure and submit to Pakistan Accord for review. | 3 months | 2025-10-29 | 2026-01-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S32 | Other Damage/Defects | Brickwork instability | This refers to the non-load masonry wall around the perimeter of the Power House building. The southwest and northwest masonry walls are separating out from the RC columns and are unrestrained. The large span of the masonry wall may collapse due to lateral movement. | Implement the remedial work | S31 + 3 months | 2026-01-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S33 | Other Damage/Defects | Health and Safety | This issue relates to Processing Unit. Inadequate cover to a drainage channel located south of the Processing Unit is observed. This presents a risk for a person of falling into the drainage channel due to slip / trip – Health & Safety concern. | Provide appropriate cover to all drainage trenches. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S34 | Other Damage/Defects | Health and Safety | This issue relates to Stitching Unit Roof of the Stitching Unit lack edge protection. Stitching Unit roof is equipped with PV solar panels. Inadequate roof edge protection presents a risk of potential injury from slips, trips, or falls while accessing and maintaining services on the roofs – Health & Safety concern. | Provide adequate edge protection on the roofs, and on any other part of the factory with the same issue. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S35 | Other Damage/Defects | Health and Safety | This issue relates to Power House. Roof of the Power House building lack edge protection. Inadequate roof edge protection presents a risk of potential injury from slips, trips, or falls while accessing and maintaining services on the roofs – Health & Safety concern. | Provide adequate edge protection on the roofs, and on any other part of the factory with the same issue. | 1 month | 2025-10-29 | 2025-11-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S36 | Structural Documentation | Documentation unavailable | Most of the buildings are either missing structural general arrangement drawings or need to be updated. • Weaving Unit: Structural drawings are not available and need to be prepared. • Greige Godown: Structural framing layouts of the greige godown are not available and need to be prepared. • RC columns layout of the building is available; however, the structural sizes of the columns are not indicated. Drawing needs to be updated. • Structural drawings for the extension between the Stitching Unit and Greige Godown are not available and need to be prepared. • Stitching Unit: Structural framing layout between gridlines 1-8 of the ground floor of Stitching Unit are available. However, the layouts between gridlines 8–18 are missing, and need to be prepared. • Structural framing layout of basement, 1st and 2nd floor are not available, and need to be prepared. • Structural framing layout of columns are not available, and need to be prepared. • Processing Unit: Structural drawings of the Processing Unit are not available and need to be prepared. • Head Office: Structural drawings of the Head Office are not available and need to be prepared. • Store: Structural drawings of the Store are not available and need to be prepared. • The architectural drawings of all buildings are not available except the Head Office and need to be prepared. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as built documentation. | 6 months | 2025-10-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S37 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in the Factory. | Building structural engineer to review design documentation to confirm load capacity of the structure. Develop safe load plans and submit to Pakistan Accord for review. | 6 months | 2025-10-29 | 2026-04-29 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S38 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in the Factory. | Factory to post safe load plans on each floor. | S37 + 1 month | 2026-04-29 | 2026-05-29 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixtures
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1