## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
28 & 29-Oct-2024
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Nishat Mills Limited (Home Textile Unit) - 5 Km Rohi Nala Rd, Nishat Avenue, Off 22 Km Ferozpur Rd. Lahore, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 28 & 29-Oct-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-04-07 | 2025-06-02 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation or electrical room layout drawings available for the factory. | Develop detailed substation layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-06-05 | 2025-09-05 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation or electrical room layout drawings available for the factory. | Regularly update and review the substation layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2 + 3 months | 2025-09-05 | 2025-12-05 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the provided SLDs were outdated and only available for the main LT panels, with no information provided for the individual distribution panels. Additionally, the SLDs were missing essential details, including information on solar panels and their connections, cable types (PVC/XLPE), conductor materials (CU/AL), protective devices for solar and other sources, load distribution clarity, UPS system specifications, and the earthing system. Furthermore, the SLDs did not match the actual installations in the main LT panels. | Update the existing electrical single-line diagrams for the entire facility following the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the provided SLDs were outdated and only available for the main LT panels, with no information provided for the individual distribution panels. Additionally, the SLDs were missing essential details, including information on solar panels and their connections, cable types (PVC/XLPE), conductor materials (CU/AL), protective devices for solar and other sources, load distribution clarity, UPS system specifications, and the earthing system. Furthermore, the SLDs did not match the actual installations in the main LT panels. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4 + 2 months | 2025-10-02 | 2025-12-02 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-06-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6 + 2 months | 2025-12-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | Circuit breakers were found to be damaged inside the distribution panels of Unit 31 on the 2nd floor. For example, the circuit breaker levers were broken, and the labels had been removed. | Replace all the broken circuit breakers to ensure the safety and reliability of the electrical system. | 1 months | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Circuit breakers | It was observed that multiple cables were underrated and not appropriate for the connected circuit breaker sizes throughout the facility, for example: • At the LT panel of Unit 31, 630A circuit breakers were connected to 70 mm² PVC cables and 250A circuit breakers were connected to 35 mm²PVC cables. • At the main power distribution panel of Unit 31 Extension, 400A circuit breakers were connected to 70 mm² PVC cables. • At the distribution panel of Unit 32, a 250A circuit breaker was connected to a 6 mm² PVC cable, and 125A 3-pole circuit breakers were connected to a single 16 mm² PVC cables on the ground floor. Additionally, 60A circuit breakers were connected to a 2.5 mm² PVC cable on both the 2nd and 3rd floors. • At the main power distribution panel of the Accessory Store, a 125A circuit breaker was connected to a 10mm² PVC cable. | Evaluate the circuit breaker (CB) ratings and cable sizes for all circuits mentioned above according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | Hot spots were observed, particularly at the following locations: − 157.0⁰C inside Unit 32, 4th floor power distribution board. − 121.0⁰C inside Accessory Store, 2nd floor LDB − 80.5⁰C inside Unit 31 Extension, 2nd floor power distribution board. − 79.3⁰C inside Unit 32, 4th floor power distribution board. − 70.0⁰C inside Unit 31 Extension, ground floor power distribution board. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted, and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | Hot spots were observed, particularly at the following locations: − 157.0⁰C inside Unit 32, 4th floor power distribution board. − 121.0⁰C inside Accessory Store, 2nd floor LDB − 80.5⁰C inside Unit 31 Extension, 2nd floor power distribution board. − 79.3⁰C inside Unit 32, 4th floor power distribution board. − 70.0⁰C inside Unit 31 Extension, ground floor power distribution board. | During the inspection, some circuits were identified where the temperature was exceeding 20°C above ambient temperature. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Hot Spots | Hot spots were observed, particularly at the following locations: − 157.0⁰C inside Unit 32, 4th floor power distribution board. − 121.0⁰C inside Accessory Store, 2nd floor LDB − 80.5⁰C inside Unit 31 Extension, 2nd floor power distribution board. − 79.3⁰C inside Unit 32, 4th floor power distribution board. − 70.0⁰C inside Unit 31 Extension, ground floor power distribution board. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | E11 + 6 months | 2025-07-02 | 2026-01-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Earthing system | In Unit 32, on the 1st floor, neutral and earth wires were improperly interconnected on the same connecting strip inside the distribution board. | Design and evaluate the earthing system installation throughout the facility. Disconnect the earth bars from the neutral bars with the distribution boards and ensure proper separation and connection. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | The following equipotential bonding issues were identified, including but not limited to the areas mentioned below: • Drinking water coolers lacked proper earthing and bonding. • Panel doors exhibited inadequate bonding, as seen in the LT room panel. • In several distribution boards in Unit 32, the earth cable for the panel door was broken. • Cable ducts were not properly bonded at each segment, such as in Unit 31 on the 2nd floor. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 6 months | 2025-06-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | During the inspection of outlets and machine plugs in the Stitching area on the 3rd floor of Unit 31, it was found that some stitching machines were missing the earth cable. This lack of proper earthing poses a significant risk of electrical shock to workers operating the machinery. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 6 months | 2025-06-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. | Prepare a dedicated SLD for Earth and Neutral for the full system including identification of earth pits, main earth bar, earth neutral connection, earth cable sizes, grounding/bonding of conductive parts (pipework, metallic frame, tapware) and the topology of the system shall be indicated on the SLD (TN-C, TN-S, TT, TN-C-S). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Earthing system | Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E16 + 2 month | 2025-10-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | Combustible material was found inside the distribution panel in the folding area of Unit 31. | Combustible materials found inside and near electrical panels should be immediately removed, and a designated safety zone should be established and maintained to prevent future accumulation. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | In Unit 32 on the 1st floor, the MCB breakers were hanging unsupported inside the distribution panel. | Install support brackets for the breakers in distribution panel to ensure proper stability and compliance with safety standards. | 2 months | 2025-06-02 | 2025-08-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical components were found to be unsuitable for the environmental conditions in which they were installed, including Unit 31 Extension 1st floor, where an electrical enclosure made of combustible material was found. | Identify electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed following Section 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical panels showed signs of corrosion, indicating potential exposure to moisture or other corrosive elements, including Unit 31 ground floor electrical enclosures. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Panel/cabling/busbar | Exposed copper connecting strips were found inside several distribution boards, including the Unit 31 1st floor distribution board and the Unit 32 ground floor distribution board. | Exposed copper connecting strips should be properly insulated with suitable materials to prevent electrical hazards. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Panel/cabling/busbar | Additional concerns included missing phase separators, improper termination of cables, and inadequate cable dressing in the Accessory Store and the lighting and power distribution boards (DBs) on the 4th floor of Unit 31 and Unit 32. | Install missing phase separators, ensure proper cable management by organizing and securing cables within the panels using cable ties, clips, or ducting. Verify that all connections are neatly arranged and labelled to improve safety, ease of maintenance, and compliance with electrical standards such as BS 7671. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Panel/cabling/busbar | Additional concerns included missing phase separators, improper termination of cables, and inadequate cable dressing in the Accessory Store and the lighting and power distribution boards (DBs) on the 4th floor of Unit 31 and Unit 32. | Establish a schedule for regular maintenance and inspection of the panel, cabling, and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E23 + 2 months | 2025-10-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Loop Connection | During the inspection loop connections were identified within the electrical panels, such as in main power distribution board of Accessory Store, the folding area in Unit 31, and the power distribution board on the 2nd floor of Unit 32. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed within all the electrical panels of Unit 32 power distribution boards. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Openings | The inspection revealed unsealed openings in the wall and distribution boards in the Unit 31 Extension and Accessory Store main power distribution panel room. | Corrective actions are required to seal all openings and replace missing plates to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Openings | The inspection revealed unsealed openings in the wall and distribution boards in the Unit 31 Extension and Accessory Store main power distribution panel room. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | E27 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | DBs & Elec Protection Systems | Adequate accessibility | At some locations, such as Unit 31 LT room and ground & 4th floor, it was found that the electrical panels lacked the required space for inspection and easy access due to obstructions created by placed items. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust inside the lighting and power distribution panels in the Unit 31 folding area. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust inside the lighting and power distribution panels in the Unit 31 folding area. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E30 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. • No lightning protection system was installed in Unit 31 & Unit 31 Extension, and there was no risk assessment provided to confirm whether it was not required. • A lightning protection system was provided in Unit 32, however, there was no study available to confirm its adequacy. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance requirements based on BS EN 62305 standard. Submit design calculations for the Pakistan Accord review. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. • No lightning protection system was installed in Unit 31 & Unit 31 Extension, and there was no risk assessment provided to confirm whether it was not required. • A lightning protection system was provided in Unit 32, however, there was no study available to confirm its adequacy. | If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. | E32 + 5 months | 2025-07-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, several issues were noted with the fire alarm system, including the use of non-listed, non-addressable equipment, inadequate detection coverage, non-fire-rated cables, and faulty sounders and flashers. Furthermore, the system was found to be non-compliant with NFPA 72 standards. Additional issues were identified regarding the Fire Alarm Detection System (FADS), specifically: • The FACP for Unit 31 was in silent mode due to faults displayed on the panel and could not be reset. • Detection devices in both Unit 31 and Unit 31 Extension had either been removed or were unsupported and hanging from the ceiling. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, several issues were noted with the fire alarm system, including the use of non-listed, non-addressable equipment, inadequate detection coverage, non-fire-rated cables, and faulty sounders and flashers. Furthermore, the system was found to be non-compliant with NFPA 72 standards. Additional issues were identified regarding the Fire Alarm Detection System (FADS), specifically: • The FACP for Unit 31 was in silent mode due to faults displayed on the panel and could not be reset. • Detection devices in both Unit 31 and Unit 31 Extension had either been removed or were unsupported and hanging from the ceiling. | (1) Submit design documentation for new system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, several issues were noted with the fire alarm system, including the use of non-listed, non-addressable equipment, inadequate detection coverage, non-fire-rated cables, and faulty sounders and flashers. Furthermore, the system was found to be non-compliant with NFPA 72 standards. Additional issues were identified regarding the Fire Alarm Detection System (FADS), specifically: • The FACP for Unit 31 was in silent mode due to faults displayed on the panel and could not be reset. • Detection devices in both Unit 31 and Unit 31 Extension had either been removed or were unsupported and hanging from the ceiling. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E35 + 1 month | 2025-09-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, several issues were noted with the fire alarm system, including the use of non-listed, non-addressable equipment, inadequate detection coverage, non-fire-rated cables, and faulty sounders and flashers. Furthermore, the system was found to be non-compliant with NFPA 72 standards. Additional issues were identified regarding the Fire Alarm Detection System (FADS), specifically: • The FACP for Unit 31 was in silent mode due to faults displayed on the panel and could not be reset. • Detection devices in both Unit 31 and Unit 31 Extension had either been removed or were unsupported and hanging from the ceiling. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E36 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, several issues were noted with the fire alarm system, including the use of non-listed, non-addressable equipment, inadequate detection coverage, non-fire-rated cables, and faulty sounders and flashers. Furthermore, the system was found to be non-compliant with NFPA 72 standards. Additional issues were identified regarding the Fire Alarm Detection System (FADS), specifically: • The FACP for Unit 31 was in silent mode due to faults displayed on the panel and could not be reset. • Detection devices in both Unit 31 and Unit 31 Extension had either been removed or were unsupported and hanging from the ceiling. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | E37 + 5 months | 2026-02-02 | 2026-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, several issues were noted with the fire alarm system, including the use of non-listed, non-addressable equipment, inadequate detection coverage, non-fire-rated cables, and faulty sounders and flashers. Furthermore, the system was found to be non-compliant with NFPA 72 standards. Additional issues were identified regarding the Fire Alarm Detection System (FADS), specifically: • The FACP for Unit 31 was in silent mode due to faults displayed on the panel and could not be reset. • Detection devices in both Unit 31 and Unit 31 Extension had either been removed or were unsupported and hanging from the ceiling. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E38 + 3 months | 2026-07-02 | 2026-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, several issues were noted with the fire alarm system, including the use of non-listed, non-addressable equipment, inadequate detection coverage, non-fire-rated cables, and faulty sounders and flashers. Furthermore, the system was found to be non-compliant with NFPA 72 standards. Additional issues were identified regarding the Fire Alarm Detection System (FADS), specifically: • The FACP for Unit 31 was in silent mode due to faults displayed on the panel and could not be reset. • Detection devices in both Unit 31 and Unit 31 Extension had either been removed or were unsupported and hanging from the ceiling. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E39 + 3 months | 2026-10-02 | 2027-01-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional on the 3rd floor Accessory Store. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 2 months | 2025-06-02 | 2025-08-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional on the 3rd floor Accessory Store. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E41 + 3 months | 2025-08-02 | 2025-11-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Emergency Lighting | Provided but insufficient | The emergency lighting system was non-compliant and not installed in all required areas, including the egress routes on the 3rd floor of Unit 31, storage aisles of the Accessory Store, emergency stairwells, HT and Transformer Rooms. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Emergency Lighting | Provided but insufficient | Non-illuminated exit signs were used on egress routes without nearby emergency lights in most areas. | Install illuminated exit signs or emergency lights near non-illuminated exit signs to ensure visibility along egress routes during emergencies. | E43 + 2 months | 2025-10-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | Emergency Lighting | Provided but insufficient | A central UPS was utilized to provide backup power to the emergency lighting; however, the battery calculations were not available, and non-fire-rated cables were used. | Upgrade the UPS system to ensure sufficient battery autonomy for providing backup power to the emergency fittings throughout the facility and ensure installation with fire-rated cabling. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Emergency Lighting | Provided but insufficient | External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during evening evacuations. | Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Emergency Lighting | Provided but insufficient | External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during evening evacuations. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E46 + 2 months | 2025-10-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-06-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E48 + 2 months | 2025-12-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | It was observed that the HT Room was poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | Add more lighting fixtures in poorly lit areas to ensure even distribution of light. Focus on areas that require the highest visibility, such as around equipment and control panels. | 2 months | 2025-06-02 | 2025-08-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | It was observed that the HT Room was poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | Establish regular maintenance and testing of luminaires within the spaces to ensure adequate performance. | E50 + 3 months | 2025-08-02 | 2025-11-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Generator, Transformer & Sub-Station Room | Breathing system | The silica gel in the breather of 2000 kVA Transformer was found to be saturated, indicating the need for replacement. | Inspect and replace the silica gel in all Transformer breathers to maintain optimal moisture control, prevent insulation degradation, and enhance the overall safety and reliability of the transformers. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Generator, Transformer & Sub-Station Room | Breathing system | The silica gel in the breather of 2000 kVA Transformer was found to be saturated, indicating the need for replacement. | Implement a regular maintenance schedule to periodically inspect and service the breathing system components, ensuring the silica gel is replaced as needed and that all seals and connections are intact to maintain system integrity. | E52 + 2 months | 2025-07-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Cabling & Wiring | Cable support and protection | Proper support was not provided for cables in Units 31 and 32; instead, they were hung along the walls and ceiling. Inadequate support can lead to sagging or stress on cable trays and cables, potentially causing damage or failure. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 374 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Cabling & Wiring | Cable support and protection | The shelling wire support for hanging bulbs and tube rods in Unit 31 on the 2nd floor poses electrical hazards from inadequate support, risking short circuits or fires. Additionally, it increases the likelihood of bulbs or tubes falling, which could injure personnel below. | Remove the shelling wire support and ensure that appropriate cable support systems are installed for hanging bulbs and tube rods to enhance safety and compliance. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 375 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Cabling & Wiring | Cable support and protection | Electrical cables were found running at floor level for machine connections. This arrangement creates a tripping hazard for personnel working in the area, and the cables are susceptible to damage from constant foot traffic, especially during an evacuation. | Elevate the cables off the floor to eliminate tripping hazards and prevent damage from foot traffic in accordance with Regulation 522.6 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 376 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Cabling & Wiring | Cable support and protection | On the working table in Unit 31 Extension, 1st floor, the weighing scale's charger adaptor is taped, indicating potential damage and posing an electrical and fire hazard. Additionally, the charger cord across the workspace creates a trip hazard. | Replace the taped adaptor with a new, properly insulated one and secure the cord to eliminate trip hazards. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 377 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Cabling & Wiring | Cable support and protection | Cable trays and cable ducts were found rusted both inside the production floors and along the external walls of Unit 32. | Replace rusted cable trays and ducts to prevent potential damage to cables and ensure safe electrical installations. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 378 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Cable support and protection | Cable trays and cable ducts were found rusted both inside the production floors and along the external walls of Unit 32. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices. Conduct safety training sessions for all personnel to educate them on the dangers of short-circuiting electrical systems and enforce strict safety protocols. | E58 + 2 months | 2025-10-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 379 | 421 | 6 | 5 |  | Initial | [11 empty] | E60 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems, including those in HT room cable trench, Unit 31 and 32 were found to be filled with a significant amount of lint and dust, which poses a serious fire risk. | Clean all cable trunking systems to remove accumulated dust and lint, ensuring that any potential fire hazards are mitigated. | 2 months | 2025-06-02 | 2025-08-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 380 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems, including those in HT room cable trench, Unit 31 and 32 were found to be filled with a significant amount of lint and dust, which poses a serious fire risk. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | E60 + 3 months | 2025-08-02 | 2025-11-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 381 | 421 | 6 | 5 |  | Initial | [11 empty] | E62 | Cabling & Wiring | Splicing of cables | Cable terminations within all panels and distribution boards were made without cable lugs, leading to broken strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 382 | 421 | 6 | 5 |  | Initial | [11 empty] | E63 | Cabling & Wiring | Splicing of cables | Cable terminations within all panels and distribution boards were made without cable lugs, leading to broken strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | E62 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 383 | 421 | 6 | 5 |  | Initial | [11 empty] | E64 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations, including Unit 31 and Accessory Store LPDBs and cable trays, where cables were either damaged or two cables were being joined together. This method of joining is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 384 | 421 | 6 | 5 |  | Initial | [11 empty] | E65 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations, including Unit 31 and Accessory Store LPDBs and cable trays, where cables were either damaged or two cables were being joined together. This method of joining is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Provide cable soldering training and equipment to staff along with heat shrink sleeves in lieu of PVC tape joints. | E64 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 385 | 421 | 6 | 5 |  | Initial | [11 empty] | E66 | Cabling & Wiring | Splicing of cables | The power cables for the drinking water cooler were improperly connected using a PVC connector and tape joint, lacking a proper on-off switch and receptacle, which could be hazard of potential short circuit due to its poor insulation. | Install a proper on-off switch and receptacle for the drinking water cooler, and replace the PVC connector with a secure, compliant electrical connections. | 2 months | 2025-06-02 | 2025-08-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 416 | 421 | 6 | 5 |  | Initial | [11 empty] | E67 | Cabling & Wiring | Splicing of cables | The power cables for the drinking water cooler were improperly connected using a PVC connector and tape joint, lacking a proper on-off switch and receptacle, which could be hazard of potential short circuit due to its poor insulation. | Replace all PVC connectors with compliant electrical junctions for secure, reliable connections and improved safety. | E66 + 3 months | 2025-08-02 | 2025-11-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 417 | 421 | 6 | 5 |  | Initial | [11 empty] | E68 | Cabling & Wiring | Splicing of cables | Power cables laying exposed on the floor in the Main LT Room, covered in polythene sheets. Covering cables with polythene sheets can trap heat, potentially leading to overheating and fire risks, compromising the safety of the installation. | Remove polythene coverings and ensure all cables are properly secured with appropriate insulation material designed for electrical cables. | 2 month | 2025-06-02 | 2025-08-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 418 | 421 | 6 | 5 |  | Initial | [11 empty] | E69 | Cabling & Wiring | Splicing of cables | Power cables laying exposed on the floor in the Main LT Room, covered in polythene sheets. Covering cables with polythene sheets can trap heat, potentially leading to overheating and fire risks, compromising the safety of the installation. | Regularly inspect and maintain electrical installations to ensure compliance and provide continuous training for staff on proper jointing techniques. | E68 + 3 months | 2025-08-02 | 2025-11-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 419 | 421 | 6 | 5 |  | Initial | [11 empty] | E70 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable color coding practices were identified, such as in distribution panels of Unit 32 and Unit 31 Extension. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 420 | 421 | 6 | 5 |  | Initial | [11 empty] | E71 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable color coding practices were identified, such as in distribution panels of Unit 32 and Unit 31 Extension. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations, and ensuring sustained safety and operational efficiency. | E70 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 421 | 421 | 6 | 5 |  | Initial | [11 empty] | E72 | Cabling & Wiring | Fixtures | Non-IP rated power receptacles were installed in locations such as near drinking water coolers and wet lab areas. Receptacles placed in unsuitable locations, like non-IP rated sockets exposed to moisture, are at higher risk of ingress and corrosion, potentially leading to electrical short circuits or fires, posing a severe safety hazard. | Relocate non-IP rated power receptacles from areas exposed to moisture, such as near drinking water coolers and wet lab areas, to dry, protected locations. For areas where receptacles are exposed to environmental elements, install suitably IP-rated power outlets to prevent ingress and ensure electrical safety. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 422 | 421 | 6 | 5 |  | Initial | [11 empty] | E73 | Cabling & Wiring | Fixtures | Non-IP rated power receptacles were installed in locations such as near drinking water coolers and wet lab areas. Receptacles placed in unsuitable locations, like non-IP rated sockets exposed to moisture, are at higher risk of ingress and corrosion, potentially leading to electrical short circuits or fires, posing a severe safety hazard. | Develop installation guidelines and training for personnel to ensure future power receptacles are installed in compliant and safe locations. | E72 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 423 | 421 | 6 | 5 |  | Initial | [11 empty] | E74 | Cabling & Wiring | Fixtures | Several power receptacles were mounted on wooden box. Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. | Replace combustible wooden ply backings with non-combustible materials to reduce fire risk. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 424 | 421 | 6 | 5 |  | Initial | [11 empty] | E75 | Cabling & Wiring | Fixtures | Several power receptacles were mounted on wooden box. Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. | Establish a facility-wide standard to use only non-combustible materials for mounting electrical components and conduct regular audits for compliance. | E74 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 425 | 421 | 6 | 5 |  | Initial | [11 empty] | E76 | Cabling & Wiring | Fixtures | Damaged receptacles were found in LT rooms and 2nd floor of Unit 31. Damaged receptacles with exposed parts can lead to lose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. | Replace or repair broken and exposed power receptacles immediately to restore safe and secure connections. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 426 | 421 | 6 | 5 |  | Initial | [11 empty] | E77 | Cabling & Wiring | Fixtures | Damaged receptacles were found in LT rooms and 2nd floor of Unit 31. Damaged receptacles with exposed parts can lead to lose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. | Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. | E76 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 427 | 421 | 6 | 5 |  | Initial | [11 empty] | E78 | Cabling & Wiring | Fixtures | In Unit 31 on the 2nd floor, one tube rod was insecurely hung from the ceiling fan hook. | Remove the insecurely hung tube rod and properly fasten it using appropriate lighting fixture to ensure safety. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 428 | 421 | 6 | 5 |  | Initial | [11 empty] | E79 | Cabling & Wiring | Fixtures | In Unit 31 on the 2nd floor, one tube rod was insecurely hung from the ceiling fan hook. | Securely fasten all tube rods using appropriate lighting fixtures and regularly inspect them to ensure ongoing safety and stability. | E78 + 3 months | 2025-07-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
28 & 29-Oct-2024
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Nishat Mills Limited (Home Textile Unit) - 5 Km Rohi Nala Rd, Nishat Avenue, Off 22 Km Ferozpur Rd. Lahore, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 28 & 29-Oct-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-04-07 | 2025-06-02 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | Escape doors are lockable in all buildings. Sliding doors serve for escape from areas with more than 10 occupants at discharge of staircase S2 level ground Unit 31 and level 2 Unit 32. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-06-02 | 2025-06-16 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | Escape doors are lockable in all buildings. Sliding doors serve for escape from areas with more than 10 occupants at discharge of staircase S2 level ground Unit 31 and level 2 Unit 32. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | Escape doors are lockable in all buildings. Sliding doors serve for escape from areas with more than 10 occupants at discharge of staircase S2 level ground Unit 31 and level 2 Unit 32. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F2 + 3 months | 2025-06-16 | 2025-09-16 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | Obstructions on escape route in Unit 31 Extension level ground. Protected stair S8 discharges inside the building at a distance from building exit. Headroom issue observed at level 3 Unit 31 machine storage area where effective headroom is reduced to 1.8m for escape. | Remove obstructions on escape routes and keep them clear for escape. Provide warning signs where headroom height is less than 2.05 m on escape routes. | 2 weeks | 2025-06-02 | 2025-06-16 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | Obstructions on escape route in Unit 31 Extension level ground. Protected stair S8 discharges inside the building at a distance from building exit. Headroom issue observed at level 3 Unit 31 machine storage area where effective headroom is reduced to 1.8m for escape. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). Propose modifications to ensure 2.05 m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Exit access | Obstructions on escape route in Unit 31 Extension level ground. Protected stair S8 discharges inside the building at a distance from building exit. Headroom issue observed at level 3 Unit 31 machine storage area where effective headroom is reduced to 1.8m for escape. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. - All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. - Implement measures to ensure adequate clear head height is achieved along all escape routes. | F6 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Travel distance | Common path of travel distances exceeds permitted limits at multiple levels in Accessory Store Building and Unit 31 Building as mentioned in tables under Building Use section 2.2 of this report. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification work on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Travel distance | Common path of travel distances exceeds permitted limits at multiple levels in Accessory Store Building and Unit 31 Building as mentioned in tables under Building Use section 2.2 of this report. | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F8 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Number of exits | Exits from level 1, 2 and 3 of Accessory Store building do not meet the remoteness criteria as the distance between the staircase is 9.5m (refer to the figures 16, 17 and 18 under Building means of egress details layouts). | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Building Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification work. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Number of exits | Exits from level 1, 2 and 3 of Accessory Store building do not meet the remoteness criteria as the distance between the staircase is 9.5m (refer to the figures 16, 17 and 18 under Building means of egress details layouts). | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Building Standard. | F10 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Protection of stairs | Unprotected openings into stairs S1, S2, S4, S5, S7, S8, S9, all levels. Doors not fire doors in staircase S1, S2, S4, S5, S6, S7, S8, S9 all levels. Fire load in stairs S1 level ground and S6 level ground. | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | 2025-06-02 | 2025-06-16 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Protection of stairs | Unprotected openings into stairs S1, S2, S4, S5, S7, S8, S9, all levels. Doors not fire doors in staircase S1, S2, S4, S5, S6, S7, S8, S9 all levels. Fire load in stairs S1 level ground and S6 level ground. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Protection of stairs | Unprotected openings into stairs S1, S2, S4, S5, S7, S8, S9, all levels. Doors not fire doors in staircase S1, S2, S4, S5, S6, S7, S8, S9 all levels. Fire load in stairs S1 level ground and S6 level ground. | all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F13 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Exit discharge | Exit discharge of Staircase S7 is blocked by gate opening inwards. Discharge routes of stairs S1, S2, S4 and S6 are not fire separated from the rest of the building. External escape route of Canteen Unit 31 ground level has unprotected opening in form of escape door of production Unit 32 ground level. | Remove obstructions on external escape routes and keep them clear for escape. | 2 weeks | 2025-06-02 | 2025-06-16 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Exit discharge | Exit discharge of Staircase S7 is blocked by gate opening inwards. Discharge routes of stairs S1, S2, S4 and S6 are not fire separated from the rest of the building. External escape route of Canteen Unit 31 ground level has unprotected opening in form of escape door of production Unit 32 ground level. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Means of Escape | Exit discharge | Exit discharge of Staircase S7 is blocked by gate opening inwards. Discharge routes of stairs S1, S2, S4 and S6 are not fire separated from the rest of the building. External escape route of canteen Unit 31 ground level has unprotected opening in form of escape door of production Unit 32 ground level. | - Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high-risk areas. | F16 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Means of Escape | Exit signage | Missing exit signs in corridors and circulation areas of all buildings. Missing exit signs in production and storage areas of all buildings. Missing exit signs in offices. Electrically powered exit signs in all buildings are not a tested and listed system. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Means of Escape | Exit signage | Missing exit signs in corridors and circulation areas of all buildings. Missing exit signs in production and storage areas of all buildings. Missing exit signs in offices. Electrically powered exit signs in all buildings are not a tested and listed system. | Ensure that all exit signage is checked periodically and in good working condition. | F18 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Separation of high-risk areas | Electrical room is not fire separated in production Unit 31 level 1. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Separation of high-risk areas | Electrical room is not fire separated in production Unit 31 level 1. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F20 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction in all buildings. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction in all buildings. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F22 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Separation of occupancies | Canteen not separated from production area at Unit 31 ground level. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification work. The drawings should cover: - Different occupancy types in the building. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of occupancies | Canteen not separated from production area at Unit 31 ground level. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F24 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Separation of occupancies | Unit 31 has bridge connections with Unit 31 Extension and Unit 32 at different levels which are not fire separated. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification work. The drawings should cover: - Occupancy types in the buildings. - Spacing between the buildings. - Proposed fire separation details (including fire rating of walls and doors.) | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Separation of occupancies | Unit 31 has bridge connections with Unit 31 Extension and Unit 32 at different levels which are not fire separated. | Provide fire rated separation between buildings as per proposal reviewed by Pakistan Accord. | F26 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 437 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Rated Construction | Floor openings | Penetrations through fire rated ceiling (multiple levels) in Unit 32 are not sealed with fire stop material. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 438 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Rated Construction | Floor openings | Penetrations through fire rated ceiling (multiple levels) in Unit 32 are not sealed with fire stop material. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F28 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 439 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Rated Construction | Storage | Storage areas in Unit 32, Unit 31 and Unit 31 Extension buildings all levels are not fire separated from the production. Storage area in Accessory Store building is not fire separated from the office at level 1. Miscellaneous storage in Unit 31 Extension level 3 exceeds permitted limit. Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above). | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification work. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 440 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Rated Construction | Storage | Storage areas in Unit 32, Unit 31, and Unit 31 Extension buildings all levels are not fire separated from the production. Storage area in Accessory Store Building is not fire separated from the office at level 1. Miscellaneous storage in Unit 31 Extension level 3 exceeds permitted limit. Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above). | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F30 + 4 months | 2025-10-02 | 2026-02-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 502 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Standpipe system | Standpipe system is required in Unit 31 and Unit 32 buildings due to height above 15m. Connection points are not compliant in all buildings. Pressure / flow is not adequate in all buildings. Missing standpipe outlets inside all stairs. | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | 2025-06-02 | 2025-10-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 503 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Suppression | Standpipe system | Standpipe system is required in Unit 31 and Unit 32 buildings due to height above 15m. Connection points are not compliant in all buildings. Pressure / flow is not adequate in all buildings. Missing standpipe outlets inside all stairs. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F32 + 1 month | 2025-10-02 | 2025-11-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 504 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Suppression | Standpipe system | Standpipe system is required in Unit 31 and Unit 32 buildings due to height above 15m. Connection points are not compliant in all buildings. Pressure / flow is not adequate in all buildings. Missing standpipe outlets inside all stairs. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F33 + 4 months | 2025-11-02 | 2026-03-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 505 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Suppression | Standpipe system | Standpipe system is required in Unit 31 and Unit 32 buildings due to height above 15m. Connection points are not compliant in all buildings. Pressure / flow is not adequate in all buildings. Missing standpipe outlets inside all stairs. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F34 + 3 months | 2026-03-02 | 2026-06-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 506 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Suppression | Standpipe system | Standpipe system is required in Unit 31 and Unit 32 buildings due to height above 15m. Connection points are not compliant in all buildings. Pressure / flow is not adequate in all buildings. Missing standpipe outlets inside all stairs. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | F35 + 3 months | 2026-06-02 | 2026-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 507 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Suppression | Standpipe system | Standpipe system is required in Unit 31 and Unit 32 buildings due to height above 15m. Connection points are not compliant in all buildings. Pressure / flow is not adequate in all buildings. Missing standpipe outlets inside all stairs. | (6). Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete. | F36 + 3 months | 2026-09-02 | 2026-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 508 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Suppression | Fire pumps | The fire pump set is not listed. | Provide electric duty pump, diesel backup fire pumps and jockey pumps, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 18 months | 2025-06-02 | 2026-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 509 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels. There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 1 month | 2025-06-02 | 2025-07-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 510 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels. There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F39 + 1 month | 2025-07-02 | 2025-08-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 511 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps. Inadequate records of maintenance of Standpipes. | - Prepare a schedule of proposed system maintenance for all life safety systems - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 512 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Pumps. Inadequate records of maintenance of Standpipes. | - Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. | F41 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 513 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps. Inadequate records of testing of Standpipes. | -Prepare a schedule of proposed system testing for all life safety systems. -Identify how systems will be tested and who is responsible. -The schedule to be submitted to Accord for review and approval. | 3 months | 2025-06-02 | 2025-09-02 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 514 | 421 | 6 | 5 |  | Initial | [11 empty] | F44 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps. Inadequate records of testing of Standpipes. | -Ensure all systems are being tested as per the schedule agreed with Accord. -Keep testing records. | F43 + 3 months | 2025-09-02 | 2025-12-02 | AGREE |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
28 & 29-Oct-2024
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Nishat Mills Limited (Home Textile Unit) - 5 Km Rohi Nala Rd, Nishat Avenue, Off 22 Km Ferozpur Rd. Lahore, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 28 & 29-Oct-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-04-07 | 2025-06-02 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Structural System | Lateral stability system | This refers to the lateral stability system of the Accessories Store, where half of the building utilizes a flat slab system, and the other half incorporates a moment frame system. Due to the inherently lower stiffness of flat slabs, their lateral load resistance is limited. Therefore, a detailed structural analysis is essential to evaluate the performance of this hybrid system under lateral loads, (gravity and wind) as per accordance with Pakistan Accord Standard. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate and submit the report to Pakistan Accord. | 3 months | 2025-05-16 | 2025-08-16 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Structural System | Lateral stability system | This refers to the lateral stability system of the Accessories Store, where half of the building utilizes a flat slab system, and the other half incorporates a moment frame system. Due to the inherently lower stiffness of flat slabs, their lateral load resistance is limited. Therefore, a detailed structural analysis is essential to evaluate the performance of this hybrid system under lateral loads, (gravity and wind) as per accordance with Pakistan Accord Standard. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 3 months | 2025-05-17 | 2025-08-17 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Structural System | Lateral stability system | This refers to the lateral stability system of the Accessories Store, where half of the building utilizes a flat slab system, and the other half incorporates a moment frame system. Due to the inherently lower stiffness of flat slabs, their lateral load resistance is limited. Therefore, a detailed structural analysis is essential to evaluate the performance of this hybrid system under lateral loads, (gravity and wind) as per accordance with Pakistan Accord Standard. | Propose strengthening work as required. | S3 + 1 month | 2025-05-18 | 2025-06-18 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Structural System | Lateral stability system | This refers to the lateral stability system of the Accessories Store, where half of the building utilizes a flat slab system, and the other half incorporates a moment frame system. Due to the inherently lower stiffness of flat slabs, their lateral load resistance is limited. Therefore, a detailed structural analysis is essential to evaluate the performance of this hybrid system under lateral loads, (gravity and wind) as per accordance with Pakistan Accord Standard. | Carry out remedial work as required. | S4+4 months | 2025-05-19 | 2025-09-19 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Other Damage/Defects | Health and Safety | There is inadequate edge protection which presents a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of services. Accessories store: No edge protection is provided at accessories store roof. | Provide adequate edge protection on the roof of accessories roof and on any other part of the factory with the same issue. | 1 month | 2025-05-20 | 2025-06-20 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Other Damage/Defects | Health and Safety | There is inadequate edge protection which present a risk of potential injury resulting from slip, trip or fall from doors during the access and maintenance of services. Unit 31 and Unit 31 Extension connecting bridge doors are provided in Unit 31 and the Unit 31 Extension connecting bridge, which open outward onto an overhang slab without any protection. | Provide adequate edge protection on the roof of accessories Store and on any other part of the factory with the same issue. | 1 month | 2025-05-21 | 2025-06-21 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Structural Documentation | Lack of safe load plans | No safe load plans were post in the factory. | Building structural engineer to review design documentation to confirm load capacity of the structures. | 6 months | 2025-05-22 | 2025-11-22 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Structural Documentation | Lack of safe load plans | No safe load plans were post in the factory. | Factory to post safe load plans on each floor. | S8 + 1 month | 2025-05-23 | 2025-06-23 | AGREE |  |  |  | In Progress

## ECategories
Eatable | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
|  | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1