## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
07-May-2025
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Yunus Textile Mills Ltd. - H-23/1, Landhi Industrial Area, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 07-May-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-11 | 2025-10-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2+1 months | 2026-01-06 | 2026-02-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but not up to date and detailed for overall facility, also there were missing necessary details such as circuit identification, cable/breaker sizes, protective devices, voltage levels, standard legends, and distribution board tags. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but not up to date and detailed for overall facility, also there were missing necessary details such as circuit identification, cable/breaker sizes, protective devices, voltage levels, standard legends, and distribution board tags. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4+1 months | 2026-04-06 | 2026-05-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory had only the fire alarm layout available, with no electrical layout drawings for small power, lighting, or containment systems. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 months | 2025-10-06 | 2026-06-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory had only the fire alarm layout available, with no electrical layout drawings for small power, lighting, or containment systems. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6+1 months | 2026-06-06 | 2026-07-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. This issue was specifically observed at the ground floor of Processing 02, Stitching Canteen ground floor, LT Room in the Power House, and Stenter Machine panel in Processing 02. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Circuit breakers | Improper mounting of circuit breaker observed at Luwa AC 1 panel in the Weaving Shed, not in accordance with standard installation practices. | Ensure proper mounting of the circuit breaker as per standard installation practices. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Circuit breakers | Single-phase connection taken from a three-phase circuit breaker at Processing 01 LT Room, which is not compliant with standard electrical practices | Ensure the use of a dedicated single-phase circuit breaker for single-phase loads to provide proper protection and maintain compliance with standards. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. This issue was observed in the Processing Lab 1st floor, Workshop, Sizing Department and Weaving distribution boards. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. This issue was observed in the Processing Lab 1st floor, Workshop, Sizing Department and Weaving distribution boards. | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Hot Spots | It was also found that the thermography report was available at the site. However, there was no summary and remediation action taken on findings. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | E12 + 6 months | 2026-04-06 | 2026-10-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | There was no earthing design and testing report available in the facility. | Design and evaluate the earthing system installation throughout the facility. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. This issue was specifically observed at the ground floor of Processing 01, Engine Hall LDB in the Power House, and industrial sockets on the first floor of the stitching area. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | Equipotential bonding for the cable trays and metallic panel covers was missing. This issue was specifically observed at the first floor stitching panel, LDB 17 in Processing 01, and HT panels in the Processing 01 LT Room. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. This issue was specifically observed at the ground floor of Processing 01, Engine Hall LDB in the Power House, and industrial sockets on the first floor of the stitching area. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E16 + 6 months | 2026-04-06 | 2026-10-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. This was observed at bore pump supply near Guest House. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. This was observed at panel behind Guest House. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | There were visible signs of damage to panels, cables, and busbars. This issue was specifically observed at the ground floor of Processing 01 and the compressor panel on the ground floor of Processing 02. | Ensure all equipment is installed in accordance with manufacturer guidelines, including proper placement, ventilation, and accessibility for safe and reliable operation. | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical panel mounted on inappropriate support near Guest House building and at the ground floor of the processing building, posing safety and stability concerns. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical panel mounted on inappropriate support near Guest House building and at the ground floor of the processing building, posing safety and stability concerns. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E21 + 6 months | 2026-01-06 | 2026-07-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Loop Connection | In these loop connections, one circuit breaker is energised by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. This issue was specifically observed at the LDB and Processing Panel on the ground floor of Processing 01, G9 Warehouse Main Electric Panel, MLTP 01 Warping Panel, and PDB 14 Workshop Electric Panel. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Multiple connections | In these cases, multiple circuits were being protected by a single circuit breaker. This issue was specifically observed at the ground floor Stitching Canteen, maintenance Workshop Office in Processing 01, lab at ground floor Processing 02, first floor Stitching Building, LT panel in the Power House, and in the weaving section. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Openings | Unsealed openings were discovered in cable trays. The front doors on a number of panels had been removed at power factor improvement (PFI) plant in LT Room. This issue was specifically observed at the cable trays on the first floor of Processing 02 and the PFI panel in the LT Room of the Power House. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Openings | Unsealed openings were discovered in cable trays. The front doors on a number of panels had been removed at power factor improvement (PFI) plant in LT Room. This issue was specifically observed at the cable trays on the first floor of Processing 02 and the PFI panel in the LT Room of the Power House. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | E25 + 3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Adequate accessibility | At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. In several instances, the placement of electrical panels adjacent to machines that continuously reject heat has caused the surrounding temperature to exceed ambient levels by several degrees. This temperature rise further increases the temperature of the panels and boards nearby. This issue was specifically observed at the distribution board in ground floor Processing 02, LDB 06 in Processing 01, LDB at ground floor Processing 01, and control panels in Processing 01. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no study available to confirm its adequacy. | If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). | E28 + 6 months | 2025-12-06 | 2026-06-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at the ground floor of Processing 02 and the LT panel in the Power House Building. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. This issue was specifically observed at the ground floor of Processing 02 and the LT panel in the Power House Building. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E30 + 6 months | 2025-11-06 | 2026-05-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. There were eight fire alarm panels installed, divided block-wise from Block A to Block H. However, the fire alarm system exhibits several major deficiencies, including the use of conventional panels and non-fire-rated cabling, which compromises system integrity during fire conditions. Detector coverage was missing or insufficient in several critical areas, including Processing 02 offices, Power House, Stitching Building Office, and G9 Warehouse. Additionally, some detectors were found removed, and large spaces like the LT Room were inadequately covered. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 2 weeks | 2025-10-06 | 2025-10-20 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | This relates to the entire facility. (1) Submit design documentation for new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E33 + 1 month | 2026-01-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E34 + 4 months | 2026-02-06 | 2026-06-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E35 +5 months | 2026-06-06 | 2026-11-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E36 +3 months | 2026-11-06 | 2027-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant fire alarm system found installed in the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E37 + 3 months | 2027-02-06 | 2027-05-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Fire Alarm & Detection System (FADS) | Maintenance records | The following observations were made with regards to testing and maintenance: i. Routine testing of the Fire Alarm and Detection System (FADS) has not been performed consistently. ii. The testing and maintenance of the Fire Alarm and Detection System (FADS) have not been conducted in accordance with the requirements specified in Chapter 14 of NFPA 72. | Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | General & Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations. This issue was observed at ground floor Processing 02. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | General & Emergency Lighting | Provided but non-functional | During the inspection it was observed that emergency lighting was provided but not functional in a number of locations. This issue was observed at ground floor Processing 02. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | General & Emergency Lighting | Provided but insufficient | Several areas lack sufficient emergency lighting coverage. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | General & Emergency Lighting | Provided but insufficient | The backup power supply to the emergency luminaires is insufficient. | Upgrade the backup power supply to ensure it can adequately support all emergency luminaires during a power failure. This includes installing additional battery packs or generators as necessary to comply with the Building Code of Pakistan Fire Safety Provisions 2016. | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | General & Emergency Lighting | Provided but insufficient | During the inspection the emergency lighting arrangement throughout the facility was assessed. i. Several areas lack sufficient emergency lighting coverage. ii. The backup power supply to the emergency luminaires is insufficient. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | General & Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Proper circuitry is crucial to ensure that emergency lighting is automatically activated when general lighting fails. This automatic activation is essential for maintaining sufficient illumination, allowing for the safe evacuation of occupants and preventing panic during power outages. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | General & Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Proper circuitry is crucial to ensure that emergency lighting is automatically activated when general lighting fails. This automatic activation is essential for maintaining sufficient illumination, allowing for the safe evacuation of occupants and preventing panic during power outages. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer areas. This issue was specifically observed at transformer and HT Room in Power House. | Redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the generator and transformer receive adequate ventilation. This might involve repositioning vents or adding ductwork. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | Several sections of the room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. This issue was specifically observed at transformer and HT Room in Power House. | Add more lighting fixtures in poorly lit areas to ensure even distribution of light throughout the room. Focus on areas that require the highest visibility, such as around equipment and control panels. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | An assessment of the existing ventilation system was conducted, alongside an evaluation of the lighting setup in various parts of the room, to determine their compliance with recommended standards. i. The ventilation system was inadequate, with insufficient airflow leading to heat accumulation, particularly around the generator and transformer areas. ii. Several sections of the room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | Establish regular maintenance and testing of the ventilation system and luminaires within the spaces to ensure adequate performance. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Generator, Transformer & Sub-Station Room | Room separation | The physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. It was observed that the separation between HT/LT Room in Processing 01, Transformer and HT Panel in the Power House Building was inadequate. | Install temporary fire-resistant barriers and seal any gaps and openings between the HT/LT and transformer immediately reduce the risk of fire and electrical fault propagation. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Generator, Transformer & Sub-Station Room | Room separation | The physical separation between these critical areas was assessed. The barriers, walls, and partitions designed to isolate each component were examined to ensure they met safety standards and provided adequate separation. It was observed that the separation between HT/LT Room in Processing 01, Transformer and HT Panel in the Power House Building was inadequate. | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Generator, Transformer & Sub-Station Room | Battery | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. This issue was observed at Generator Room in the Power House. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Generator, Transformer & Sub-Station Room | Battery | Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. This issue was observed at Generator Room in the Power House. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Generator, Transformer & Sub-Station Room | Battery | The placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. This issue was observed at mechanical Workshop near Processing 02. | Reposition batteries that are improperly placed to ensure they comply with safety regulations, allowing for safe access and adequate ventilation. Mark and clear pathways around battery installations to ensure easy and safe access for maintenance and emergencies. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Generator, Transformer & Sub-Station Room | Battery | The placement of some batteries did not comply with safety regulations, potentially hindering safe access and proper ventilation. This issue was observed at mechanical Workshop near Processing 02. | Conduct regular audits of battery placements to ensure ongoing compliance with safety standards and regulations. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Cabling & Wiring | Cable support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 4 months | 2025-10-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Cabling & Wiring | Cable support and protection | Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Cabling & Wiring | Cable support and protection | Damaged cable containment was observed near the gas room behind the Guest House, posing a potential electrical and fire hazard due to its proximity to flammable areas. | Replace or repair the damaged cable containment with a properly rated and enclosed system, ensuring adequate mechanical protection and separation from flammable zones in accordance with electrical safety standards. | 4 months | 2025-10-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Cable support and protection | Damaged cable containment was observed near the gas room behind the Guest House, posing a potential electrical and fire hazard due to its proximity to flammable areas. | Ensure electrical safety by replacing all damaged cable containment with secure, compliant, and fire-rated solutions to minimize potential hazards. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 370 | 421 | 6 | 5 |  | Initial | [11 empty] | E60 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at the cable trench below the LT Room and Generator Room in the Power House, as well as at the cable trays in Processing 02. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 2 months | 2025-10-06 | 2025-12-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 371 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed at the cable trench below the LT Room and Generator Room in the Power House, as well as at the cable trays in Processing 02. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E62 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was specifically observed at the first floor of Processing 02, LDB Power House, and first floor Stitching Areas. | install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | 2025-10-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E63 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was specifically observed at the first floor of Processing 02, LDB Power House, and first floor Stitching Areas. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 374 | 421 | 6 | 5 |  | Initial | [11 empty] | E64 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed at the weaving section, processing department, Processing 02 department, and sizing exhaust fan panel in the Weaving Section. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | 2025-10-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 375 | 421 | 6 | 5 |  | Initial | [11 empty] | E65 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed at the weaving section, processing department, Processing 02 department, and sizing exhaust fan panel in the Weaving Section. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 376 | 421 | 6 | 5 |  | Initial | [11 empty] | E66 | Cabling & Wiring | Splicing of cables | Machine power wires were inserted directly into power receptacles without a power plug. This practice is highly dangerous as it can lead to loose connections, electrical shocks, and short circuits. Direct insertion bypasses proper safety mechanisms, significantly increasing the risk of fire and electrical hazards, thereby endangering life safety. This issue was specifically observed at the Mechanical Workshop near Processing 02 and the first floor the Digital Printing Area. | Replace the directly inserted power wires with proper power plugs to ensure safe and secure connections. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 377 | 421 | 6 | 5 |  | Initial | [11 empty] | E67 | Cabling & Wiring | Splicing of cables | Machine power wires were inserted directly into power receptacles without a power plug. This practice is highly dangerous as it can lead to loose connections, electrical shocks, and short circuits. Direct insertion bypasses proper safety mechanisms, significantly increasing the risk of fire and electrical hazards, thereby endangering life safety. This issue was specifically observed at the Mechanical Workshop near Processing 02 and the first floor the Digital Printing Area. | Develop and enforce a facility-wide electrical safety protocol that mandates the use of power plugs for all equipment. Conduct regular safety audits and provide training sessions to staff to reinforce the importance of using proper power plugs and adherence to electrical safety standards | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 378 | 421 | 6 | 5 |  | Initial | [11 empty] | E68 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was specifically observed at the first floor of Building 02, LDB 4 in the Weaving Building, and in the first floor of the Stitching Area. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 379 | 421 | 6 | 5 |  | Initial | [11 empty] | E69 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. This issue was specifically observed at the first floor of Building 02, LDB 4 in the Weaving Building, and in the first floor of the Stitching Area. | Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 380 | 421 | 6 | 5 |  | Initial | [11 empty] | E70 | Cabling & Wiring | Fixtures | Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was specifically observed at the LT Room and the first floor of the Stitching Area. | Replace combustible wooden ply backings with non-combustible materials to reduce fire risk. | 4 months | 2025-10-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 381 | 421 | 6 | 5 |  | Initial | [11 empty] | E71 | Cabling & Wiring | Fixtures | Power receptacles mounted on combustible wooden ply: Installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety. This issue was specifically observed at the LT Room and the first floor of the Stitching Area. | Establish a facility-wide standard to use only non-combustible materials for mounting electrical components, and conduct regular audits for compliance. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 382 | 421 | 6 | 5 |  | Initial | [11 empty] | E72 | Cabling & Wiring | Fixtures | Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. This issue was specifically observed on the ground floor of Processing 02 and the Generator Room in the Power House. | Replace or repair broken and exposed power receptacles immediately to restore safe and secure connections. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 383 | 421 | 6 | 5 |  | Initial | [11 empty] | E73 | Cabling & Wiring | Fixtures | Broken and exposed power receptacles: Damaged receptacles with exposed parts can lead to loose connections and increased electrical resistance. This condition can cause overheating, potentially igniting surrounding materials and increasing the risk of electrical fires, posing a serious life safety threat. This issue was specifically observed on the ground floor of Processing 02 and the Generator Room in the Power House. | Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components to maintain safety standards. iii. Ensure proper and secure mounting of all electrical equipment as per manufacturer guidelines and standard installation practices. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 384 | 421 | 6 | 5 |  | Initial | [11 empty] | E74 | Cabling & Wiring | Fixtures | Inappropriately mounted fixture above the VFD panel at the ground floor of Processing 02, and improper VFD mounting at the Mercerize 2 panel in Processing, potentially affecting equipment safety and performance. | Ensure all fixtures and VFDs are securely and properly mounted in accordance with manufacturer guidelines and standard electrical installation practices. | 4 months | 2025-10-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 385 | 421 | 6 | 5 |  | Initial | [11 empty] | E75 | Cabling & Wiring | Fixtures | Inappropriately mounted fixture above the VFD panel at the ground floor of Processing 02, and improper VFD mounting at the Mercerize 2 Panel in Processing, potentially affecting equipment safety and performance. | Ensure proper and secure mounting of all electrical equipment as per manufacturer guidelines and standard installation practices. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 416 | 421 | 6 | 5 |  | Initial | [11 empty] | E76 | Cabling & Wiring | Fixtures | A damaged power receptacle was observed, which poses risks of electric shock, short circuit, or potential fire hazards due to exposed or weakened connections. | Replace the damaged power receptacle with a compliant, enclosed, and properly rated unit in accordance with standard electrical safety codes. | 4 months | 2025-10-06 | 2026-02-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 417 | 421 | 6 | 5 |  | Initial | [11 empty] | E77 | Cabling & Wiring | Fixtures | A damaged power receptacle was observed, which poses risks of electric shock, short circuit, or potential fire hazards due to exposed or weakened connections. | Conduct a facility-wide inspection of all power receptacles and sockets, replace any additional defective units, and implement a periodic maintenance schedule to prevent future occurrences. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [13 empty] | Yunus Textile Mills Ltd. - H-23/1, Landhi Industrial Area, Karachi, Sindh, Pakistan
Date of Initial Inspection
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-11 | 2025-10-06 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Escape doors | Escape doors across the facility are lockable. - Escape doors are found locked at entry into staircase S33 at level 1. - Doors serving areas with over 50 occupants swing against the direction of escape at Stitching Building Canteen exit south side, Weaving Building ground level majority of the escape doors swinging against the direction of escape. - Doors swing against the direction of escape at Weaving Building door connecting sizing ground level and Weaving Shed 1 (this door is used for escape from both sides as part of egress strategy). - Sliding doors serve for escape from areas with more than 10 occupants at entry into staircase S33 at level 1, S34 level 1, S12 level 1, at ground level Waterjet Building, Processing 2 level 3, Processing 2 S18 discharge door sliding, Processing 2 Workshop sliding door, Guest House Building sliding mess area ground and Conference Room level 1. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-10-06 | 2025-10-20 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Escape doors | Escape doors across the facility are lockable. - Escape doors are found locked at entry into staircase S33 at level 1. - Doors serving areas with over 50 occupants swing against the direction of escape at Stitching Building Canteen exit south side, Weaving Building ground level majority of the escape doors swinging against the direction of escape. - Doors swing against the direction of escape at Weaving Building door connecting sizing ground level and Weaving Shed 1 (this door is used for escape from both sides as part of egress strategy). - Sliding doors serve for escape from areas with more than 10 occupants at entry into staircase S33 at level 1, S34 level 1, S12 level 1, at ground level Waterjet Building, Processing 2 level 3, Processing 2 S18 discharge door sliding, Processing 2 Workshop sliding door, Guest House Building sliding mess area ground and Conference Room level 1. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | 2025-10-06 | 2026-01-06 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Escape doors | Escape doors across the facility are lockable. - Escape doors are found locked at entry into staircase S33 at level 1. - Doors serving areas with over 50 occupants swing against the direction of escape at Stitching Building Canteen exit south side, Weaving Building ground level majority of the escape doors swinging against the direction of escape. - Doors swing against the direction of escape at Weaving Building door connecting sizing ground level and Weaving Shed 1 (this door is used for escape from both sides as part of egress strategy). - Sliding doors serve for escape from areas with more than 10 occupants at entry into staircase S33 at level 1, S34 level 1, S12 level 1, at ground level Waterjet Building, Processing 2 level 3, Processing 2 S18 discharge door sliding, Processing 2 Workshop sliding door, Guest House Building sliding mess area ground and Conference Room level 1. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3+3 months | 2026-01-06 | 2026-04-06 |  |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Exit access | Obstructions on escape route at: a. Escape passage for entry into staircase S2 Processing 1 Building level 1 is blocked. b. Exit access is blocked at Weaving roof (level 2). c. Commercial planning office Processing 1 Building level 1 exit access restricted to 0.4m. d. Obstruction towards S13 Processing 1 level 1. Trip hazards on escape route at: a. Level 1 Processing 1 staircase S6. b. At S36 stairs entrance at level 1 Weaving Building. c. At entry into stair S10 al level 1. d. At exit access level 3 Processing 2 Building. - Protected stair S1, S4, S5, S12, S13, S14, S16, S20, S31, S33, S34, S35, S37 discharges inside the building at a distance from building exit. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) at entry into S11 Processing 1 Building which is 1.9m, at entry into S18 Processing 1 Building which is 1.8m. | Remove obstructions and trip hazards on escape routes and keep them clear for escape. Provide warning signs where headroom height is less than 2.05 m on escape routes. | 2 weeks | 2025-10-06 | 2025-10-20 |  |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Exit access | Obstructions on escape route at: a. Escape passage for entry into staircase S2 Processing 1 Building level 1 is blocked. b. Exit access is blocked at Weaving roof (level 2). c. Commercial planning office Processing 1 Building level 1 exit access restricted to 0.4m. d. Obstruction towards S13 Processing 1 level 1. Trip hazards on escape route at: a. Level 1 Processing 1 staircase S6. b. At S36 stairs entrance at level 1 Weaving Building. c. At entry into stair S10 al level 1. d. At exit access level 3 Processing 2 Building. - Protected stair S1, S4, S5, S12, S13, S14, S16, S20, S31, S33, S34, S35, S37 discharges inside the building at a distance from building exit. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) at entry into S11 Processing 1 Building which is 1.9m, at entry into S18 Processing 1 Building which is 1.8m. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Exit access | Obstructions on escape route at: a. Escape passage for entry into staircase S2 Processing 1 Building level 1 is blocked. b. Exit access is blocked at Weaving roof (level 2). c. Commercial planning office Processing 1 Building level 1 exit access restricted to 0.4m. d. Obstruction towards S13 Processing 1 level 1. Trip hazards on escape route at: a. Level 1 Processing 1 staircase S6. b. At S36 stairs entrance at level 1 Weaving Building. c. At entry into stair S10 al level 1. d. At exit access level 3 Processing 2 Building. - Protected stair S1, S4, S5, S12, S13, S14, S16, S20, S31, S33, S34, S35, S37 discharges inside the building at a distance from building exit. - Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) at entry into S11 Processing 1 Building which is 1.9m, at entry into S18 Processing 1 Building which is 1.8m. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. Implement measures to ensure adequate clear head height is achieved along all escape routes. | F6+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Travel distance | Common path of travel distances (CPT) exceed permitted limits at (for details refer to the layouts in the section Building Means of Egress Details): a. Head Office Building level ground with a CPT of 30m. b. Processing 1 Building level 1 Marketing Office with a CPT of 53m due to the non availability of staircase S9 as this staircase takes occupants to evacuate through the roof. c. Processing 1 Building level 1 TD office block with a CPT of 25m. d. Processing 1 Building level Engraving Department with a CPT of 33m. e. Processing 2 Building has CPT of 33m on all upper levels above ground, f. Weaving Building level ground has CPT at multiple locations with distance of 38m, 40m, 58m, 30m, 40m, 57m, 25m. g. Weaving Building level 2 has a CPT of 29m. h. Waterjet Building level ground has CPT of 49m at two different locations in Waterjet and Warping areas and 37m, 27m CPT at G9 Storage Area. i. Masjid Building has CPT of 27m at level 1 and 26m at level 2/roof. j. Stitching Building level 1 has CPT at multiple locations including 45m at stitching area near S30, 39m at Warehouse 2A, and 25m at Warehouse 2B. Alternative Travel distance (ATD) to the nearest of alternative exits exceeds distance limits at (for details refer to the layouts in the section Building Means of Egress Details): a. Processing 1 Building level ground with ATD of 76m (this issue is observed at complete level ground at multiple locations). b. Processing 1 Building level 1 John department with ATD of 71m. c. Processing 2 Building has ATD of 75m on all levels (on levels 1 to 3 its is mainly because of the staircase S19a not meeting minimum requirements for egress as the stair width is 0.6m). d. Weaving Building level ground has ATD of 109m and 86m. e. Waterjet Building level ground has ATD of 63m. f. Stitching Building level ground has ATD of 67m at Fabric Warehouse. | Reduce the common path of travel distance to a maximum of 46 m in the areas with higher common path of travel or vacate the area until the travel distance is reduced. | 2 weeks | 2025-10-06 | 2025-10-20 |  |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Travel distance | Common path of travel distances (CPT) exceed permitted limits at (for details refer to the layouts in the section Building Means of Egress Details): a. Head Office Building level ground with a CPT of 30m. b. Processing 1 Building level 1 Marketing Office with a CPT of 53m due to the non availability of staircase S9 as this staircase takes occupants to evacuate through the roof. c. Processing 1 Building level 1 TD office block with a CPT of 25m. d. Processing 1 Building level Engraving Department with a CPT of 33m. e. Processing 2 Building has CPT of 33m on all upper levels above ground, f. Weaving Building level ground has CPT at multiple locations with distance of 38m, 40m, 58m, 30m, 40m, 57m, 25m. g. Weaving Building level 2 has a CPT of 29m. h. Waterjet Building level ground has CPT of 49m at two different locations in Waterjet and Warping areas and 37m, 27m CPT at G9 Storage Area. i. Masjid Building has CPT of 27m at level 1 and 26m at level 2/roof. j. Stitching Building level 1 has CPT at multiple locations including 45m at stitching area near S30, 39m at Warehouse 2A, and 25m at Warehouse 2B. Alternative Travel distance (ATD) to the nearest of alternative exits exceeds distance limits at (for details refer to the layouts in the section Building Means of Egress Details): a. Processing 1 Building level ground with ATD of 76m (this issue is observed at complete level ground at multiple locations). b. Processing 1 Building level 1 John department with ATD of 71m. c. Processing 2 Building has ATD of 75m on all levels (on levels 1 to 3 its is mainly because of the staircase S19a not meeting minimum requirements for egress as the stair width is 0.6m). d. Weaving Building level ground has ATD of 109m and 86m. e. Waterjet Building level ground has ATD of 63m. f. Stitching Building level ground has ATD of 67m at Fabric Warehouse. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification work on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Travel distance | Common path of travel distances (CPT) exceed permitted limits at (for details refer to the layouts in the section Building Means of Egress Details): a. Head Office building level ground with a CPT of 30m. b. Processing 1 Building level 1 Marketing office wit CPT of 53m due to the non availability of staircase S9 as this staircase takes occupants to evacuate through the roof. c. Processing 1 Building level 1 TD office block with a CPT of 25m. d. Processing 1 Building level Engraving department with a CPT of 33m. e. Processing 2 Building has CPT of 33m on all upper levels above ground. f. Weaving Building level ground has CPT at multiple locations with distance of 38m, 40m, 58m, 30m, 40m, 57m, 25m. g. Weaving Building level 2 has a CPT of 29m. h. Waterjet Building level ground has CPT of 49m at two different locations in Waterjet and Warping areas and 37m, 27m CPT at G9 storage area. i. Masjid Building has CPT of 27m at level 1 and 26m at level 2/roof. j. Stitching Building level 1 has CPT at multiple locations including 45m at stitching area near S30, 39m at Warehouse 2A, and 25m at Warehouse 2B. Alternative Travel distance (ATD) to the nearest of alternative exits exceeds distance limits at (for details refer to the layouts in the section Building Means of Egress Details): a. Processing 1 Building level ground with ATD of 76m (this issue is observed at complete level ground at multiple locations). b. Processing 1 Building level 1 John Department with ATD of 71m. c. Processing 2 Building has ATD of 75m on all levels (on levels 1 to 3 its is mainly because of the staircase S19a not meeting minimum requirements for egress as the stair width is 0.6m), d. Weaving Building level ground has ATD of 109m and 86m. f. Waterjet Building level ground has ATD of 63m. g. Stitching Building level ground has ATD of 67m at Fabric Warehouse. | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | F9+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Number of exits | Exits converge in a single point of failure at: - Fabric Godown Waterjet Building, Weaving Building level ground Yarn Godown. - Single exit from roof of Masjid Building. | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification work. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Number of exits | - Exits converge in a single point of failure at Fabric godown Waterjet Building, Weaving Building level ground Yarn Godown. - Single exit from roof of Masjid Building. | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Standard. | F11+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Protection of stairs | - Unprotected openings into stairs S1, S3, S2, S4, S5, S6, S8, S10, S11, S12, S15, S17, S21, S22, S25, S27, S28, S29, S30, S32, S33, S34, S35, S36, S37. - Missing fire rated enclosure and fire doors in stair S2, S14, S16, S20, S26, S31. - Fire doors propped open at S35 level 1, S18 & S19 all levels. - Doors not fire doors at staircase S1, S3, S2, S4, S5, S6, S7, S13, S17, S21, S22, S24, S25, S29, S30, S32, S33, S34, S35, S36, S37. - Non listed fire doors at S27. - Fire load in stairs S5, S6, S7, S12, S18, S19, S28. - Stair S9 discharging into a roof. - Services passing through or within stairs S1 level ground, S36 level 1. | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | 2025-10-06 | 2025-10-20 |  |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Protection of stairs | - Unprotected openings into stairs S1, S3, S2, S4, S5, S6, S8, S10, S11, S12, S15, S17, S21, S22, S25, S27, S28, S29, S30, S32, S33, S34, S35, S36, S37. - Missing fire rated enclosure and fire doors in stair S2, S14, S16, S20, S26, S31. - Fire doors propped open at S35 level 1, S18 & S19 all levels. - Doors not fire doors at staircase S1, S3, S2, S4, S5, S6, S7, S13, S17, S21, S22, S24, S25, S29, S30, S32, S33, S34, S35, S36, S37. - Non listed fire doors at S27. - Fire load in stairs S5, S6, S7, S12, S18, S19, S28. - Stair S9 discharging into a roof. - Services passing through or within stairs S1 level ground, S36 level 1. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification work. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Protection of stairs | - Unprotected openings into stairs S1, S3, S2, S4, S5, S6, S8, S10, S11, S12, S15, S17, S21, S22, S25, S27, S28, S29, S30, S32, S33, S34, S35, S36, S37. - Missing fire rated enclosure and fire doors in stair S2, S14, S16, S20, S26, S31. - Fire doors propped open at S35 level 1, S18 & S19 all levels. - Doors not fire doors at staircase S1, S3, S2, S4, S5, S6, S7, S13, S17, S21, S22, S24, S25, S29, S30, S32, S33, S34, S35, S36, S37. - Non listed fire doors at S27. - Fire load in stairs S5, S6, S7, S12, S18, S19, S28. - Stair S9 discharging into a roof. - Services passing through or within stairs S1 level ground, S36 level 1. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F14+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Escape stair condition | - There are missing handrails in S7, S12. - Obstacles in stairs S35 at level 1. - T read depth in S12, S15 and S17 (external steel structure staircase) is less than the minimum required. | Remove all obstructions from staircase. | 2 weeks | 2025-10-06 | 2025-10-20 |  |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Means of Escape | Escape stair condition | - There are missing handrails in S7, S12. - Obstacles in stairs S35 at level 1. - T read depth in S12, S15 and S17 (external steel structure staircase) is less than the minimum required. | Ensure the following are provided: - Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. - Tread depth to meet the minimum requirements of BCP. | 3 months | 2025-10-06 | 2026-01-06 |  |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Means of Escape | Exit discharge | - Exit discharge from Weaving Building Z32 at ground floor is obstructed by truck parking and second exit from Weaving Building Yarn Godown at ground is also blocked by storage. - Discharge route of Processing 1 near S6 has open storage and passage blocked. - North exit discharge of processing 1 has chemical storage and obstructed passage which reduces the passage and the effective minimum width required on discharge route is not achieved. | Remove obstructions on external escape routes and keep them clear for escape. | 2 weeks | 2025-10-06 | 2025-10-20 |  |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs S2 level 1, S16. - Missing exit signs in circulation areas of production across the facility. - Missing exit signs in multiple office areas including marketing office and design studio at Processing 1 Building, Head Office Building, and Guest House Building. - Exit signage across the facility is not uniform in terms of colour and size. - Exit signs are misleading at sizing to warping production area at ground floor, at weaving shed 1 from chiller area in chiller plant room (signage taking occupants to plant room). - Exit sign is misleading at marketing office S9 where it is taking the occupants to roof. - Electrically powered exit signs are not a tested and listed system. | Remove misleading directional escape signs. | 2 weeks | 2025-10-06 | 2025-10-20 |  |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs S2 level 1, S16. - Missing exit signs in circulation areas of production across the facility. - Missing exit signs in multiple office areas including marketing office and design studio at Processing 1 Building, Head Office Building, and Guest House Building. - Exit signage across the facility is not uniform in terms of colour and size. - Exit signs are misleading at sizing to warping production area at ground floor, at weaving shed 1 from chiller area in chiller plant room (signage taking occupants to plant room). - Exit sign is misleading at marketing office S9 where it is taking the occupants to roof. - Electrically powered exit signs are not a tested and listed system. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-10-06 | 2026-01-06 |  |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Means of Escape | Exit signage | - Missing exit signs at entry into stairs S2 level 1, S16. - Missing exit signs in circulation areas of production across the facility. - Missing exit signs in multiple office areas including marketing office and design studio at Processing 1 Building, Head Office Building, and Guest House Building. - Exit signage across the facility is not uniform in terms of colour and size. - Exit signs are misleading at sizing to warping production area at ground floor, at weaving shed 1 from chiller area in chiller plant room (signage taking occupants to plant room). - Exit sign is misleading at marketing office S9 where it is taking the occupants to roof. - Electrically powered exit signs are not a tested and listed system. | Ensure that all exit signage is checked periodically and in good working condition. | F20+3 months | 2026-01-06 | 2026-04-06 |  |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Separation of high-risk areas | - Electrical room is adjacent to Generator Room and is not fire separated in Weaving Building. - Electrical panel alongside tender machine not fire separated at Processing 1 ground level. - Cooking area is not fire separated from dining areas at Weaving and Stitching Buildings Canteens. - Chiller plant to Weaving Loom Shed 1 are not fire separated at ground level Weaving Building. - Processing 2 level 2 and level 1 electrical room, not fire separated from production. - Fire pump not fire separated from electrical panels, chiller area and domestic water pumps, chiller area. - LT Room from production in Weaving Building level ground at multiple locations including near the power house. - Control Room/LT Room is not fire separated from generators in power house Weaving Building level ground. - Processing 2 ground level workshop is not fire separated from production. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Separation of high-risk areas | - Electrical room is adjacent to Generator Room and is not fire separated in Weaving Building. - Electrical panel alongside tender machine not fire separated at Processing 1 ground level. - Cooking area is not fire separated from dining areas at Weaving and Stitching Buildings Canteens. - Chiller plant to Weaving Loom Shed 1 are not fire separated at ground level Weaving Building. - Processing 2 level 2 and level 1 electrical room, not fire separated from production. - Fire pump not fire separated from electrical panels, chiller area and domestic water pumps, chiller area. - LT Room from production in Weaving Building level ground at multiple locations including near the power house. - Control Room/LT Room is not fire separated from generators in power house Weaving Building level ground. - Processing 2 ground level workshop is not fire separated from production. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F22+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Separation of shafts | - Lift shafts are not separated with fire rated construction across the facility. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Separation of shafts | - Lift shafts are not separated with fire rated construction across the facility. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F24+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Floor openings | - Open voids are connecting different levels at ground level Weaving Building, -Cone rewinding area Weaving Building has a non fire rated duct passing through the slab, Processing 1 engraving screen area floor opening from processing area on ground level, Head Office Building central lobby floor opening, Guest House Building central lobby floor opening. - Fire rated slab openings which are not fire separated at, Greige Fabric storage Weaving Building, at cone rewinding area ground to level 1 conduit piercing through the ceiling. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of floor openings. - Proposed fire separation details (including fire rating of walls and doors). | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Floor openings | - Open voids connecting different levels at ground level Weaving Building, cone rewinding area Weaving Building where a non fire rated duct is passing through the slab, Processing 1 engraving screen area floor opening from processing area on ground level, Head office building central lobby floor opening, Guest House Building central lobby floor opening. - Fire rated slab openings which are not fire separated at, greige fabric storage Weaving Building, at cone rewinding area ground to level 1 conduit piercing through the ceiling. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F26+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building in Processing 1, Processing 2, Weaving, Waterjet and Stitching Buildings at multiple levels. Some of the examples include: a. Processing 1 Processing Store sampling not fire separated from office area and production, Fabric Storage Area from production, Storage not fire separated from production at John Department level 1, b. Weaving Building Grey fabric storage area is not fire separated from production at level 1 and Yarn Godown is not fire separated from production at ground. c. Waterjet Building Fabric Godowns in is not fire separated from production. d. Stitching Building level 1 Warehouse and sub store from production. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) at Stitching Building level 1 miscellaneous storage not organised in 23 sq m. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification work. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building in Processing 1, Processing 2, Weaving, Waterjet and Stitching Buildings at multiple levels. Some of the examples include: a. Processing 1 Processing Store sampling not fire separated from office area and production, Fabric Storage Area from production, Storage not fire separated from production at John Department level 1, b. Weaving Building Grey fabric storage area is not fire separated from production at level 1 and Yarn Godown is not fire separated from production at ground. c. Waterjet Building Fabric Godowns in is not fire separated from production. d. Stitching Building level 1 Warehouse and sub store from production. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) at Stitching Building level 1 miscellaneous storage not organised in 23 sq m. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F28+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided in Processing 2 Building where he height of the building measured from fire department access to the top most occupied floor is more than 18.3m. | (1) Submit design documentation for a sprinkler system (along with required standpipe system) and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certification of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided in Processing 2 Building where he height of the building measured from fire department access to the top most occupied floor is more than 18.3m. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F30+1 month | 2026-02-06 | 2026-03-06 |  |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided in Processing 2 Building where he height of the building measured from fire department access to the top most occupied floor is more than 18.3m. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F31+3 months | 2026-03-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided in Processing 2 Building where he height of the building measured from fire department access to the top most occupied floor is more than 18.3m. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F32+3 months | 2026-06-06 | 2026-09-06 |  |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided in Processing 2 Building where he height of the building measured from fire department access to the top most occupied floor is more than 18.3m. | (5) Factory to advise Pakistan Accord when SUPS installation is fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | F33+3 months | 2026-09-06 | 2026-12-06 |  |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided in Processing 2 Building where he height of the building measured from fire department access to the top most occupied floor is more than 18.3m. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete. | F34+4 months=18 months | 2026-12-06 | Invalid |  |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Fire Suppression | Standpipe system | Standpipe system is required in Processing 1, Processing 2, and Weaving Buildings where all three have fire floor area more than 2325 sq m andnumber of stories are more than 2. - Missing standpipe outlets in protected staircase in all three buildings. - Standpipe system comprise of non listed products and the coverage of the system is not sufficient in all buildings. | Provide full testing and commissioning (T&C) certification from the system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the system will be complete by following the steps (1) to (6) above. | 18 months | 2025-10-06 | 2027-04-06 |  |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Fire Suppression | Fire pumps | - There are four locations at which fire pumps are installed. All Fire pump sets are non listed, excluding fire pump 4 (only diesel engine pump) which is listed. - Fire pumps do not start automatically. - All fire pumps are installed with negative suction arrangement. - Fire pumps 1, 2 & 3 are not in fire separated rooms. | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following the steps (1) to (6) above. | 18 months | 2025-10-06 | 2027-04-06 |  |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Fire Suppression | Fire extinguishers | - Insufficient coverage of fire extinguishers in Stitching Building. - Poor condition of fire extinguishers at few of the locations including near Guest House Building. | Ensure that all building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 2 months | 2025-10-06 | 2025-12-06 |  |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Suppression | Fire extinguishers | - Insufficient coverage of fire extinguishers in Stitching Building. - Poor condition of fire extinguishers at few of the locations including near Guest House Building. | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | F38+2 months | 2025-12-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Hazardous Materials | Chemicals handling | - Large amounts of chemicals in production areas at Processing 1 level ground jigar machine area. | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Hazardous Materials | Chemicals handling | - Large amounts of chemicals in production areas at Processing 1 level ground jigar machine area. | Implement the chemical handling strategy on site as agreed with Accord. | F40+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room at Processing 1 Building level ground, Stitching Building level ground, Processing 2 Building level 2, west side of Masjid Building in discharge route, Weaving Building level ground. - Inadequate ventilation in some of the chemical storage areas mentioned above. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of all chemical storage areas . - Locations of fire rated walls and doors to protect these rooms . - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) . - Ventilation provisions to each of these rooms. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room at Processing 1 Building level ground, Stitching Building level ground, Processing 2 Building level 2, west side of Masjid Building in discharge route, Weaving Building level ground. - Inadequate ventilation in some of the chemical storage areas mentioned above. | Implement the above plan on site. All chemical storage areas to be compliant with Pakistan Accord Standard. | F42+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | F44 | Hazardous Materials | Diesel storage | - Diesel storage is not fire separated from the rest of the building at Weaving Building level 1 Warehouse area. - Inadequate ventilation of Diesel Storage Area. | Prepare drawings showing the proposed diesel storage arrangements to comply with NFPA 30. These shall be submitted to Accord for review and approval prior to the rectification work. The drawings should cover: - Locations of the proposed diesel storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. - Bunding details. | 4 months | 2025-10-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | F45 | Hazardous Materials | Diesel storage | - Diesel storage is not fire separated from the rest of the building at Weaving Building level 1 Warehouse area. - Inadequate ventilation of Diesel Storage Area. | Implement the above plan on site. All diesel storage areas to be compliant with Pakistan Accord Standard. | F44+4 months | 2026-02-06 | 2026-06-06 |  |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | F46 | Fire Safety Management | Fire drills | - Not all staff are involved in fire drills. - Not all staff know what to do in the event of fire. | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | 2025-10-06 | 2025-12-06 |  |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | F47 | Fire Safety Management | Fire drills | - Not all staff are involved in fire drills. - Not all staff know what to do in the event of fire. | Ensure fire drills are performed a minimum 2 times per year. | F46+2 months | 2025-12-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | F48 | Fire Safety Management | Records of system testing | - No records of testing of Fire Pumps. - No records of testing of Standpipes. - Inadequate records of testing of Fire Extinguishers. - No records of testing of Fire Doors. | - Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-10-06 | 2026-01-06 |  |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | F49 | Fire Safety Management | Records of system testing | - No records of testing of Fire Pumps - No records of testing of Standpipes - Inadequate records of testing of Fire Extinguishers - No records of testing of Fire Doors. | - Ensure all systems are being tested as per the schedule agreed with Accord. - Keep testing records. | F48+3 months | 2026-01-06 | 2026-04-06 |  |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | F50 | Fire Safety Management | Records of systems maintenance | - No records of maintenance of Fire Pumps. - No records of maintenance of Standpipes. - Inadequate records of maintenance of Fire Extinguishers.Y61 - No records of maintenance of Fire Doors. | - Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-10-06 | 2026-01-06 |  |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | F51 | Fire Safety Management | Records of systems maintenance | - No records of maintenance of Fire Pumps. - No records of maintenance of Standpipes. - Inadequate records of maintenance of Fire Extinguishers. - No records of maintenance of Fire Doors. | - Ensure all systems are being maintained as per the schedule agreed with Accord . - Keep maintenance records. | F50+3 months | 2026-01-06 | 2026-04-06 |  |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | F52 | Fire Safety Management | Emergency Action Plan | - The EAP document does not details the procedures, roles and responsibilities in the event of fire. - Escape diagrams are misleading at some of the locations including Processing 1 design studios S6 staircase misleading. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-10-06 | 2025-12-06 |  |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | F53 | Fire Safety Management | Emergency Action Plan | - The EAP document does not details the procedures, roles and responsibilities in the event of fire. - Escape diagrams are misleading at some of the locations including Processing 1 design studios S6 staircase misleading. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practised as part of fire drills. | F52+2 months | 2025-12-06 | 2026-02-06 |  |  |  |  | In Progress
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
07-May-2025
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [13 empty] | Yunus Textile Mills Ltd. - H-23/1, Landhi Industrial Area, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 07-May-2025
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-11 | 2025-10-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Potential Overstress | Highly stressed columns | This observation relates to Processing-2 where column supporting overhead water tank was found to be highly stressed at ground level. The potential cause could be due to larger grids or due to water tank. | Verify in-situ reinforcement by removing cover and confirming no. and diameter of bars and submit results to Pakistan Accord. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Potential Overstress | Highly stressed columns | This observation relates to Processing-2 where column supporting overhead water tank was found to be highly stressed at ground level. The potential cause could be due to larger grids or due to water tank. | Verify strength of reinforcement through laboratory tensile strength testing and verify rebar dia and number at ground level. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Potential Overstress | Highly stressed columns | This observation relates to Processing-2 where column supporting overhead water tank was found to be highly stressed at ground level. The potential cause could be due to larger grids or due to water tank. | Verify in-situ concrete strength for the identified columns either by 100mm dia. cores from at least 4 columns or existing cylinder strength data and submit results to Accord. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Potential Overstress | Highly stressed columns | This observation relates to Processing-2 where column supporting overhead water tank was found to be highly stressed at ground level. The potential cause could be due to larger grids or due to water tank. | Factory Engineer to review design, loads and columns stresses in area identified above. | S4+3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Potential Overstress | Highly stressed columns | This observation relates to Processing-2 where column supporting overhead water tank was found to be highly stressed at ground level. The potential cause could be due to larger grids or due to water tank. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S5+ 3 months | 2026-04-06 | 2026-07-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Cracking | Column | This observation refers to the cracking observed at ground floor exterior columns and roof level water tank supporting columns of Weaving Building. The potential cause of cracking at ground floor can be water ingress leading to corrosion of rebar resulted from drainage pipes nearby affecting multiple exterior columns and the potential cause of cracking at roof level might be due to corrosion of reinforcement resulting from penetration of water or from exposure to atmosphere. The column is not observed to be overstressed. | Propose measures to prevent future damage and to repair the existing damage and submit to Pakistan Accord for review. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Cracking | Column | This observation refers to the cracking observed at ground floor exterior columns and roof level water tank supporting columns of Weaving Building. The potential cause of cracking at ground floor can be water ingress leading to corrosion of rebar resulted from drainage pipes nearby affecting multiple exterior columns and the potential cause of cracking at roof level might be due to corrosion of reinforcement resulting from penetration of water or from exposure to atmosphere. The column is not observed to be overstressed. | Carry out the remedial work. | S7+3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Cracking | Column | This observation relates to crack in column observed in Processing-1 Building at ground floor. the column was supporting Mezzanine floor from one end. The potential cause of cracking in column could be humidity or moisture from machines used for wet processing. The column was not found to be overstressed. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Cracking | Column | This observation relates to crack in column observed in Processing-1 Building at ground floor. the column was supporting Mezzanine floor from one end. The potential cause of cracking in column could be humidity or moisture from machines used for wet processing. The column was not found to be overstressed. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Pakistan Accord for approval. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Cracking | Column | This observation relates to crack in column observed in Processing-1 Building at ground floor. the column was supporting Mezzanine floor from one end. The potential cause of cracking in column could be humidity or moisture from machines used for wet processing. The column was not found to be overstressed. | Carry out the remedial work. | S10+3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Cracking | Beams | This observation relates to Weaving Building where horizontal and diagonal cracks have been observed in multiple inverted beams at roof level. These cracks extend toward the supports and are likely caused by differential shrinkage. The potential cause of these cracks could be exposure to atmosphere | Building Engineer to carry out condition survey of the RC beams to investigate cause and impact of these cracks on the capacity of the beams. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Cracking | Beams | This observation relates to Weaving Building where horizontal and diagonal cracks have been observed in multiple inverted beams at roof level. These cracks extend toward the supports and are likely caused by differential shrinkage. The potential cause of these cracks could be exposure to atmosphere. | Propose measures to prevent future damage and to repair the existing damage /strengthen the column as required and submit to Accord for approval. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Cracking | Beams | This observation relates to Weaving Building where horizontal and diagonal cracks have been observed in multiple inverted beams at roof level. These cracks extend toward the supports and are likely caused by differential shrinkage. The potential cause of these cracks could be exposure to atmosphere. | Once reviewed, implement the remedial work. Continue monitoring them on an on-going basis. | S13+3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Other Damage/Defects | Corrosion of reinforcement | This refers to the exposed rebars on the roof floor of the Weaving Building where the rebars were corroded because of being open to the atmosphere. This corrosion can lead to reduction in the capacity of the rebars. | Propose measures to prevent further damage and submit the report to Pakistan Accord. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Other Damage/Defects | Corrosion of reinforcement | This refers to the exposed rebars on the roof floor of the Weaving Building where the rebars were corroded because of being open to the atmosphere. This corrosion can lead to reduction in the capacity of the rebars | Implement the remedial work. | S15+3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Other Damage/Defects | Corrosion of reinforcement | This refers to the exposed rebars on the roof floor of the Stitching building where the rebars were corroded because of being open to the atmosphere. This corrosion can lead to reduction in the capacity of the rebars | Propose measures to prevent further damage and submit the report to Pakistan Accord. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Other Damage/Defects | Corrosion of reinforcement | This refers to the exposed rebars on the roof floor of the Stitching building where the rebars were corroded because of being open to the atmosphere. This corrosion can lead to reduction in the capacity of the rebars. | Implement the remedial work. | S17+3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 3rd and 2nd floor of Processing-2 Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress or lack of waterproofing. At few locations, slab is already spalled and rebars is exposed. | Identify the cause of the damage / source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 3rd and 2nd floor of Processing-2 Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress or lack of waterproofing. At few locations, slab is already spalled and rebars is exposed. | Inspect damage to the slab and propose repairs to structure and submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 3rd and 2nd floor of Processing-2 Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress or lack of waterproofing. At few locations, slab is already spalled and rebars is exposed. | Implement remedial work. | S20 + 3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 3rd and 2nd floor of Processing-2 Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress or lack of waterproofing. At few locations, slab is already spalled and rebars is exposed. | Continue to monitor for future signs of water ingress/damage. | S21 + 3 months | 2026-04-06 | 2026-07-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 1st floor of the Weaving Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Identify the cause of the damage and propose measures to prevent further water damage. | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 1st floor of Weaving Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Inspect damage to the slab and propose repairs to structure and submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S25 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 1st floor of Weaving Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Implement remedial work. | S24 + 3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S26 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in slab at 1st floor of Weaving Building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Continue to monitor for future signs of water ingress/damage. | S25 + 3 months | 2026-04-06 | 2026-07-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S27 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in roof slab and beam of waterjet building (ground only). The potential cause of the spalling might be the lack of waterproofing of the roof slab. | Identify the cause of the damage / source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S28 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in roof slab and beam of waterjet building (ground only). The potential cause of the spalling might be the lack of waterproofing of the roof slab. | Inspect damage to the slab and propose repairs to structure and submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S29 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in roof slab and beam of waterjet building (ground only). The potential cause of the spalling might be the lack of waterproofing of the roof slab. | Implement remedial work. | S28 + 3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S30 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in roof slab and beam of waterjet building (ground only). The potential cause of the spalling might be the lack of waterproofing of the roof slab. | Continue to monitor for future signs of water ingress/damage. | S29 + 3 months | 2026-04-06 | 2026-07-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S31 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in cantilever slab at ground floor of stitching building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Identify the cause of the damage / source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S32 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in cantilever slab at ground floor of stitching building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Inspect damage to the slab and propose repairs to structure and submit report capturing above to Pakistan Accord for approval. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S33 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in cantilever slab at ground floor of stitching building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Implement remedial work. | S32 + 3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S34 | Other Damage/Defects | Spalling concrete | This relates to spalling of concrete in cantilever slab at ground floor of stitching building. The potential cause of spalling of concrete might be due to corrosion of reinforcement resulted from water ingress. | Continue to monitor for future signs of water ingress/damage. | S33 + 3 months | 2026-04-06 | 2026-07-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S35 | Other Damage/Defects | Column impact damage | This relates to Processing-1 Building, where damaged edges of columns observed and also reinforcement exposed of columns. The potential cause of damage might be due to collision of trolleys during transporting goods. | Repair damage to column corners and external faces. | 3 months | 2025-10-06 | 2026-01-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S36 | Other Damage/Defects | Column impact damage | This relates to Processing-1 Building, where damaged edges of columns observed and also reinforcement exposed of columns. The potential cause of damage might be due to collision of trolleys during transporting goods. | Install protective measures to prevent damage recurring. | S35 + 3 months | 2026-01-06 | 2026-04-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S37 | Other Damage/Defects | Column impact damage | This relates to Processing-1 Building, where damaged edges of columns observed and also reinforcement exposed of columns. The potential cause of damage might be due to collision of trolleys during transporting goods. | Continue to monitor condition of columns in highly trafficked areas. | S36 + 3 months | 2026-04-06 | 2026-07-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S38 | Other Damage/Defects | Health and Safety | It concerns with inadequate edge protection which present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of services on roof. There was lack of edge protection on the roof Processing-1 Building – Health & Safety concern. | Provide adequate edge protection on the roof of Processing-1 Building. | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S39 | Other Damage/Defects | Health and Safety | It concerns with corroded and broken railing and platform which present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of services – Health & Safety concern. • Railing and platform is corroded and broken in Weaving Building. | Repair/replace the corroded railing in Weaving Building. | 1 month | 2025-10-06 | 2025-11-06 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S40 | Structural Documentation | Documentation unavailable | This observation relates to documentation of the factory: The structural drawing of these buildings were available. 1. Processing-1. 2. Processing-2. 3. Weaving. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built structural documentation. | 6 months | 2025-10-06 | 2026-04-06 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability