## Electrical
[9 empty] | Last Inspection Date | [13 empty] | ELECTRICAL SAFETY
31-Dec-2024
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [13 empty] | Dynamic Sportswear (Pvt.) Ltd. - Main Canal Bank, Chung Punjgran, Multan Road, Lahore, Punjab, Pakistan
[9 empty] | Date of Initial Inspection | [13 empty] | 30 & 31-Dec-2024
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | E1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Electrical Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-01 | 2025-09-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation or electrical room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation or electrical room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Regularly update and review the substation layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E2 + 3 months | 2025-10-26 | 2026-01-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that, electrical single line diagrams (SLDs) for the factory were available but missing necessary technical details like cable sizes, circuit tagging, short circuit ratings etc. This deficiency was noted in all electrical rooms and areas distribution boards where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Update the electrical single-line diagrams for the entire facility following the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that, electrical single line diagrams (SLDs) for the factory were available but missing necessary technical details like cable sizes, circuit tagging, short circuit ratings etc. This deficiency was noted in all electrical rooms and areas distribution boards where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E4 + 2 months | 2025-11-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | 2025-09-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | E7 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E6 + 2 months | 2026-03-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | E8 | DBs & Elec Protection Systems | Circuit breakers | It was found that the circuit breakers had higher current ratings than the cables could safely withstand, which poses a significant risk of overheating and potential fire hazards. Conversely, other circuit breakers (CB) had lower ratings than necessary, resulting in frequent and unnecessary tripping. This issue was specifically observed at: - Sub-station room Building 5. - HFO control room Building 7. - Knitting Hall-1 first floor Building 3 . - Office areas of Building 1. | Evaluate the circuit breaker (CB) ratings and cable sizes for all circuits mentioned above according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | E9 | DBs & Elec Protection Systems | Circuit breakers | During the inspection, it was found that some triple pole breakers had their phases short circuited & utilize only one or two poles for operation causing imbalance in the system and false tripping. This issue was specifically observed at: - Packing area ground floor of Building 1. | Utilize all three phases of 3 or 4 pole circuit breakers to ensure proper functioning & unnecessary tripping due to load imbalance. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | E10 | DBs & Elec Protection Systems | Hot Spots | During the inspection, it was observed that several circuit breakers & electrical components including cables show signs of burning due to overheating. This issue was specifically observed at: - Security Offices DB Building 4. - Packing Hall distribution board Building 1. - Pressing Section ground floor distribution board Building 3. - Knitting Hall 1, 4, 9 distribution boards first floor Building 3. | Replace the damaged & burned cables & circuit breakers according to Section 433.1.1 and Appendix 4 of BS 7671 18TH Edition + A2 (2022). | 1 week | 2025-09-26 | 2025-10-03 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | E11 | DBs & Elec Protection Systems | Hot Spots | Hot spots were observed, particularly at the following locations: - Hotspot of 134°C found in DB at GF packing area Building 1. - Hotspot of 166°C found in DB at GF muff winding & rewinding Building 3. - Hotspot of 119°C found in DB at GF muff winding & rewinding Building 3. - Hotspot of 96.5°C found in DB at Knitting Hall-1 1F Building 3. - Hotspot of 93.4°C found in DB at GF press hall Building 3. - Hotspot of 88.1°C found in electrical panel at GF packing area Building 1. - Hotspot of 92.3°C found in DB at GF press hall Building 3. - Hotspot of 81.5°C found in cables outside main entrance of Building 3. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted, and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | E12 | DBs & Elec Protection Systems | Hot Spots | Hot spots were observed, particularly at the following locations: - Hotspot of 134°C found in DB at GF packing area Building 1. - Hotspot of 166°C found in DB at GF muff winding & rewinding Building 3. - Hotspot of 119°C found in DB at GF muff winding & rewinding Building 3. - Hotspot of 96.5°C found in DB at Knitting Hall-1 1F Building 3. - Hotspot of 93.4°C found in DB at GF press hall Building 3. - Hotspot of 88.1°C found in electrical panel at GF packing area Building 1. - Hotspot of 92.3°C found in DB at GF press hall Building 3. - Hotspot of 81.5°C found in cables outside main entrance of Building 3. | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | E13 | DBs & Elec Protection Systems | Hot Spots | Hot spots were observed, particularly at the following locations: - Hotspot of 134°C found in DB at GF packing area Building 1. - Hotspot of 166°C found in DB at GF muff winding & rewinding Building 3. - Hotspot of 119°C found in DB at GF muff winding & rewinding Building 3. - Hotspot of 96.5°C found in DB at Knitting Hall-1 1F Building 3. - Hotspot of 93.4°C found in DB at GF press hall Building 3. - Hotspot of 88.1°C found in electrical panel at GF packing area Building 1. - Hotspot of 92.3°C found in DB at GF press hall Building 3. - Hotspot of 81.5°C found in cables outside main entrance of Building 3. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. | E12 + 6 months | 2025-10-26 | 2026-04-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | E14 | DBs & Elec Protection Systems | Earthing system | During the inspection, it was noted that the earthing cables were incorrectly connected to the neutral bar in the doubling hall GF Building 3 & RF Dryer. | Design and evaluate the earthing system installation throughout the facility. Disconnect the earthing cables from the neutral bars with the distribution boards and ensure proper separation and connection. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | E15 | DBs & Elec Protection Systems | Earthing system | During the inspection, it was noted that earth pits were inaccessible, covered with dirt & debris, and the earth rod was not visible. | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | E16 | DBs & Elec Protection Systems | Earthing system | During the inspection, equipotential bonding issues for cable trays and metallic panel covers were identified, including but not limited to the areas mentioned below: - Outside of Building 5. - Outside of Building 3. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | E17 | DBs & Elec Protection Systems | Earthing system | During the inspection, it was noted that the metallic doors & metallic racks with electrical components attached to them are not earthed. It was observed specifically at: - GF packing area Building 1. - pressing section GF Building 3. - Knitting Hall 1F Building 3. | Implement equipotential bonding for all metallic doors & metallic racks to comply with BS 7671 Regulation 411.3.1.2. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | E18 | DBs & Elec Protection Systems | Earthing system | During the inspection it was found that the earthing system was absent in multiple locations, several distribution boards lacked earthing cables, many distribution boards do not have the required number of earthing cables, and many electrical machines & sockets do not have any earth connections. This issue was observed in areas such as: - Sub-station room Building 5. - Packing Area GF Building 1. - GF & 1F Building 3 . - HFO Room Building 7. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | E19 | DBs & Elec Protection Systems | Earthing system | During the inspection, no earth testing & earth pits maintenance records were available on site. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. Conduct Earth tests in the facility carried out by Certified Professional and submit the earth testing record to the Pakistan Accord for review along with equipment calibration certifications. | E18 + 2 months | 2025-12-26 | 2026-02-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, the HT panel was found covered with polyethylene sheet in sub-station room Building 5. | Remove the polyethylene sheet from the HT panels. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, several panels have cables with damaged insulation, which can lead to short circuits potentially causing fire hazard. This was observed in DB at the rooftop of Building 3. | Remove & replace cables with damaged insulation. Cables with exposed conductors can cause potential life & safety hazards. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | E22 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, there were panels with non-functional & broken components such as voltmeters, ammeters, phase indication lights. This was observed specifically in LT panel at shed opposite Building 1. | Inspect & repair panels having broken & non-functional components including voltmeters, ammeters, phase indication lights, selector switch etc. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | E23 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, there was improper cable dressing, improper dressing of cables leads to excessive heat generation which can cause the insulation to melt. This was observed at: - Office Area of Building 1. - Packing Hall Building 1. - Washing Area of Building 3. | Implement proper cable dressing, remove loose cables inside distribution board & panels. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | E24 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, in several external areas electrical components were found to be unsuitable for the environmental conditions in which they were installed like outside Building 5 & Building 2. | Identify electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed following Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | E25 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, electrical panels showed signs of corrosion, indicating potential exposure to moisture or other corrosive elements, including outside Building 5 & Building 2. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | E26 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection in some panels, electrical components were hanging freely & fixed without any proper support. This issue was specifically observed at outside of Building 5 & rooftop of Building 3. | Inspect and fix all panels with improperly fixed & hanging components to ensure the integrity of the electrical system following Section 522 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | E27 | DBs & Elec Protection Systems | Panel/cabling/busbar | The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. The HT Panel was found covered with polyethylene sheet in sub-station room Building 5. ii. In several external areas such as outside Building 5 & Building 2, it was observed that electrical components were not suitable for the environmental conditions in which they were installed. iii. Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. iv. In some panels, electrical components were hanging freely & fixed without any proper support. This issue was specifically observed at outside of Building 5 & rooftop of Building 3. v. In areas such as the Office Area of Building 1, Packing Hall Building 1 & Washing Area of Building 3, there was improper cable dressing. Improper dressing of cables leads to excessive heat generation which can cause the insulation to melt. vi. Several panels have cables with damaged insulation, which can lead to short circuits potentially causing fire hazard. This was observed in DB at the rooftop of Building 3. vii. There were panels with non-functional & broken components such as voltmeters, ammeters, phase indication lights. This was observed specifically in LT Panel at shed opposite Building 1. | Establish a schedule for regular maintenance and inspection of the panel, cabling, and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E26 + 2 months | 2025-11-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | E28 | DBs & Elec Protection Systems | Loop Connection | During the inspection loop connections were identified within the electrical panels, such as at 1F overlock hall, 1F Knitting Hall-9 of Building 3 & outside of Building 1. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilized to provide each circuit with the required live, neutral, and earth connections. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | E29 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed within all the electrical panels in areas such as DB in corridor of 1F Building 1, Dyeing Hall GF Building 3 & Knitting Hall-2 1F Building 3. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | E30 | DBs & Elec Protection Systems | Openings | The inspection revealed unsealed openings in the panels and distribution boards in sub-station room Building 5, packing hall GF Building 1 & Knitting Hall-4 1F Building 3. | Corrective actions are required to seal all openings and replace missing plates to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | E31 | DBs & Elec Protection Systems | Openings | The inspection revealed unsealed openings in the panels and distribution boards in sub-station room Building 5, Packing Hall GF Building 1 & Knitting Hall-4 1F Building 3. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | E30 + 3 months | 2025-11-26 | 2026-02-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | E32 | DBs & Elec Protection Systems | Adequate accessibility | During the inspection, at numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. At several instances, the placement of electrical panels adjacent to machines that continuously reject heat has caused the surrounding temperature to exceed ambient levels by several degrees. This temperature rise further increases the temperature of the panels and boards nearby. These issues were found in the Knitting Hall-14 1F Building 3, muff winding & rewinding GF Building 3, Dyeing Hall Building 3 & outside main entrance of Building 3. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | E33 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems at Knitting Hall-3 1F Building 3, yarn covering hall Building 3 & muff winding & rewinding GF Building 3. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | E34 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems at Knitting Hall-3 1F Building 3, yarn covering hall Building 3 & muff winding & rewinding GF Building 3. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E33 + 3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | E35 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system consisting of lightning arrestors was provided, however, there was no study available to confirm its adequacy. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. Also, provide the risk assessment report for Accord review. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | E36 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system consisting of lightning arrestors was provided, however, there was no study available to confirm its adequacy. | If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard. | E35 + 4 months | 2025-11-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, it was observed that There were four conventional fire alarm panels installed inside the factory in Building 4 security room. Following observations were made: The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and MCP coverage, faulty or non-functional detectors, non-fire rated cables, low audibility in various areas, inadequate visual coverage, non-compliant 220V AC hooters and overall non-compliance with NFPA 72 standards. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, it was observed that There were four conventional fire alarm panels installed inside the factory in Building 4 security room. Following observations were made: The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and MCP coverage, faulty or non-functional detectors, non-fire rated cables, low audibility in various areas, inadequate visual coverage, non-compliant 220V AC hooters and overall non-compliance with NFPA 72 standards. | (1) Submit design documentation for new system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, it was observed that There were four conventional fire alarm panels installed inside the factory in Building 4 security room. Following observations were made: The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and MCP coverage, faulty or non-functional detectors, non-fire rated cables, low audibility in various areas, inadequate visual coverage, non-compliant 220V AC hooters and overall non-compliance with NFPA 72 standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E38 + 1 month | 2025-12-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, it was observed that There were four conventional fire alarm panels installed inside the factory in Building 4 security room. Following observations were made: The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and MCP coverage, faulty or non-functional detectors, non-fire rated cables, low audibility in various areas, inadequate visual coverage, non-compliant 220V AC hooters and overall non-compliance with NFPA 72 standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E39 + 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | E41 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, it was observed that There were four conventional fire alarm panels installed inside the factory in Building 4 security room. Following observations were made: The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and MCP coverage, faulty or non-functional detectors, non-fire rated cables, low audibility in various areas, inadequate visual coverage, non-compliant 220V AC hooters and overall non-compliance with NFPA 72 standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | E40 + 5 months | 2026-05-26 | 2026-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | E42 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, it was observed that There were four conventional fire alarm panels installed inside the factory in Building 4 security room. Following observations were made: The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and MCP coverage, faulty or non-functional detectors, non-fire rated cables, low audibility in various areas, inadequate visual coverage, non-compliant 220V AC hooters and overall non-compliance with NFPA 72 standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E41 + 3 months | 2026-10-26 | 2027-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | E43 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection, it was observed that There were four conventional fire alarm panels installed inside the factory in Building 4 security room. Following observations were made: The conventional Fire Alarm and Detection System was non-listed, non-functional, and exhibited several deficiencies, including inappropriate detection and MCP coverage, faulty or non-functional detectors, non-fire rated cables, low audibility in various areas, inadequate visual coverage, non-compliant 220V AC hooters and overall non-compliance with NFPA 72 standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E42 + 3 months | 2027-01-26 | 2027-04-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | E44 | Emergency Lighting | Provided but insufficient | During the inspection, several areas lack sufficient emergency lighting coverage. The following are some examples of these areas: - Warehouse Container. - Sub-station room Building 5. - HFO area Building 7. - Canteen in Building 2. - Dyeing Hall GF Building 3. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. Also, submit design documentation for Accord review. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 355 | 421 | 6 | 5 |  | Initial | [11 empty] | E45 | Emergency Lighting | Provided but insufficient | Multiple emergency luminaires indicate the need for maintenance throughout the facility. This issue was specifically observed at ground floor Building 2 & sub-station room Building 5. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 356 | 421 | 6 | 5 |  | Initial | [11 empty] | E46 | Emergency Lighting | Provided but insufficient | During the inspection it was observed that external emergency lighting was not provided at assembly areas, preventing people from reaching a place of safety outside the facility during nighttime evacuations. | Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s) | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 357 | 421 | 6 | 5 |  | Initial | [11 empty] | E47 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that the emergency lighting was provided but is non-functional in several areas. This issue was specifically observed at Dyeing Hall GF Building 3 & pressing section GF Building 3. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 358 | 421 | 6 | 5 |  | Initial | [11 empty] | E48 | Emergency Lighting | Provided but non-functional | During the inspection it was observed that the emergency lighting was provided but is non-functional in several areas. This issue was specifically observed at Dyeing Hall GF Building 3 & pressing section GF Building 3. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E47 + 3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 359 | 421 | 6 | 5 |  | Initial | [11 empty] | E49 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | 2025-09-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 360 | 421 | 6 | 5 |  | Initial | [11 empty] | E50 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | E49 + 2 months | 2026-03-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 361 | 421 | 6 | 5 |  | Initial | [11 empty] | E51 | Generator, Transformer & Sub-Station Room | Breathing system | During the inspection of the transformer's breathing system, the breathing system exhibited signs of wear and deterioration. The silica gel in the breather was found to be saturated, indicating the need for replacement. Additionally, transformer oil leakage was observed around the conservator tank & transformer body. | Replace the silica gel in the breather and repair any leaks around the breather housing to prevent moisture ingress into the transformer's insulation oil. Inspect the transformer body for any oil leakage and spillage, repair or maintain the components to ensure the proper functioning of the transformer. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 362 | 421 | 6 | 5 |  | Initial | [11 empty] | E52 | Generator, Transformer & Sub-Station Room | Breathing system | During the inspection of the transformer's breathing system, the breathing system exhibited signs of wear and deterioration. The silica gel in the breather was found to be saturated, indicating the need for replacement. Additionally, transformer oil leakage was observed around the conservator tank & transformer body. | Implement a regular maintenance schedule to periodically inspect and service the breathing system components, ensuring the silica gel is replaced as needed and that all seals and connections are intact to maintain system integrity. | E51 + 2 months | 2025-11-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 363 | 421 | 6 | 5 |  | Initial | [11 empty] | E53 | Generator, Transformer & Sub-Station Room | Transformer arcing horn | The inspection revealed significant wear and deterioration of the arcing horn. It was also observed that arcing horns were missing in the transformer posing serious safety risk in case of flashover/arcing conditions . This issue was specifically observed in transformer-2 in Building 5. | Install appropriately sized arcing horns in transformer to mitigate the risk of electrical faults and fires. Replace the corroded and worn arcing horn to prevent further damage and mitigate the risk of electrical faults and fires. Inspect and clean any associated components to ensure proper function and safety. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 364 | 421 | 6 | 5 |  | Initial | [11 empty] | E54 | Generator, Transformer & Sub-Station Room | Transformer arcing horn | The inspection revealed significant wear and deterioration of the arcing horn. It was also observed that arcing horns were missing in the transformer posing serious safety risk in case of flashover/arcing conditions . This issue was specifically observed in transformer-2 in Building 5. | Establish a routine maintenance schedule for regular inspection and servicing of the arcing horn and related components. Implement measures for early detection of wear and corrosion, such as periodic testing and monitoring, to ensure the arcing horn remains in optimal condition and effectively prevents arcing -related damage. Share testing documentation/ certification for Pakistan Accord review. | E53 + 3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 365 | 421 | 6 | 5 |  | Initial | [11 empty] | E55 | Generator, Transformer & Sub-Station Room | Room separation | It was observed that there was no room separation between transformer & LT panels. The transformer & LT panels are placed with spacing of 1 meter distance between them. This type of equipment arrangement could facilitate the spread of fire or electrical faults from one area to another. | Install temporary fire-resistant barriers and seal any gaps and openings between the generator, transformer, and substation areas to immediately reduce the risk of fire and electrical fault propagation | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 366 | 421 | 6 | 5 |  | Initial | [11 empty] | E56 | Generator, Transformer & Sub-Station Room | Room separation | It was observed that there was no room separation between transformer & LT panels. The transformer & LT panels are placed with spacing of 1 meter distance between them. This type of equipment arrangement could facilitate the spread of fire or electrical faults from one area to another. | Redesign and reconstruct the layout to include permanent fire-resistant walls and partitions that comply with relevant safety standards such as BS 7671 and NFPA 110, ensuring proper physical separation and enhanced safety for all critical areas. Establish a regular inspection and maintenance schedule to ensure the integrity of these barriers over time. | E55 + 4 months | 2025-11-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 367 | 421 | 6 | 5 |  | Initial | [11 empty] | E57 | Generator, Transformer & Sub-Station Room | Battery | During the inspection, the following observations were noted with battery systems: - Noticeable spills of battery fluid were observed, which can lead to corrosion and pose a chemical hazard. - Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. This issue was specifically observed in the sub-station area Building 5, HFO control room Building 7 & Fresh Arrival Office Building 1. | Clean any battery fluid spills using appropriate neutralizing agents and safety equipment to prevent corrosion and chemical hazards. Inspect and repair any affected battery cells or enclosures to prevent further leakage. Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Remove any flammable material from battery terminals. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 368 | 421 | 6 | 5 |  | Initial | [11 empty] | E58 | Generator, Transformer & Sub-Station Room | Battery | During the inspection, the following observations were noted with battery systems: - Noticeable spills of battery fluid were observed, which can lead to corrosion and pose a chemical hazard. - Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. This issue was specifically observed in the sub-station area Building 5, HFO control room Building 7 & Fresh Arrival Office Building 1. | Develop a periodic maintenance program to ensure every battery in the facility is installed properly with clean terminals and proper cable termination. Record battery voltage level and discharge test every 6 months. Replace batteries as necessary. | E57 + 2 months | 2025-10-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 369 | 421 | 6 | 5 |  | Initial | [11 empty] | E59 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables; they were laid directly on the ground, hung along the walls & laid overhead without support system. Several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. This issue was specifically observed outside Building 3 & 5, muff winding & rewinding GF Building 3 & at the backside of the Building 3. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 370 | 421 | 6 | 5 |  | Initial | [11 empty] | E60 | Cabling & Wiring | Cables support and protection | Numerous loose connections were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections and the practice of inserting exposed wires directly into sockets to prevent electrical hazards. This issue was specifically observed in washing area GF Building 3. | Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 371 | 421 | 6 | 5 |  | Initial | [11 empty] | E61 | Cabling & Wiring | Cables support and protection | Improperly sized cable trays were utilized for cables resulting in improper support for cables. Moreover, cables were wrapped on cable tray using transparent PVC tape. This can result in overloading, overheating of cables and is also a potential fire risk. This issue was specifically observed in muff winding & rewinding GF Building 3. | Replace the inadequately sized cable trays with properly sized cable trays & trunking, allowing proper spacing & support to cables. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 372 | 421 | 6 | 5 |  | Initial | [11 empty] | E62 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables; they were laid directly on the ground, hung along the walls & laid overhead without support system. Several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. This issue was specifically observed outside Building 3 & 5, muff winding & rewinding GF Building 3 & at the backside of the Building 3. Numerous loose connections were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections and the practice of inserting exposed wires directly into sockets to prevent electrical hazards. This issue was specifically observed in washing area GF Building 3. Improperly sized cable trays were utilized for cables resulting in improper support for cables. Moreover, cables were wrapped on cable tray using transparent PVC tape. This can result in overloading, overheating of cables and is also a potential fire risk. This issue was specifically observed in muff winding & rewinding GF Building 3. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. Redesign the cable routing system to ensure cables are safely positioned away from high-traffic areas, maintaining compliance with safety regulations. Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices. | E61 + 4months | 2025-11-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 373 | 421 | 6 | 5 |  | Initial | [11 empty] | E63 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed in sub-station rooms in Building 5. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 374 | 421 | 6 | 5 |  | Initial | [11 empty] | E64 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. This issue was specifically observed in sub-station rooms in Building 5. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | E63 + 3 months | 2025-10-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 375 | 421 | 6 | 5 |  | Initial | [11 empty] | E65 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was specifically observed in distribution boards of Building 5, Building 1, Building 3 & Building 2. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 376 | 421 | 6 | 5 |  | Initial | [11 empty] | E66 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. This issue was specifically observed in distribution boards of building 5, Building 1, Building 3 & Building 2. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | E65 + 3 months | 2025-11-26 | 2026-02-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 377 | 421 | 6 | 5 |  | Initial | [11 empty] | E67 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed in distribution boards of building 5, Building 1, Building 3 & Building 2. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 378 | 421 | 6 | 5 |  | Initial | [11 empty] | E68 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. This issue was specifically observed in distribution boards of building 5, Building 1, Building 3 & Building 2. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Provide cable soldering training and equipment to staff along with heat shrink sleeves in lieu of PVC tape joints. | E67 + 3 months | 2025-11-26 | 2026-02-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 379 | 421 | 6 | 5 |  | Initial | [11 empty] | E69 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable color coding practices were identified, such as in GF Dyeing lab, Pressing Section, Yarn Covering area Building 3, Knitting Hall 6 Building 3, GF Packing Hall, Office Areas in Building 1. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable color coding. This involves re-labelling or re-insulating the cables with the appropriate color codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 380 | 421 | 6 | 5 |  | Initial | [11 empty] | E70 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable color coding practices were identified, such as in GF Dyeing lab, Pressing Section, Yarn Covering area Building 3, Knitting Hall 6 Building 3, GF Packing Hall, Office Areas in Building 1. | Develop and enforce a strict protocol for cable color coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized color coding system, thereby preventing future deviations, and ensuring sustained safety and operational efficiency. | E69 + 3 months | 2025-11-26 | 2026-02-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 381 | 421 | 6 | 5 |  | Initial | [11 empty] | E71 | Cabling & Wiring | Fixtures | During the inspection, it was found that many light fixtures were hung without proper support, which could cause falling hazard & equipment damage. This issue was specifically observed at Diesel Generator Room Building 5, Canteen Area 1F Building 2, Packing Hall GF, Office Areas GF Building 1. | Install appropriate mounting hardware to securely hang LED lights and prevent cable damage. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 382 | 421 | 6 | 5 |  | Initial | [11 empty] | E72 | Cabling & Wiring | Fixtures | During the inspection, it was found that many light fixtures were hung without proper support, which could cause falling hazard & equipment damage. This issue was specifically observed at Diesel Generator Room Building 5, Canteen Area 1F Building 2, Packing Hall GF, Office Areas GF Building 1. | Implement a regular inspection and maintenance schedule to check and secure all lighting fixtures ensuring they remain safely and correctly installed. | E71 + 2 months | 2025-10-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 383 | 421 | 6 | 5 |  | Initial | [11 empty] | E73 | Cabling & Wiring | Fixtures | During the inspection, it was found that many light fixtures were hung without proper support, which could cause falling hazard & equipment damage. This issue was specifically observed at Diesel Generator Room Building 5, Canteen Area 1F Building 2, Packing Hall GF, Office Areas GF Building 1. | Replace or repair broken and exposed switchboards immediately to restore safe and secure connections. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 384 | 421 | 6 | 5 |  | Initial | [11 empty] | E74 | Cabling & Wiring | Fixtures | During the inspection, it was found that many light fixtures were hung without proper support, which could cause falling hazard & equipment damage. This issue was specifically observed at Diesel Generator Room Building 5, Canteen Area 1F Building 2, Packing Hall GF, Office Areas GF Building 1. | Implement a preventive maintenance program that includes periodic checks and timely replacement of damaged electrical components including switchboards, sockets & junction boxes etc to maintain safety standards. | E73 + 2 months | 2025-10-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 385 | 421 | 6 | 5 |  | Initial | [11 empty] | E75 | Cabling & Wiring | Fixtures | During the inspection it was noted that non-compliant flammable wooden switchboards were used in a few locations which could cause fire in case of short circuit/fault condition. This issue was specifically observed at diesel generator room Building 5, Canteen area 1F Building 2, Packing Hall GF, Office Areas GF Building 1. | Replace combustible wooden ply backings in switchboards with non-combustible materials to reduce fire risk. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 416 | 421 | 6 | 5 |  | Initial | [11 empty] | E76 | Cabling & Wiring | Fixtures | During the inspection it was noted that non-compliant flammable wooden switchboards were used in a few locations which could cause fire in case of short circuit/fault condition. This issue was specifically observed at diesel generator room Building 5, Canteen area 1F Building 2, Packing Hall GF, Office Areas GF Building 1. | Establish a facility-wide standard to use only non-combustible materials for mounting electrical components and conduct regular audits for compliance. | E75 + 2 months | 2025-10-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[9 empty] | Last Inspection Date | [13 empty] | FIRE SAFETY
31-Dec-2024
Corrective Action Plan - Fire
Dynamic Sportswear (Pvt.) Ltd. - Main Canal Bank, Chung Punjgran, Multan Road, Lahore, Punjab, Pakistan
[9 empty] | Factory Name & Address | [13 empty] | 30 & 31-Dec-2024
Date of Initial Inspection
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | F1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Fire Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-01 | 2025-09-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F2 | Means of Escape | Protection of stairs | -Unprotected openings into stairs (S6 & S7) at Building 1, S11 at Building 2 (S1 & S3) all floors at Building 3. -Fire load in stairs S2 at Building 3 (ground floor). | Remove fire load from stairs. | 2 weeks | 2025-09-26 | 2025-10-10 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F3 | Means of Escape | Protection of stairs | -Unprotected openings into stairs (S6 & S7) at Building 1, S11 at Building 2 (S1 & S3) all floors at Building 3. -Fire load in stairs S2 at Building 3 (ground floor). | - Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Propose modifications for the stairs discharging into roof. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F4 | Means of Escape | Protection of stairs | -Unprotected openings into stairs (S6 & S7) at Building 1, S11 at Building 2 (S1 & S3) all floors at Building 3. -Fire load in stairs S2 at Building 3 (ground floor). | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F3+ 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | F5 | Means of Escape | Travel distance | -Common path of travel distances exceeds permitted limits in Building 2 at 1st floor (32 m), Building 3 at 1st floor (31 m) & Building 6 at 1st floor (35 m). | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 4 Months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | [11 empty] | F6 | Means of Escape | Travel distance | -Common path of travel distances exceeds permitted limits in Building 2 at 1st floor (32 m), Building 3 at 1st floor (31 m) & Building 6 at 1st floor (35 m). | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | F5+ 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | [11 empty] | F7 | Means of Escape | Escape doors | - Most of the escape doors are lockable/locked at Building 1 (ground floor), Building 2 (1st floor) & most of the doors in Building 3. - Few of the escape doors installed were rolling shutter type used for escape at Building 1A (ground floor) & Building 3 (ground & 1st floor). - Doors serving areas for more than 50 occupants swings against the direction of escape at Building 3 (1st floor). | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 2025-09-26 | 2025-10-10 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | [11 empty] | F8 | Means of Escape | Escape doors | - Most of the escape doors are lockable/locked at Building 1 (ground floor), Building 2 (1st floor) & most of the doors in Building 3. - Few of the escape doors installed were rolling shutter type used for escape at Building 1A (ground floor) & Building 3 (ground & 1st floor). - Doors serving areas for more than 50 occupants swings against the direction of escape at Building 3 (1st floor). | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace rolling shutter with swing doors open in the direction of travel to an exit. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | [11 empty] | F9 | Means of Escape | Escape doors | -Most of the escape doors are lockable/locked at Building 1 (ground floor), Building 2 (1st floor) & most of the doors in Building 3. -Few of the escape doors installed were rolling shutter type used for escape at Building 1A (ground floor) & Building 3 (ground & 1st floor). -Doors serving areas for more than 50 occupants swings against the direction of escape at Building 3 (1st floor). | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F8 + 3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [11 empty] | F10 | Means of Escape | Exit access | -Stair S-7 of Building 1A, S11 of Building 2 & S-1 to S-3 of Building 3 discharge inside building at a distance from building exit. -Obstructions/ Trip hazard on escape route at Building 1 (ground floor) & Building 3 (2nd floor). -Door opening in S6 (1st floor) acts as obstruction in escape route. | Remove obstructions/trip hazard on escape routes and keep them clear for escape. | 2 weeks | 2025-09-26 | 2025-10-10 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | [11 empty] | F11 | Means of Escape | Exit access | -Stair S-7 of Building 1A, S11 of Building 2 & S-1 to S-3 of Building 3 discharge inside building at a distance from building exit. -Obstructions/ Trip hazard on escape route at Building 1 (ground floor) & Building 3 (2nd floor). -Door opening in S6 (1st floor) acts as obstruction in escape route. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). Submit the proposal to Pakistan Accord for review. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | [11 empty] | F12 | Means of Escape | Exit access | -Stair S-7 of Building 1A, S11 of Building 2 & S-1 to S-3 of Building 3 discharge inside building at a distance from building exit. -Obstructions/ Trip hazard on escape route at Building 1 (ground floor) & Building 3 (2nd floor). -Door opening in S6 (1st floor) acts as obstruction in escape route. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. | F11+ 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | [11 empty] | F13 | Means of Escape | Exit discharge | -Exit discharge from stair S-4 & S-5 not separated from washing, dyeing, boiler & HFO area at Building 3. -Exit discharge from workshop area of Building 1 not separated from chemicals store. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: -Layout showing the location of fire rated walls/doors to protect stair discharge routes. -Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [11 empty] | F14 | Means of Escape | Exit discharge | -Exit discharge from stair S-4 & S-5 not separated from washing, dyeing, boiler & HFO area at Building 3. -Exit discharge from workshop area of Building 1 not separated from chemicals store. | -Ensure external exit discharge routes are adequately fire separated from the rest of the building. -Ensure external escape routes do not pass close to unprotected high-risk areas. | F13 + 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | [11 empty] | F15 | Means of Escape | Exit signage | -Electrically powered exit signs are not a tested and listed system in whole factory. -Missing exit sign at entry into stair S-1 at Building 3 (2nd floor). -Missing exit signs in office areas at Building 3 (1st floor). | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | [11 empty] | F16 | Means of Escape | Exit signage | -Electrically powered exit signs are not a tested and listed system in whole factory. -Missing exit sign at entry into stair S-1 at Building 3 (2nd floor). -Missing exit signs in office areas at Building 3 (1st floor). | Ensure that all exit signage is checked periodically and in good working condition. | F15+ 3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | [11 empty] | F17 | Fire Rated Construction | Separation of high-risk areas | -Boiler area is not separated from production area at Building 3 (ground floor). -Electrical room is not separated from genset area at Building 7 (ground floor) & transformer area at Building 5 (ground floor). -Fuel storage area is not fire separated with fire rated construction at Building 7. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to the Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). - Locations of fire- rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 Months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | [11 empty] | F18 | Fire Rated Construction | Separation of high-risk areas | -Boiler area is not separated from production area at Building 3 (ground floor). -Electrical room is not separated from genset area at Building 7 (ground floor) & transformer area at Building 5 (ground floor). -Fuel storage area is not fire separated with fire rated construction at Building 7. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F17 + 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | [11 empty] | F19 | Fire Rated Construction | Separation of shafts | - All the lift shafts are not fire separated in Building 3 (all floors). | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to the Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 Months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | [11 empty] | F20 | Fire Rated Construction | Separation of shafts | - All the lift shafts are not fire separated in Building 3 (all floors). | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F19 + 4 Months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | [11 empty] | F21 | Fire Rated Construction | Separation of occupancies | '-Offices are not separated from knitting area at Building 3 (1st floor). -Childcare room not separated from finishing area & don’t have direct access from building at Building 1 (ground floor). | Evacuate the childcare room. | 2 weeks | 2025-09-26 | 2025-10-10 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | [11 empty] | F22 | Fire Rated Construction | Separation of occupancies | - Offices are not separated from knitting area at Building 3 (1st floor). - Childcare room not separated from finishing area & don’t have direct access from building at Building 1 (ground floor), | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building, - Proposed fire separation details (including fire rating of walls, floors and doors), | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | [11 empty] | F23 | Fire Rated Construction | Separation of occupancies | '- Offices are not separated from knitting area at Building 3 (1st floor). - Childcare room not separated from finishing area & don’t have direct access from building at Building 1 (ground floor). | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F22 + 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | [11 empty] | F24 | Fire Rated Construction | Atrium | - Atrium not fire separated at Building 3. | Prepare drawings showing the proposed fire separation and means of escape from all areas bordering on the atrium and submit to Pakistan Accord for review. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | [11 empty] | F25 | Fire Rated Construction | Atrium | - Atrium not fire separated at Building 3. | Provide fire rated construction including opening protection assemblies i.e. fire doors and alternative means of escape as needed and according to the layouts and documents reviewed by Pakistan Accord. | F24+ 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | [11 empty] | F26 | Fire Rated Construction | Storage | - Storage not separated from Compressor Area (2nd floor), Knitting (1st floor), Packing, Dyeing & Genset Area (ground floor) at Building 3 & Packing Area at Building 1 (ground floor). | Identify all designated storage areas. Identify which storage areas can be re-arranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | [11 empty] | F27 | Fire Rated Construction | Storage | - Storage not separated from Compressor Area (2nd floor), Knitting (1st floor), Packing, Dyeing & Genset Area (ground floor) at Building 3 & Packing Area at Building 1 (ground floor). | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F26 + 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 170 | 421 | 6 | 5 |  | Initial | [11 empty] | F28 | Fire Suppression | Standpipe system | - There are no standpipes in Building 3 which are required since building area is more than 2325 m2 & more than 2 floors. | (1) Submit design documentation for a standpipes system, along with required supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 171 | 421 | 6 | 5 |  | Initial | [11 empty] | F29 | Fire Suppression | Standpipe system | - There are no standpipes in Building 3 which are required since building area is more than 2325 m2 & more than 2 floors. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F28 + 1 month | 2026-01-26 | 2026-02-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | [11 empty] | F30 | Fire Suppression | Standpipe system | - There are no standpipes in Building 3 which are required since building area is more than 2325 m2 & more than 2 floors. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F29 + 3 months | 2026-02-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 173 | 421 | 6 | 5 |  | Initial | [11 empty] | F31 | Fire Suppression | Standpipe system | - There are no standpipes in Building 3 which required since building area is more than 2325 m2 & more than 2 floors. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F30+ 4 months | 2026-05-26 | 2026-09-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 174 | 421 | 6 | 5 |  | Initial | [11 empty] | F32 | Fire Suppression | Standpipe system | - There are no standpipes in Building 3 which required since building area is more than 2325 m2 & more than 2 floors. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F31 + 3 months | 2026-09-26 | 2026-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 175 | 421 | 6 | 5 |  | Initial | [11 empty] | F33 | Fire Suppression | Standpipe system | - There are no standpipes in Building 3 which required since building area is more than 2325 m2 & more than 2 floors. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F32 + 3 months | 2026-12-26 | 2027-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 176 | 421 | 6 | 5 |  | Initial | [11 empty] | F34 | Fire Suppression | Fire pumps | - Fire pump set is not installed on site. | Provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Accord for review. | 18 months | 2025-09-26 | 2027-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 177 | 421 | 6 | 5 |  | Initial | [11 empty] | F35 | Hazardous Materials | Chemicals storage | - Main chemical store is not fire separated with fire rated construction at Building 1B. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 314 | 421 | 6 | 5 |  | Initial | [11 empty] | F36 | Hazardous Materials | Chemicals storage | - Main chemical store is not fire separated with fire rated construction at Building 1B. | Implement the above plan on site. All chemical storage areas to be compliant with Accord Standard. | F35 + 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 315 | 421 | 6 | 5 |  | Initial | [11 empty] | F37 | Hazardous Materials | Diesel storage | -Diesel storage tank has no bunding at Building 5 & Building 7 (ground floor). | Prepare drawings showing diesel storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of diesel storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. - Bunding details. | 4 months | 2025-09-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 346 | 421 | 6 | 5 |  | Initial | [11 empty] | F38 | Hazardous Materials | Diesel storage | -Diesel storage tank has no bunding at Building 5 & Building 7 (ground floor). | Implement the above plan on site. All diesel storage areas to be compliant with Accord Standard. | F37 + 4 months | 2026-01-26 | 2026-05-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 349 | 421 | 6 | 5 |  | Initial | [11 empty] | F39 | Fire Safety Management | Records of systems maintenance | - No records of maintenance of Fire extinguishers. | - Prepare maintenance schedule for all life safety systems -Identify how the systems will be maintained and who is responsible. - The schedule is to be submitted to Accord for review and approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 350 | 421 | 6 | 5 |  | Initial | [11 empty] | F40 | Fire Safety Management | Records of systems maintenance | - No records of maintenance of Fire extinguishers. | - Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. | F39 + 3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 351 | 421 | 6 | 5 |  | Initial | [11 empty] | F41 | Fire Safety Management | Records of system testing | - No records of testing of Fire extinguishers. | - Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 352 | 421 | 6 | 5 |  | Initial | [11 empty] | F42 | Fire Safety Management | Records of system testing | - No records of testing of Fire extinguishers. | - Ensure all systems are being tested as per the schedule agreed with Accord . - Keep testing records. | F41+ 3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 353 | 421 | 6 | 5 |  | Initial | [11 empty] | F43 | Fire Safety Management | Emergency Action Plan | An Emergency Action Plan (EAP) exists; however, it lacks detailed documentation outlining specific procedures, roles, and responsibilities in the event of a fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 2025-09-26 | 2025-11-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 354 | 421 | 6 | 5 |  | Initial | [11 empty] | F44 | Fire Safety Management | Emergency Action Plan | An Emergency Action Plan (EAP) exists; however, it lacks detailed documentation outlining specific procedures, roles, and responsibilities in the event of a fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F43 + 2 months | 2025-11-26 | 2026-01-26 | AGREE |  |  |  | In Progress
| 3 | 8 |  | 384 | 421 | 6 | 5
| 3 | 8 |  | 385 | 421 | 6 | 5
| 3 | 8 |  | 416 | 421 | 6 | 5
| 3 | 8 |  | 417 | 421 | 6 | 5
| 3 | 8 |  | 418 | 421 | 6 | 5
| 3 | 8 |  | 419 | 421 | 6 | 5
| 3 | 8 |  | 420 | 421 | 6 | 5
| 3 | 8 |  | 421 | 421 | 6 | 5
| 3 | 8 |  | 422 | 421 | 6 | 5
| 3 | 8 |  | 423 | 421 | 6 | 5
| 3 | 8 |  | 424 | 421 | 6 | 5
| 3 | 8 |  | 425 | 421 | 6 | 5
| 3 | 8 |  | 426 | 421 | 6 | 5
| 3 | 8 |  | 427 | 421 | 6 | 5
| 3 | 8 |  | 428 | 421 | 6 | 5
| 3 | 8 |  | 429 | 421 | 6 | 5
| 3 | 8 |  | 430 | 421 | 6 | 5
| 3 | 8 |  | 431 | 421 | 6 | 5
| 3 | 8 |  | 432 | 421 | 6 | 5
| 3 | 8 |  | 433 | 421 | 6 | 5
| 3 | 8 |  | 434 | 421 | 6 | 5
| 3 | 8 |  | 435 | 421 | 6 | 5
| 3 | 8 |  | 436 | 421 | 6 | 5
| 3 | 8 |  | 437 | 421 | 6 | 5
| 3 | 8 |  | 438 | 421 | 6 | 5
| 3 | 8 |  | 439 | 421 | 6 | 5
| 3 | 8 |  | 440 | 421 | 6 | 5
| 3 | 8 |  | 502 | 421 | 6 | 5
| 3 | 8 |  | 503 | 421 | 6 | 5
| 3 | 8 |  | 504 | 421 | 6 | 5
| 3 | 8 |  | 505 | 421 | 6 | 5
| 3 | 8 |  | 506 | 421 | 6 | 5
| 3 | 8 |  | 507 | 421 | 6 | 5
| 3 | 8 |  | 508 | 421 | 6 | 5
| 3 | 8 |  | 509 | 421 | 6 | 5
| 3 | 8 |  | 510 | 421 | 6 | 5
| 3 | 8 |  | 511 | 421 | 6 | 5
| 3 | 8 |  | 512 | 421 | 6 | 5
| 3 | 8 |  | 513 | 421 | 6 | 5
| 3 | 8 |  | 514 | 421 | 6 | 5
| 3 | 8 |  | 515 | 421 | 6 | 5
| 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [13 empty] | STRUCTURAL SAFETY
31-Dec-2024
Corrective Action Plan - Structural
Dynamic Sportswear (Pvt.) Ltd. - Main Canal Bank, Chung Punjgran, Multan Road, Lahore, Punjab, Pakistan
[9 empty] | Factory Name & Address | [13 empty] | 30 & 31-Dec-2024
Date of Initial Inspection
[23 empty] | Remediation Plan Confirmed |  | Finance Plan Confirmed
[23 empty] | FALSE |  | FALSE
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | REFERENCE NUMBER | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | AGREED | AGREED | FACTORY AGREEMENT WITH DATES | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
[27 empty] | REMEDIATION START DATE | REMEDIATION FINISH DATE
[9 empty] | Initial | [11 empty] | S1 | Remediation Support Services | External Consultant Engagement |  | Engage a Consultant Structural Safety Engineer to proceed with the remediation. | 8 weeks | 2025-08-01 | 2025-09-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S2 | Cracking | Column | This refers to Building 1A, where peripheral columns on the ground and first floors exhibit cracks. These cracks are likely the result of concrete degradation caused by prolonged exposure to weathering, which has led to reinforcement corrosion. The situation has worsened due to delayed maintenance and insufficient measures to prevent water ingress. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S3 | Cracking | Column | This refers to Building 1A, where peripheral columns on the ground and first floors exhibit cracks. These cracks are likely the result of concrete degradation caused by prolonged exposure to weathering, which has led to reinforcement corrosion. The situation has worsened due to delayed maintenance and insufficient measures to prevent water ingress. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S4 | Cracking | Column | This refers to Building 1A, where peripheral columns on the ground and first floors exhibit cracks. These cracks are likely the result of concrete degradation caused by prolonged exposure to weathering, which has led to reinforcement corrosion. The situation has worsened due to delayed maintenance and insufficient measures to prevent water ingress. | Carry out the remedial work. | S3+3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S5 | Cracking | Column | This refers to Building 1A, where peripheral columns on the ground and first floors exhibit cracks. These cracks are likely the result of concrete degradation caused by prolonged exposure to weathering, which has led to reinforcement corrosion. The situation has worsened due to delayed maintenance and insufficient measures to prevent water ingress. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking and the residual load capacity including condition of concrete and rebar. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S6 | Cracking | Column | This refers to Building 1A, where peripheral columns on the ground and first floors exhibit cracks. These cracks are likely the result of concrete degradation caused by prolonged exposure to weathering, which has led to reinforcement corrosion. The situation has worsened due to delayed maintenance and insufficient measures to prevent water ingress. | Propose measures to prevent future damage and to repair the existing damage / strengthen the column as required and submit to Accord for approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S7 | Cracking | Column | This refers to Building 1A, where peripheral columns on the ground and first floors exhibit cracks. These cracks are likely the result of concrete degradation caused by prolonged exposure to weathering, which has led to reinforcement corrosion. The situation has worsened due to delayed maintenance and insufficient measures to prevent water ingress. | Carry out the remedial work. | S6+3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S8 | Structural Documentation | Documentation unavailable | Structural drawings were unavailable for all buildings except Building 3. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | 2025-09-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S9 | Structural Documentation | Differs from as-built structure | Provided structural drawings does not match with existing structure. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | 2025-09-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S10 | Structural Documentation | Lack of safe load plans | No safe loading plans were posted on the floors. | Building structural engineer to review design documentation to confirm load capacity of the structures. Develop safe load plans and submit to the Accord. Factory to post safe load plans on each floor. | 6 months | 2025-09-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S11 | Structural Documentation | Non-engineered structure | Building 1A – Steel Pipe columns in Building 1A rest directly on the slab without proper base connection or anchorage, and the lack of lateral supports combined with large grid spacing poses significant risks of instability under lateral loads. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S12 | Structural Documentation | Non-engineered structure | Building 1A – Steel Pipe columns in Building 1A rest directly on the slab without proper base connection or anchorage, and the lack of lateral supports combined with large grid spacing poses significant risks of instability under lateral loads. | Propose strengthening work as required and submit to Pakistan Accord for approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S13 | Structural Documentation | Non-engineered structure | Building 1A – Steel Pipe columns in Building 1A rest directly on the slab without proper base connection or anchorage, and the lack of lateral supports combined with large grid spacing poses significant risks of instability under lateral loads. | Implement strengthening work as required. | S12+3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S14 | Structural Documentation | Non-engineered structure | Building 6 – Columns appear to rest directly on masonry walls, and are possibly embedded in plain concrete, with small pipe sections used as columns additionally beams connecting these pipe columns have small sections. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S15 | Structural Documentation | Non-engineered structure | Building 6 – Columns appear to rest directly on masonry walls, and are possibly embedded in plain concrete, with small pipe sections used as columns additionally beams connecting these pipe columns have small sections. | Propose strengthening work as required and submit to Pakistan Accord for approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S16 | Structural Documentation | Non-engineered structure | Building 6 – Columns appear to rest directly on masonry walls, and are possibly embedded in plain concrete, with small pipe sections used as columns additionally beams connecting these pipe columns have small sections. | Implement strengthening work as required. | S15+3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S17 | Structural Documentation | Non-engineered structure | Building 7 – Double-height steel structure with lattice columns and no lateral bracing. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if it is adequate. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S18 | Structural Documentation | Non-engineered structure | Building 7 – Double-height steel structure with lattice columns and no lateral bracing. | Propose strengthening work as required and submit to Pakistan Accord for approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S19 | Structural Documentation | Non-engineered structure | Building 7 – Double-height steel structure with lattice columns and no lateral bracing. | Implement strengthening work as required. | S18+3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S20 | Other Damage/Defects | Moisture ingress | This concerns Building 3, first floor, where persistent moisture ingress has been observed on the slab and beams. Overtime water ingress can lead to corrosion and spalling of main beams which could affect their structural capacity. The primary cause of this issue is the lack of waterproofing on the roof. | Identify the cause of the damage / source of water ingress and propose measures to prevent further water damage. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S21 | Other Damage/Defects | Moisture ingress | This concerns Building 3, first floor, where persistent moisture ingress has been observed on the slab and beams. Overtime water ingress can lead to corrosion and spalling of main beams which could affect their structural capacity. The primary cause of this issue is the lack of waterproofing on the roof. | Inspect damage to the slab and beam and propose repairs to structure. Submit report capturing above to Accord for approval. | 3 months | 2025-09-26 | 2025-12-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S22 | Other Damage/Defects | Moisture ingress | This concerns Building 3, first floor, where persistent moisture ingress has been observed on the slab and beams. Overtime water ingress can lead to corrosion and spalling of main beams which could affect their structural capacity. The primary cause of this issue is the lack of waterproofing on the roof. | Implement work. Continue to monitor for future signs of water ingress/damage. | S21+3 months | 2025-12-26 | 2026-03-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S23 | Other Damage/Defects | Health and Safety | It concerns with inadequate edge protection which present a risk of potential injury resulting from slip, trip or fall from Roof during the access and maintenance of services. In Building 2, no adequate edge protection is provided on roof. | Provide adequate edge protection on the roof and on any other part of the factory with the same issue. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress
[9 empty] | Initial | [11 empty] | S24 | Other Damage/Defects | Health and Safety | It concerns with inadequate edge protection which present a risk of potential injury resulting from slip, trip or fall from Roof during the access and maintenance of services. In Building 1A no adequate edge protection is provided on roof. | Provide adequate edge protection on the roof and on any other part of the factory with the same issue. | 1 month | 2025-09-26 | 2025-10-26 | AGREE |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cable support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
anotehr electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixtures
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | Chemicals handling | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Chemicals storage | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Diesel storage | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Gas storage | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1