## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
2024-05-14
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Azgard-9 -2.5 KM Off, Manga, Raiwind Road, District Kasur, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-05-14
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | The single line diagram available on site lacked sufficient details and was not up-to-date. | Engage a qualified electrical engineer to develop comprehensive electrical single line diagrams for the entire facility. | 3 months | We will develop the comprehensive electrical single line diagrams for the entire facility. Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | The factory lacked essential electrical layout drawings, including small power layouts, lighting layouts, and containment layouts. | Consult a qualified engineer to upgrade all electrical layout drawings. Submit Electrical Layout drawings to the Pakistan Accord for review. | 6 months | We will upgrade all electrical drawings. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Circuit breakers | During the inspection it was observed that Circuit breaker mounted on side wall near solar room is neither in containment nor have any weather proofing. | Identify and replace circuit breaker and enclosure that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 1 months | DB purchasing is in process & it will be installed soon |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | During the inspection, the Compressor room metallic stand of control Distribution Board is equipped with a live circuit breaker at high risk of short circuit. | The live circuit breaker will be de-energized, insulated, grounded, and tested. If necessary, it will be replaced or relocated. Actions will be documented, and regular inspections scheduled. | 1 month | DB purchasing is in process & it will be installed soon |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Circuit breakers | During the inspection, it was observed that a hanging single pole circuit breaker found in compressor control room. | The hanging single pole circuit breaker will be secured, insulated, and tested for safety. If necessary, it will be replaced or relocated. All actions will be documented, and regular inspections scheduled. | 1 month | Already removed it from compressor control room |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | During the inspection, a live circuit breaker found resting on metallic enclosure of a dryer can cause any abnormal fault due to its abrupt position | The live circuit breaker resting on the metallic enclosure will be immediately secured, insulated, and properly positioned. If needed, it will be replaced or relocated. | 1 month | DB purchasing is in process & it will be installed soon |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Hot Spots | During the inspection several signs abnormal temperatures were observed: - LT Room (Power House): 90°C to 110°C at breaker-contactor links and termination. - Compressor Circuit breaker at 100°C on Red phase. - Cable terminals (Denim Unit) at 87.2°C on cable connector | Finding shows that high temperatures need immediate rectification by addressing and repairing the cause of abnormal temperature in cable joint, which may involve overloading, connection tightening, or replacement of faulty cable joint. | 1 month | We have rectify the issue which is causing abnormal temperature & resolve it (Connection tightening) |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | There was no updated thermographic survey report available on site. | Carry out independent thermographic survey. | E7 + 6 months | We will conduct an independent thermography |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Earthing system | There was an incomplete earthing system found throughout the facility, the earth pits were present but the earth was just connected to the main LTs. No Earth connection was observed in power distribution board placed in LT room | All earth connections must be connected to earth pits via their respective distribution board. Connect all metal bodies of Electric panels to the earth terminal within electric panels. | 2 months | we have almost connect every distribution board with earthing via earth pit. Remaining DBS work is is progress. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | There was an incomplete earthing system found throughout the facility, No Earth connection was found to capacitor placed in between two LT panel enclosures | All earth connections must be connected to earth pits via their respective distribution board. Connect all metal bodies of Electric panels to the earth terminal within electric panels. | E9 + 1 month | we have removed the capacitor bank panel which is without earthing system. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | In most of the areas, earth bonding of cable tray, metal structures, metal tables and motor frames found missing such as: - No Earth found connected to externally placed transformer metallic fencings - No equipotential bonding on hard water tank control panel and associated equipment | Metal that is likely to be live near electrical installation shall be bonded with earth to avoid any hazard. | E10 + 1 month | We will connect earthing with transformer fence. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, The cabling and wiring below the LT panel (in motor area), were found to be bunched and crossing over sharp edges of existing cable trays. This setup is in close proximity to a wet pump environment, increasing the risk of insulation failure and short circuits. | The bunched cabling and wiring below the LT panel will be rerouted to avoid sharp edges and properly secured. Additional insulation or protective conduit will be applied as needed. Identify and replace cables that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 1 month | we will add additional insulation to protect cables. Cables will be identified and replaced as necessary if not suitable for the environmental conditions in which they are installed |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, The HT panel doors were found to be non-lockable while the VCB was energized. Additionally, there was a lack of mechanical interlocking between the HT doors and the CB "ON" status, which requires immediate rectification | Ensure all HT panel doors are lockable and interlocked both mechanically and electrically to avoid any hazard. | 1 month | We have locked all HT panels also we have done mechanical interlocking with door. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, Almost all cubicles in the LT room of the powerhouse lack proper cable dressing and show evident signs of poor maintenance. Additionally, there are no appropriately installed safety covers inside the cubicles, causing busbars to be exposed. | All electric panel must be maintained regularly, ensuring cable dressing, terminal tightening and removal of lint and dust. Cable dressing need to be done for each distribution board. | 2 months | Safety covers purchasing is in progress & will be install soom also cable dressing will be proper dressed. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, The training room distribution board was found in a very poor condition. A tangle of cables and unmounted circuit breakers were observed, which could potentially lead to short circuits or fires inside the panel | Schedule a proper maintenance records to monitor and control. Ensure no cable bunching and splicing at all. All electrical components must be protection against fire risk factors. | 6 month | Factory will make a proper maintenance records to monitor and control. Ensure no cable bunching and splicing at all. All electrical components must be protection against fire risk factors. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Loop Connection | During our inspection, we observed the loop connections within the overall panel: - Loop connections in multiple DBs of production area - Loop connections in lighting DB of stitching and packing area. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. | 1 month | Factory will modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Multiple Connections | While conducting our survey we have noticed that Multiple connections were found on a circuit breaker inside panel, one MCB/MCCB is running many circuits in sharing, power socket in canteen area that is inadequate. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. | 2 months | Factory will modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Openings | During inspection it was observed at various location that Multiple distribution board found to have openings | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 2 months | Company will Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Adequate accessibility | During the survey, it was noted that an interlocking of generators is placed at backdoor of a LT panel, it was noted that: distribution panel mounted in cutting area is at a very low height, NGR is placed in control room maintaining less clearance from either side and Compressor panel at roof is stuck with storage material | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 2 months | Factory will provide Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, it was found that dust and dirt had accumulated inside many distribution boards. Few examples are listed below: - All cubicle in LT room is filled with link and dust - Non-maintained condition observed in control room cubicles that can be evident | Ensure that electrical panels are cleaned, inspected and free from lint, dust and dirt. Maintain the schedule of cleaning and maintenance for each distribution board that is in dirt and dusty condition. | 1 month | We have cleaned all IT panels & auxiliary panels. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During inspection it was observed that two of the roofs were equipped with Solar Panels but there was no Lightning Protection system (LPS) is installed in the facility. Any document related to LPS assessment was also not found. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 6 months | LPS system is already installed on solar system, for rest of the building we will provide risk assessment report and submit to Accord for review. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This related to the Power House: There was a conventional FADS system, but due to a faulty card, the system was non-operational at the time of inspection.Non-compliant fire detection and alarm system, not a listed system that does not provide alarm and notification features consistent with building standards. | This related to the Power House: (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) for the Powerhouse complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E22 + 1 months | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E23 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E24 + 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E25 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E26 + 3 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This related to the Spinning Unit: There were a few push buttons for the notification system in the spinning area, but the alarm sound was insufficient in the auto cone and storage areas. Non-compliant fire detection and alarm system, not a listed system that does not provide alarm and notification features consistent with building standards. | This related to the Spinning Unit: (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) for the Spinning Unit complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E28 + 1 months | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E29 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E30+ 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E31 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E32 + 3 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This related to the Denim Unit: A push button notification system was in place, but the alarm was not loud enough to be heard in the Air Jet Looms area.Non-compliant fire detection and alarm system, not a listed system that does not provide alarm and notification features consistent with building standards. | This related to the Denim Unit: (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) for the Denim Unit complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E34 + 1 months | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E35 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E36 + 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E37 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E38 + 3 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This related to the Associated Areas: Many areas had no FADS coverage, including the ETP (main gate), mosque, canteen, Gow downs area, bale-press machines, and other associated areas. These locations neither had coverage nor any reliable detection and notification system in case of fire. Non-compliant fire detection and alarm system, not a listed system that does not provide alarm and notification features consistent with building standards. - | This related to the Associated Areas: (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) for the Associated Areas complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E40 + 1 months | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E41 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E42+ 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E43 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E45 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E44 + 3 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E46 | Emergency Lighting | Provided but insufficient | During the inspection of the emergency lighting system, it was noted that several emergency lights did not comply with building standards: - Many walkways of finishing Area in Stitching Building - All walkways of spinning area specifically at auto cone machines - Stair case of power house - Fabric storage area in stitching building | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation | 3 months | Factory will make comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation |  |  |  | In Progress
3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E47 | Emergency Lighting | Provided but non-functional | During the inspection of the emergency lighting system, we found that only a few areas had emergency lights, but they did not work. Area having faulty emergency lights are: - Non-compliant emergency light provided in canteen area - Non-functional emergency light in power house control room - Emergency light arrangement combine circuit for multiple equipment - Insufficient emergency light in production area | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 3 months | Emergency light installed throughout the facility including control room. |  |  |  | In Progress
3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E48 | Emergency Lighting | General Lighting | During the inspection the general lighting throughout the facility was assessed. The following observations were noted: - Several locations were identified as lacking sufficient general lighting like LT Room and Transformer Room. | Conduct a thorough assessment of lighting throughout the facility to find areas with insufficient illumination. Install additional lighting fixtures in these spots to ensure adequate brightness. Ensure the new lighting design meets safety and efficiency guidelines to provide clear visibility for all tasks and emergency situations. | 1 month | Factory will assess lighting throughout the facility to find areas with insufficient illumination and will ensure clear visibility for emergency situations. |  |  |  | In Progress
3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E49 | Emergency Lighting | General Lighting | During the inspection the general lighting throughout the facility was assessed. The following observations were noted: - General lighting was controlled directly from the breakers within the Distribution Boards rather than through standard light switches. | Reconfigure the electrical control system to ensure that general lighting is operated via standard wall-mounted light switches instead of circuit breakers. This involves installing appropriate switches and rewiring the control circuits as per the National Electrical Code (NEC) and other relevant electrical safety standards. Ensure that all switches are easily accessible and clearly labelled to enhance operational efficiency and safety. | 1 month | Factory will reconfigure the electrical control system to ensure that general lighting is operated via standard wall-mounted light switches instead of circuit breakers |  |  |  | In Progress
3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E50 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | During the inspection, it was observed that several areas, such as the generator room, appeared to be systematically designed to prevent heat accumulation; however, there were no apparent natural air entry points or ventilation fans. Similarly, the ventilation in transformer rooms was insufficient. Few examples are defined below: - Excessive heat found at generator room having lack of ventilation - Both ventilation and illumination were missing in transformer room - Force air blow observed in electric panels refer | Equip generator and transformer rooms with adequate ventilation systems, ensure all areas have sufficient lighting, utilize forced air blowing systems in electric panels. Conduct regular maintenance checks, and install temperature monitoring systems in high-heat. | 3 months | Factory will provide proper Equipment generator and transformer rooms with adequate ventilation systems, ensure all areas have sufficient lighting, utilize forced air blowing systems in electric panels. |  |  |  | In Progress
3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E51 | Generator, Transformer & Sub-Station Room | Working clearance | During the survey, it was noted that various locations exhibited inadequate work clearance within facility such as : - Insufficient clearance observed for busbars to the panel backdoor - Lack of working clearance in control panel behind LT panels - HT panels not in used are found untagged and hindering the passage - Inadequate placement of NGR compromising the working clearance | Reorganise the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. | 2 months | Factory will reorganise the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. |  |  |  | In Progress
3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E52 | Generator, Transformer & Sub-Station Room | Battery | During inspection, it was observed that the batteries of generator had some fluid spills as we had seen fluid spread off the batteries. Furthermore, the battery placement for generator was inadequate and their terminal are bare. This is not safe and have a risk of electrocution as well as causing fire if exposed to combustible materials. Few examples are given below: - Inadequate battery and charger arrangement in generator room - Battery fluid found spilled on batteries - Uncovered bare copper terminals and fluid spills on batteries | Hazardous substance placed inside the Generator room need to be placed in their designated area. Bare terminals of battery need to be covered. Battery placement and cabling will be adjusted to comply with BS-7671 and NFPA standards, alongside performing a thorough periodic maintenance of the generator. | 2 months | Factory will remove hazardous substance placed inside the Generator room need to be placed in their designated area. Bare terminals of battery need to be covered. |  |  |  | In Progress
3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E53 | Cabling & Wiring | Cables support and protection | During the inspection it was observed that the cables are not protected and supported properly throughout the facility. This includes many of the following areas such as: - Cable laying out of containment at entrance of Compressor room - Loose cable with no containment in compressor room - Conduit and containment for water cooler wiring connections - Loose wiring on Monforte stenter control room in proximity of gas pipes | All kind of unsupported wiring must be laid with proper dressing and their relevant conduits. Install appropriate cable containment arrangement for the electrical system. | 3 months | Factory will provide All kind of unsupported wiring must be laid with proper dressing and their relevant conduits. Install appropriate cable containment arrangement for the electrical system. |  |  |  | In Progress
3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E54 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. PVC Tapping joints found in different distribution boards. Some areas of our finding are listed below: - Spliced cable observed in multiple distribution boards. - Spliced cables and inadequate connection in generator room - Lack of proper power plugs in compressor room - Spliced cables observed at multiple locations in production | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022) Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 3 months | Factory will Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections. And Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections |  |  |  | In Progress
3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E55 | Cabling & Wiring | Cable trench and channel cleanliness | It was noted in several locations that cleanliness was not being maintained within the electrical panels and trunking system. | Ensure that all electrical trunking and enclosures are cleaned, inspected, and free from dust and dirt. | 3 months | Factory will ensure that all electrical trunking and enclosures are cleaned, inspected, and free from dust and dirt. |  |  |  | In Progress
3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E56 | Cabling & Wiring | Colour coding | During inspection it was observed that multiple cable is equipped with wrong colour cables at Denim Unit. | All distribution board need to be wired with correct colour coding as per building standard. | 3 months | Factory will do distribution board need to be wired with correct colour coding as per building standard. |  |  |  | In Progress
3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E57 | Cabling & Wiring | Fixtures | It was observed that several three-phase receptacles were installed on the ground beside a cable tray, and some were left inside the electrical panel, lying freely on metal sheets. Areas of concern include: - Inadequate fixture observed at first floor power house on IT Rack - Damaged power sockets observed made of wood at various locations - Damage fixtures observed in multiple office area - Damaged fixtures in transformer room | Damage power receptacles need to be replaced. Every two-pin plug should be replaced with a three-pin plug which has a proper earth wire connected to it. Ensure that all power receptacles are fixed properly in place and their cables are protected as well. | 2 months | Factory will replace every two-pin plug should be replaced with a three-pin plug which has a proper earth wire connected to it. |  |  |  | In Progress
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
2024-05-14
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Azgard-9 -2.5 KM Off, Manga, Raiwind Road, District Kasur, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-05-14
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found at following locations: (list not exhaustive): - Escape doors are lockable throughout all buildings - Doors into stairs swing against the direction of escape (Spinning building) - Sliding doors serve for escape from areas with more than 10 occupants (Spinning building, Finishing & Weaving building) | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard | 1 month | Factory will remove all locking devices on escape routes. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found at following locations: (list not exhaustive): - Escape doors are lockable throughout all buildings - Doors into stairs swing against the direction of escape (Spinning building) - Sliding doors serve for escape from areas with more than 10 occupants (Spinning building, Finishing & Weaving building) | Provide easily opening mechanisms complying with Pakistan Accord Building Standard Section 1 Clauses 1.4 & 1.5. | 3 months | Factory will ensure that there are easily opening from inside mechanisms on all doors on exit routes. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Exit access | Exit access route have multiple issues include (list not exhaustive): - Obstructions on escape route Storage area (Spinning building) & Sewing area 2nd floor (Garments & Dyeing building) - Trip hazards on escape route Canteen area 1st floor (Garments & Dyeing building) - Insufficient headroom along escape | Present all proposed plans for the remedial works to Pakistan Accord complying with Pakistan Building Code Standard Section 10.5.2 for review before upgrading works begin. | 4 months | Facility Present all proposed plans for the remedial works to Pakistan Accord complying with Pakistan Building Code Standard Section 10.5.2 for review before upgrading works begin. Drawings will be shared once it is ready. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Exit access | Exit access route have multiple issues include (list not exhaustive): - Obstructions on escape route Storage area (Spinning building) & Sewing area 2nd floor (Garments & Dyeing building) - Trip hazards on escape route Canteen area 1st floor (Garments & Dyeing building) - Insufficient headroom along escape | Provide required headroom clearance height as per plan reviewed by Pakistan Accord. Ensure obstruction free exit access all the time. | F3 + 4 months | 1.Headroom clearance height will be finalized after civil team has provided the drawings. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Travel distance | Travel distances didn't meet the limits (list not exhaustive): - Common path of travel distances exceeds permitted limits at Dyeing chemical platform (Sizing, Re-beaming, Dyeing & Ball Warping building), office area 1st floor (Garments & Dyeing building) - Total travel distance exceeds permitted limit at cone rewinding (Spinning building), Old dyeing (Garments & Dyeing building), Sewing, Finishing Lower height 1st floor (Garments & Dyeing building), Finishing (Finishing & Weaving building), Sizing & Re-beaming (Sizing, Re-beaming, Dyeing & Ball warping building), Yarn/Fabric Storage (Yarn/ Fabric & Recycling building) | Review travel distances throughout the site to ensure that all travel distances meet the limits in Pakistan Accord Building Standard. Travel distance assessments are based on the assumption that exit stairways are protected and have adequate protected Exit discharge. Where this is not the case there may be additional excessive travel distances to address. Where necessary develop a plan for providing additional exits, submit to Accord for review and approval prior to commencing rectification works on site. | 4 months | Factory will hire a competent person to review the existing layouts and propose amendments to provide travel distances to emergency exits within limits. Plans showing proposals will be submitted to Accord for review. Factory will implement the plan submitted earlier to Accord for review |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Exit discharge | Exit discharge routes outside the building not sufficiently protected, This includes: - Stair discharge route is not fire separated from the building S-1, S-2, S-5, S-6 stairs (Garments & Dyeing building) - Stairs discharging S-7 into a roof (Garments & Dyeing building) - Stairs discharge inside building S-1, S-2, S-5 and S-6 (Garments & Dyeing building) | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge routes. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | Once drawing will be prepared it is shared with the assessment team in order to get final approval for further proceeding. Drawings will be prepared and shared with accord pakistan for final approval |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Exit discharge | Exit discharge routes outside the building not sufficiently protected, This includes: - Stair discharge route is not fire separated from the building S-1, S-2, S-5, S-6 stairs (Garments & Dyeing building) - Stairs discharging S-7 into a roof (Garments & Dyeing building) - Stairs discharge inside building S-1, S-2, S-5 and S-6 (Garments & Dyeing building) | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Accord Building Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). - Penetrations through doors are not permitted. All fire doors require self-closers. Doors into exit discharge routes should be kept closed (but not always locked). - All penetrations through walls into stair discharge routes need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. Ensure external escape routes are relocated so that they do not pass via high-risk areas. | F6 + 4 months | Once drawings will be finalized and reviewed by Accord it will be shared with civil team for implementation of the works. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit signage | Exits (e.g. escape stair or final exits leading directly outside the building) were not clearly marked by approved exit signs. The following deficiencies have been observed on site, including (list not exhaustive): - Missing exit signs at discharge routes (Spinning building) - Missing illuminated exit signs in production areas (All buildings) - Missing exit signs in Office corridor area (Garments & Dyeing building) - Missing exit signs at roof(Garments & Dyeing building) | Rectify signs and provide illuminated exit signage to comply with Pakistan Accord Standard. | 2 months | All signs have been displayed at all locations where highlighted. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit signage | Exits (e.g. escape stair or final exits leading directly outside the building) were not clearly marked by approved exit signs. The following deficiencies have been observed on site, including (list not exhaustive): - Missing exit signs at discharge routes (Spinning building) - Missing illuminated exit signs in production areas (All buildings) - Missing exit signs in Office corridor area (Garments & Dyeing building) - Missing exit signs at roof(Garments & Dyeing building) | Ensure that all exit signage is checked periodically and in good working condition. | 3 months | Facility will cross check its compliance in daily routine visits and also during internal audits. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Fire Rated Construction | Structural fire rating | The following deficiencies have been observed on site, including (list not exhaustive): - Steel structure of the building or parts of the building is not fire rated (mezzanine level floor of Garments & Dyeing building) | Factory consultant to identify level of fire protection needed for the structure based on height, area, provision of sprinklers and frontage space around the building, in accordance with Pakistan Accord Building Standard and reference to NFPA 5000 cl.7.6.2. | 4 months | Facility will make a plan to rectify this concern after discussing with the higher management and submit to Accord for review. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Fire Rated Construction | Structural fire rating | The following deficiencies have been observed on site, including (list not exhaustive): - Steel structure of the building or parts of the building is not fire rated (mezzanine level floor of Garments & Dyeing building) | Implement the proposal for addressing the fire protection of the structure based on proposal reviewed by Pakistan Accord. | F10 + 4 months | Facility will make a plan to rectify this concern after discussing with the higher management. Plan previously reviewed by Accord will be implemented |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Fire Rated Construction | Separation of high-risk areas | Increased fire risk areas were not fire separated from the rest of the building using the following: (list not exhaustive): - Electrical panel rooms are not fire separated from Office area (Utility building) - Generator room is not fire separated from LT/ HT panel rooms (C11, Utility building) | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. electrical rooms, generator rooms etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | Drawings will be prepared and shared with accord pakistan for final approval. Once drawings will be finalized it is shared with civil team for further work. Fire resistant walls and doors will be made as per requirements. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Fire Rated Construction | Separation of high-risk areas | Increased fire risk areas were not fire separated from the rest of the building using the following: (list not exhaustive): - Electrical panel rooms are not fire separated from Office area (Utility building) - Generator room is not fire separated from LT/ HT panel rooms (C11, Utility building) | Provide fire rated construction as agreed with in the documents reviewed by Accord. | F12 + 4 months | Fire resistant walls and doors will be made as per requirements. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Rated Construction | Separation of shafts | Shafts were not enclosed in 2-hour fire resisting construction with 90 minutes fire rated doors. (list not exhaustive): - Lift shafts are not fire separated from production floors (A8 Garments & Dyeing building) | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Technical engineering team will review the structure and then share the drawings with Accord for review |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Fire Rated Construction | Separation of shafts | Shafts were not enclosed in 2-hour fire resisting construction with 90 minutes fire rated doors. (list not exhaustive): - Lift shafts are not fire separated from production floors (A8 Garments & Dyeing building) | Ensure that the proposed design modifications are implemented and operational on site. | F14 + 4 months | Fire rated separation of lift will be completed, including brickwork/ fire rated assemblies and adequate and door operating mechanism, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Rated Construction | Separation of occupancies | Different occupancy types not fire separated from each other. (list not exhaustive): - Office area is not fire separated from the production Lower height 1st floor (Garments & Dyeing building) | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors) | 4 months | First drawing will be prepared and then shared with Accord for review prior to the final approval. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Rated Construction | Separation of occupancies | Different occupancy types not fire separated from each other. (list not exhaustive): - Office area is not fire separated from the production Lower height 1st floor (Garments & Dyeing building) | Ensure that the above plan is implemented on site. | F17 + 4 months | Fire rated separation of occupancies will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Storage | Extensive storage areas were not fire separated from the rest of the building using 2-hour fire resisting walls with 90 minutes fire rated doors. (list not exhaustive): - Storage areas are not fire separated from the rest of the building (Spinning building) - Storage areas on production floor exceed permitted limits as per Pakistan Accord standard, Cutting area (Garments & Dyeing building) Inspection/ Finishing area (Finishing & Weaving building), Ball Warping area (Sizing, Re-beaming, Dyeing building and Ball Warping building) | Identify all designated storage areas. Identify which storage areas will follow the in-process storage limitations described above and which will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details for review and approval by Accord prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | First internal initial assessment will be conducted in order to identify all areas and then drawings will be prepared accordingly. after final approval, civil work will be initiated as per plan. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Storage | Extensive storage areas were not fire separated from the rest of the building using 2-hour fire resisting walls with 90 minutes fire rated doors. (list not exhaustive): - Storage areas are not fire separated from the rest of the building (Spinning building) - Storage areas on production floor exceed permitted limits as per Pakistan Accord standard, Cutting area (Garments & Dyeing building) Inspection/ Finishing area (Finishing & Weaving building), Ball Warping area (Sizing, Re-beaming, Dyeing building and Ball Warping building) | Ensure that the above plan is implemented on site. | F18 + 4 months | Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant (Garments & Dyeing building) - Missing standpipe outlets in stairs (Garments & Dyeing building) | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, | 4 months | Factory will submit design documentation for a standpipe system and supporting infrastructure that shows full compliance of the Suppression System (SUPS) with NFPA 14 to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant (Garments & Dyeing building) - Missing standpipe outlets in stairs (Garments & Dyeing building) | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F20 + 1 month | For any components that need to be imported factory will submit documentation to Pakistan Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant (Garments & Dyeing building) - Missing standpipe outlets in stairs (Garments & Dyeing building) | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F21 + 4 months | Factory will advice Accord when all materials in-housed |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant (Garments & Dyeing building) - Missing standpipe outlets in stairs (Garments & Dyeing building) | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F22 + 3 months | Once installation of the SUPS system is complete, factory will submit full "as-built" documentation of the system to Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant (Garments & Dyeing building) - Missing standpipe outlets in stairs (Garments & Dyeing building) | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F23 + 3 months | Factory will advise Accord when installation fully functional |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant (Garments & Dyeing building) - Missing standpipe outlets in stairs (Garments & Dyeing building) | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F24+ 3 months | Factory will arrange a full T&C inspection for Accord on site |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Fire pumps | The following deficiencies have been observed on site, including (list not exhaustive): - Fire pump set is not listed | Prepare design and drawings showing how the fire pump room and equipment will be rectified to comply with NFPA 20 as part of the supporting infrastructure to the SUPS system by following steps (1) to (6) above | 18 months | Facility will relate the drawing with NFPA 20 and then share with accord pakistan for final approval. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Water supply | The following deficiencies have been observed on site, including (list not exhaustive): - No separate fire water tank - No dedicated portion of shared water tank for fire safety purposes - Fire tank uses an external reservoir, and the water quality requirements are not met | Develop a rectification plan to provide adequate fire water supplies. The plan should demonstrate compliance with NFPA 22. Submit the plan to Accord for review and approval prior to implementation on site. | 3 months | Factory will review arrangement of water supply and storage requirements to cover fire water supply as part of supporting infrastructure for the SUPS system, in accordance with NFPA 22 & 24, and submit to Accord for reviewy. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Water supply | The following deficiencies have been observed on site, including (list not exhaustive): - No separate fire water tank - No dedicated portion of shared water tank for fire safety purposes - Fire tank uses an external reservoir, and the water quality requirements are not met | Implement the plan agreed with Pakistan Accord. | 18 months | Separate water tank will be provided for fire water supplies. Facility will conduct third party water testing from approved EPA lab and then make decision accordingly. Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Hazardous Materials | Chemicals handling | The following deficiencies have been observed on site, including (list not exhaustive): - Large amounts of chemicals in production areas old Dyeing area (Garments & Dyeing building) & New dyeing area (Sizing, Re-beaming, Dyeing & Ball Warping building) | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standard that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. | 3 months | Facility will prepare a proper policy and procedure against chemical handling for the building. Organogram will be prepared and duties will be assigned accordingly. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Hazardous Materials | Chemicals handling | The following deficiencies have been observed on site, including (list not exhaustive): - Large amounts of chemicals in production areas old Dyeing area (Garments & Dyeing building) & New dyeing area (Sizing, Re-beaming, Dyeing & Ball Warping building) | Implement the chemical handling strategy on site as agreed with Pakistan Accord. | F29 + 3 months | Facility will prepare a proper policy and procedure against chemical handling for the building. Organogram will be prepared and duties will be assigned accordingly. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Hazardous Materials | Chemicals storage | The following deficiencies have been observed on site, including (list not exhaustive): - Flammable materials are not stored in a fire separated room (Chemical & General storage building) | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms | 4 months | Chemical store map will be prepared as per NFPA 30 and placement of chemicals will be done as per the compatibility chart. Locations and other fire relevant concerns will be addressed in the layout. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Hazardous Materials | Chemicals storage | The following deficiencies have been observed on site, including (list not exhaustive): - Flammable materials are not stored in a fire separated room (Chemical & General storage building) | Implement the above plan on site. All chemical storage areas to be compliant with Accord Standard. | F31 + 4 months | layout will be designed and share with the accord pakistan for final approval. Proposals for placement of chemicals will be provided following proposals reviewed previously by Accord |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Hazardous Materials | Gas storage | The following deficiencies have been observed on site, including (list not exhaustive): - Gas storage areas are not fire separated from the rest of the building workshop area (Spinning building) Workshop area (Workshop, Training room & Canteen building) and Canteen area (Garments & Dyeing building) | Prepare drawings showing gas storage areas with proposals for safe storage of gas cylinders complying with requirements of NFPA 58. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of gas storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms | 4 months | 1. Engage a qualified architect/engineer to prepare drawings for gas storage areas. 2. Submit drawings to Accord for review and approval prior to rectification works. Implement the works in accordance with proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2024-05-14
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Azgard-9 -2.5 KM Off, Manga, Raiwind Road, District Kasur, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-05-14
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Cracking | Column | Based on an initial assessment, the peripheral columns of the weaving building in the Denim unit, are cracked due degradation of concrete. Additionally, these columns show signs of water ingress. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking. Also to understand the condition of concrete and rebar and therefore determine the residual load capacity. | 2 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Cracking | Column | Based on an initial assessment, the peripheral columns of the weaving building in the Denim unit, are cracked due degradation of concrete. Additionally, these columns show signs of water ingress. | Propose measures to prevent future damage and works to repair the existing damage. | 2 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Column | Based on an initial assessment, the peripheral columns of the weaving building in the Denim unit, are cracked due degradation of concrete. Additionally, these columns show signs of water ingress. | Carry out the remedial works. Monitor the building for future signs of water damage. | S2 + 4 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Structural System | Lateral stability system | In Garments Unit Steel shed (over First Floor) has no apparent lateral stability system provided | Building Engineer to review the design and check for the lateral stability for the mentioned Steel structure. | 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Structural System | Lateral stability system | In Garments Unit Steel shed (over First Floor) has no apparent lateral stability system provided | Identify any strengthening works that may be required and submit to Pakistan Accord for review | 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural System | Lateral stability system | In Garments Unit Steel shed (over First Floor) has no apparent lateral stability system provided | Implement any remedial works required and based on the assessment submitted earlier for review | S6 + 4 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Other Damage/Defects | Corrosion of reinforcement | Beaming Hall building and sample warehouse in Denim Unit, which was constructed in 2006 with a single ground floor, has several columns with exposed reinforcement due to honeycombing. Paint is applied to the exposed reinforcement without proper treatment. To prevent corrosion of the reinforcement, appropriate treatment is necessary. | Remove existing paint and loosen aggregates and apply high strength grout mixture | 6 months | Noted and will be repainted. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Other Damage/Defects | Spalling concrete | This issue concerns whole factory,Concrete spalling caused by water ingress in the slab is prevalent in all units of the factory. • The roof slab concrete is spalled on the various buildings in garment unit, and the reinforcement is exposed to weathering conditions. Water ingress into the slab due to a lack of waterproofing on the roof slab has caused the concrete to spall. • Garments unit building 1: Water ingress leads to rusting of the reinforcement, which causes slab to spall. | Building Engineer to carry out a full condition survey to document cases of water damage/corrosion/spalling across the factory. In each case inspect areas with water damage, confirm the source of the damage, propose measures to prevent further damage and submit to Pakistan Accord for review. | 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Other Damage/Defects | Spalling concrete | This issue concerns whole factory,Concrete spalling caused by water ingress in the slab is prevalent in all units of the factory. • The roof slab concrete is spalled on the various buildings in garment unit, and the reinforcement is exposed to weathering conditions. Water ingress into the slab due to a lack of waterproofing on the roof slab has caused the concrete to spall. • Garments unit building 1: Water ingress leads to rusting of the reinforcement, which causes slab to spall. | Carry out repair works as proposed in design submitted previous to Pakistan Accord for review. | S8 + 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Other Damage/Defects | Spalling concrete | • In the Denim unit weaving building, the concrete in the upstand beams is damaged, exposing the reinforcement to weathering. | Building Engineer to carry out a full condition survey to document cases of water damage/corrosion/spalling across the factory. In each case inspect areas with water damage, confirm the source of the damage, propose measures to prevent further damage and submit to Pakistan Accord for review. | 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Other Damage/Defects | Spalling concrete | • In the Denim unit weaving building, the concrete in the upstand beams is damaged, exposing the reinforcement to weathering. | Carry out repair works as proposed in design submitted previous to Pakistan Accord for review. | S10 + 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Other Damage/Defects | Spalling concrete | • Dormitory unit: Concrete spalling is observed in the roof slab, likely due to water ingress causing reinforcement rusting. | Building Engineer to carry out a full condition survey to document cases of water damage/corrosion/spalling across the factory. In each case inspect areas with water damage, confirm the source of the damage, propose measures to prevent further damage and submit to Pakistan Accord for review. | 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Other Damage/Defects | Spalling concrete | • Dormitory unit: Concrete spalling is observed in the roof slab, likely due to water ingress causing reinforcement rusting. | Carry out repair works as proposed in design submitted previous to Pakistan Accord for review. | S12 + 3 months | Detailed assessment will be carried out by structural engineer and retrofitting proposal will be provided accordingly for approval. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Structural Documentation | Undocumented modification | This relates to the dyeing building in Garments unit. Large structural steel brackets have been installed to strengthen beams of the dyeing range building. This consists of a H-section column fixed to the existing RC column and an inclined steel strut supporting the beam. No structural drawings are available for the existing retrofitted structure. The factory was unable to explain why the brackets were installed. No deflection or other signs of distress was observed in the RC beams. It appears that the roof slab and beams have been repaired for spalling concrete. | Building Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation.Submit as-built documents to Pakistan Accord for review | 6 months | All retrofitting works are done according to detailed assessment. All related drawings & design reports will be provided for review. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Structural Documentation | Documentation unavailable | This relates to whole factory. Complete as-built architectural and structural drawings were unavailable. Some of the provided as-builts did not match the existing structure in the Garments Unit. List of missing drawings are as follows: • 7 of garment units • 16 of Denim unit • 23 of spinning Unit • 14 of Utilities Unit • 1 of Dormitory | Building Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 4 months | All missing documents will be prepared as listed. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Structural Documentation | Documentation unavailable | This relates to whole factory. Complete as-built architectural and structural drawings were unavailable. Some of the provided as-builts did not match the existing structure in the Garments Unit. List of missing drawings are as follows: • 7 of garment units • 16 of Denim unit • 23 of spinning Unit • 14 of Utilities Unit • 1 of Dormitory | Submit as-built documents to Pakistan Accord for review | S15 +2 months | All missing documents will be prepared as listed. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Other Damage/Defects | Health and Safety | Following items present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of roof. • No safe access to the Upper roof exhibited significant instability, indicating inadequate attachment to the structural system. | Provide safe access across the roof of the building for services and maintenance. Consider installation of steel stairs. | 3 months | Roof access will be restricted until the installation of stairs. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Other Damage/Defects | Health and Safety | Following items present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of roof. • No edge protection is provided to the roofs of all the buildings. | Provide an appropriate roof edge protection to all accessible roofs. | 3 months | Roof access will be restricted until the installation of roof railing / parapet. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1