## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
24-May-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Nishat Mills Ltd. (Apparel Division) Unit-2 , 2 Km Nishat Avenue, off 22 Km Ferozpure Road, Lahore, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 24-May-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | It was observed that the single-line diagrams were missing some vital information. Furthermore, every distribution panel was either missing or containing a SLD that was not updated. | Develop comprehensive electrical single-line diagrams for the entire facility by the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. Implement a regular review and update process for the single-line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | 3 months | 1. Facility will prepare the sample of SLD in accordance with the requirement outlined in section 514.9.1 of BS7671 18th edition + A2 (2022) and submit for approval to accord pakistan team for further proceeding of all SLD's. 2. Facility will make a plan for reviewing the single lines diagrams as outlined in section 514.9.1 of BS7671 18th edition + A2 (2022) and submit for approval to accord pakistan team. 3. Facility will make a training plan for maintenance personnel & emergency responders in order to ensure the interpretation of SLD's. 3. Facility will engage 3rd party for the training of maintenance personnel & emergency responders in order to ensure the interpretation of SLD's. Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | We observed that the electrical layout drawings were incomplete. This needs to be rectified to eliminate any type of confusion and to have clear schematics of the electrical network. | Develop comprehensive electrical layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). | 2 months | Facility will consult with consultant and will prepare a plan & layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Will submit to Accord team for review and further developing of comprehensive electrical layout drawings. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | We observed that the electrical layout drawings were incomplete. This needs to be rectified to eliminate any type of confusion and to have clear schematics of the electrical network. | Consult a Qualified Engineer to complete electrical layout drawings (lighting ,power, fire alarm, earthing, cable containments etc.) that depict the location and specifications of all electrical equipment and outlets to match the existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. There might be too much information to effectively display on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are visible and up to date with the current electrical installation. | E2 + 4 months | Facility will consult with electrical consultant and will prepare a plan & electrical layout drawings following the requirements outlined in remediation plan. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | it was observed that circuit breaker ratings were oversized compared to the cables connected. This issue relates to Building 69. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current carrying capacity. If the breaker has adjustable settings, it must be configured to allow current within the cable ampacity after applying derating factors. | 1 month | Facility will consult with consultant and prepare a evaluation plan to evaluate circuit breaker ratings and cable sizes for all circuits in whole facility to ensure that all breakers and cables are in accordance with Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Circuit breakers | it was observed that circuit breaker ratings were oversized compared to the cables connected. This issue relates to Building 69. | Consult a qualified engineer who can assess the situation and provide specific recommendations tailored to your electrical system and needs. They can also ensure that any changes or upgrades are done safely and in compliance with electrical codes and standards. Replace the rusted terminals with new ones. Also, develop a periodic maintenance program to protect your electrical network from these types of issues. | E4 + 1 month | 1. Facility will consult with a qualified consultant electrical engineer to verify the existing electrical system in accordance with the electrical codes and standards. 2. Facility will conduct the survey and make a plan to replace rusted terminal (if Any) with the consultation of qualified electrical engineer. Moreover, facility will make a preventive maintenance plan of electrical network to ensure the system working in accordance with electrical codes and standards & submit to accord team for review and approval. Factory will replace breakers or cables with components needed to match cables and breaker sizes and ensure that breaker size is less than current carrying capacity |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Thermography survey identified several hotspots which were identified This issue relates to the entire facility which includes buildings: (69, 69A, Workshop, Utility) | It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring the safe and reliable operation of the electrical systems. Thermographic survey should be conducted after every 6 months. | E5 + 6 months | 1. Facility will conduct survey and will take immediate corrective action with the consultation of qualified electrical engineer on identified hot spot. 2. Facility will engage 3rd party twice a year for thermographic survey. Facility will share thermographic report with Accord at 6-monthly intervals |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was noted that multiple distribution panels exhibited instances where cable mesh was either stretched or in physical contact with each other, wires lacked proper tagging. This issue relates to the entire facility which includes buildings: (69, Workshop, Utility) | Refer to BS-7671 for proper wiring and installation of cables. A distribution panel should be IP-rated, and installed adequately with enough space for working, and cables should be properly lugged with visible colour coding and tagging. Make sure that each panel has a single-line diagram installed at the panel. | 2 months | 1. Facility with conduct a survey under the supervision of qualified consultant and ensure wiring and installation of cables as per BS-7671. 2. Facility will get reviewed the SLD's by consultant and accord team. After approval will be display at each panel. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | Earth layout design was not available at site. | Develop an earth layout design in accordance with BS-7671. Submit the design to Pakistan Accord for review. | 3 months | Facility will consult with consultant and prepare the earthing system layout design in accordance with the BS-7671 and get it reviewed by Accord team for final approval. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Earthing system | The main termination from the earth pit was rusted. Distribution of earth from earth pit to floor distribution was missing. Earth bars were installed in an open environment without any covering. | Develop a periodic maintenance program to inspect and test the system to ensure its effectiveness. Over time, soil conditions and other factors like rust and environmental exposure can affect the performance of the earthing system. Every earth bar should be installed in an IP-rated distribution board if they are installed in an open environment to protect them from environmental damage. | E8 + 1 months | 1. Facility will conduct a survey and prepare a plan accordingly to install the IP rated distribution boards. 2. Facility will discuss with accord team regarding the frequency of periodic maintenance plan. 3. Facility will prepare the periodic maintenance plan for the earthing system and get it reviewed by the consultant and accord team for final approval. Facility will ensure that every earth bar is installed in an IP-rated distribution board and, if they are installed in an open environment, to protect them from environmental damage |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | The bonding mechanism was not as per standard. Cable trays, distribution boards, inner sheets, as well as metallic gates or cages were not provided with proper equipotential bonding. The bonding mechanism provided was seen as damaged. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | E9 + 2 months | Facility will conduct a survey to identify all cable trays, distribution boards, inner sheets, metallic gates or cages are earthed properly as per BS 7671 regulation 411.3.1.2. Facility will ensure that all exposed conductive parts are bonded to the main earthing terminal. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Multiple Connections | It was noticed that in almost every panel in the facility, there was a multi-looping of wires. This issue relates to the entire facility which includes buildings: (69, 69A, Workshop, Utility) | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each circuit following Section 430 of BS 7671 18th Edition + A2 (2022) | 2 months | Facility will conduct a survey under the supervision of qualified electrical engineer for identification and rectification of multi-looping of wires in accordance with the section 430 of BS7671 edition + A2 (2022). Facility will ensure that ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each circuit |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Adequate accessibility | It was observed that behind the utility building, there was a distribution board that was blocked by the hose pipe and could not be opened due to inadequate accessibility. | Inspect the facility for inadequate accessibility of electrical panels and remove everything that is blocking the area around it. Develop a periodic maintenance program to ensure that each distribution panel has enough space to reach. | 1 month | 1. Facility has prepared plan to relocate the highlighted panel and soon evidence will be shared with accord team. 2. Moreover, facility will make sure the adequate accessibility of electrical panels through routine inspections. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Lint & dust inside panel board | It was observed that there were various distribution panels and power boards that were full of dust, lint, and fluffs. | Inspect the electrical system and clean areas that are exposed to fluff and dust. Close any unwanted ingress for the prevention of lint and dust. Develop a periodic maintenance program to clean and clear all the electrical systems from fluff and dust. | 1 month | Facility has taken immediate action and clean all DB's by qualified electrical staff. Facility will prepare a plan to ensure the closure of all unwanted ingress of electrical panels/ DB's to avoid fluff, lint & dust. 3. Facility will prepare the periodic maintenance plan and submit to accord team for review and approval. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was observed that a lightning protection system was installed in the facility, but the facility does not have any design related to the installation of a lightning protection system | Consult a qualified engineer and conduct a risk assessment to evaluate the vulnerability of the facility in accordance with IEC-62305. | 1 month | 1. Facility will consult with consultant and conduct the risk assessment in accordance with IEC-62305. 2. Facility will prepare the lightning protection system layout design in accordance with the IEC-62305 for design and installation and get it reviewed by accord team for final approval. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was observed that a lightning protection system was installed in the facility, but the facility does not have any design related to the installation of a lightning protection system | If the risk assessment report favours installing a lightning protection system, seek guidance from qualified lightning protection professionals or engineers who specialize in designing and installing lightning protection systems. The lightning protection system must comply with IEC-62305 standards for design and installation. | E14 + 5 months | Facility will consult with qualified lightning protection professional and prepare the lightning protection system layout design in accordance with the IEC-62305 for design and installation/modification and get it reviewed by accord team for final approval. Once installation complete and tested Facility will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS was installed for building 69, workshop, and Utility building. | Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Facility will hire competent consultant for the review of design drawings. Once design and drawings were finalized will share with accord team for review and for further commencement of work. Facility will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS was installed for building 69, workshop, and Utility building. | Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E16 + 1 months | If any new listed components need to be purchased Facility will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS was installed for building 69, workshop, and Utility building. | Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E17 + 4 months | Once all materials have been in-housed Facility will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS was installed for building 69, workshop, and Utility building. | Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E18 + 5 months | Facility will hire competent consultant for the review of design drawings. Once design and drawings were finalized will share with accord team for review and for further commencement of work. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS was installed for building 69, workshop, and Utility building. | Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E19+ 3 month | Facility will hire competent consultant for the review of design drawings. Once design and drawings were finalized will share with accord team for review and for further commencement of work. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant FADS was installed for building 69, workshop, and Utility building. | Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E20 + 3 months | Facility will hire competent consultant for the review of design drawings. Once design and drawings were finalized will share with accord team for review and for further commencement of work. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Building 69A FADS were not as per NFPA-72 | Submit the design documentation of FADS of building 69A along with equipment certifications (MCP, Sounder, Flasher, smoke detector, heat detector) for review. | 3 months | Facility will provide the documentation pertaining to FADS of building 69A along with requested equipment certification. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Building 69A FADS were not as per NFPA-72 | Consult a qualified engineering firm that can design and install a new or upgrade the existing addressable FADS. Make sure, that FACPs are synced with each other and have a common link to notify every building. | E22 + 2 month | Facility will procure the modules to sync FACPs with each other of whole building (All Floors). Moreover, design review is in process once received will share with accord team for review and further commencing of work. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Emergency Lighting | Provided but non-functional | It was observed that the backup power supply of emergency lights was not sufficient. Emergency lights were either too dim or not working. The battery backup was too low. This issue relates to the entire facility which includes: (69, 69A, Workshop, Utility) | Consult a qualified engineer to prepare design drawings for entire facility as per Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation, and submit design document to Accord for its review. | 2 months | Facility will consult with consultant and prepare a design drawing of emergency exit lights for the whole facility in accordance with the building code of pakistan fire safety provision 2016. Once design and drawing were drafted will shared with accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Emergency Lighting | Provided but non-functional | It was observed that the backup power supply of emergency lights was not sufficient. Emergency lights were either too dim or not working. The battery backup was too low. This issue relates to the entire facility which includes: (69, 69A, Workshop, Utility) | Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the emergency lighting design submitted earlier. | E24+ 1 month | Facility will consult with consultant and prepare a design drawing of emergency exit lights for the whole facility in accordance with the building code of pakistan fire safety provision 2016. Once design and drawing were drafted will shared with accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Emergency Lighting | Provided but non-functional | It was observed that the backup power supply of emergency lights was not sufficient. Emergency lights were either too dim or not working. The battery backup was too low. This issue relates to the entire facility which includes: (69, 69A, Workshop, Utility) | Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E25+ 3 month | Facility will consult with consultant and prepare a design drawing of emergency exit lights for the whole facility in accordance with the building code of pakistan fire safety provision 2016. Once design and drawing were drafted will shared with accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Emergency Lighting | Provided but non-functional | It was observed that the backup power supply of emergency lights was not sufficient. Emergency lights were either too dim or not working. The battery backup was too low. This issue relates to the entire facility which includes: (69, 69A, Workshop, Utility) | Once installation of the Emergency lighting system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E26 + 2 months | Facility will consult with consultant and prepare a design drawing of emergency exit lights for the whole facility in accordance with the building code of pakistan fire safety provision 2016. Once design and drawing were drafted will shared with accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Emergency Lighting | Provided but non-functional | It was observed that the backup power supply of emergency lights was not sufficient. Emergency lights were either too dim or not working. The battery backup was too low. This issue relates to the entire facility which includes: (69, 69A, Workshop, Utility) | Factory to advise Pakistan Accord when emergency lighting system installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E27 + 2 months | Facility will consult with consultant and prepare a design drawing of emergency exit lights for the whole facility in accordance with the building code of pakistan fire safety provision 2016. Once design and drawing were drafted will shared with accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Cabling & Wiring | Cables support and protection | It was observed that the cables were not properly laid on cable trays. This issue relates to the entire facility which includes the building: (69, Workshop, Utility) | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) | 2 months | Facility will conduct survey and make a plan for rectification in accordance with BS 7671 18th edition + A2 (2022). Facility will secure cables with appropriate supports and insulate any exposed connection |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Cables support and protection | It was observed that the cables were not properly laid on cable trays. This issue relates to the entire facility which includes the building: (69, Workshop, Utility) | Elevate the cable trays off the floor to eliminate tripping hazards and prevent damage from foot traffic by Regulation 522.6 of BS7671 18th Edition + A2 (2022) | E29 + 1 month | This is to be discuss with accord team for better understanding. Facility will take measures to eliminate tripping hazards from cable trays and prevent damage from foot traffic |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Cabling & Wiring | Splicing of cables | Wire connectors and joints were used all over the facility. This issue relates to the entire facility which includes buildings: (69, 69A, Workshop, Utility) | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections by Regulation 526.1 of BS7671 18th Edition + A2 (2022) Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections by Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. Replace the directly inserted power wires with proper power plugs to ensure safe and secure connections. | 2 months | There are few areas in which this observation exist. Facility will take immediate corrective action in accordance with mentioned standards and submit evidences to the Accord team. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Cabling & Wiring | Fixtures | It was noticed that there were several places where power sockets were installed inadequately with cable ties. This issue relates to the entire facility which includes buildings: (69, Workshop, Utility) | Replace every damaged socket with a new one. Every power socket should be installed in a manner that complies with the standards. Develop a periodic maintenance program to ensure every piece of equipment is installed properly, is in good condition, and can be used safely. | 2 months | There are few areas in which this observation exist. Facility will take immediate corrective action in accordance with remediation plan and submit evidences to the accord team. Moreover, facility will prepare periodic maintenance plan and submit for review and final approval. |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
24-May-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Nishat Mills Ltd. (Apparel Division) Unit-2 , 2 Km Nishat Avenue, off 22 Km Ferozpure Road, Lahore, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 24-May-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Non Compliant Locking door mechanism has been observed in following areas -Examples are: •Escape doors are lockable- Building #1(Main exit door, Roof access door), Building #2 – Ground floor doors, Building#3 – All doors, Building#4- All doors | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | Facility has installed all doors having opening outside without any locking mechanism from inside moreover, locking mechanism from outside will be replace with any of suitable locking mechanism. 1. Facility will conduct survey regarding the available Non-Compliant locking doors mechanism from outside. 2. Facility will make a plan to remove the outside lockable door mechanism. 3. Furthermore, roof access door locking mechanism will be discussed with accord team. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Non Compliant Locking door mechanism has been observed in following areas -Examples are: •Escape doors are lockable- Building #1(Main exit door, Roof access door), Building #2 – Ground floor doors, Building#3 – All doors, Building#4- All doors | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | Facility has installed all doors side hinged and all doors opening are in the direction of escape route. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Non Compliant Locking door mechanism has been observed in following areas -Examples are: •Escape doors are lockable- Building #1(Main exit door, Roof access door), Building #2 – Ground floor doors, Building#3 – All doors, Building#4- All doors | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | 3 months | Facility will ensure the routine inspection in order to make sure the easy access to emergency exits. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Folowing stairs are not protected due to Unprotected openings : Building #2 – S10, S6 stairs Stair discharge route is not fire separated from the building – Building #1-S8 stairs | Remove fire load from stairs | 2 weeks | Facility will consult with consultant and will prepare a plan & design as per the accord pakistan building standard and will submit to accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Folowing stairs are not protected due to Unprotected openings : Building #2 – S10, S6 stairs | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and approval prior to rectification works. The drawings should cover: -Layout showing the location of fire rated walls/doors to protect the stairs. -Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks).Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | Facility will consult with consultant and will prepare a plan & design as per the accord pakistan building standard and will submit to Accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Folowing stairs are not protected due to Unprotected openings : Building #2 – S10, S6 stairs | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: -All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. | F5 + 4 months | Facility will consult with consultant and will prepare a plan & design as per the accord pakistan building standard and will submit to accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Folowing stairs are not protected due to Unprotected openings : Building #2 – S10, S6 stairs | All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. | 4 months | Facility will consult with consultant and will prepare a plan & design as per the Accord pakistan standard and will submit to accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit access | Stair discharge route is not fire separated from the building – Building #1-S8 stairs | Where stairs discharge within a building, a fire separated corridor shall be provided that leads outside building. Provide all fire doors with self-closing and self-latching devices, and push-bar panic hardware where required in accordance with Pakistan Accord Building Standard. If fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system. | 4 months | Need discussion with accord team. Factory will prepare drawings showing proposal for protecting access to building exit or alternative arrangement to ensure safe egress from internal stairway and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit access | Stair discharge route is not fire separated from the building – Building #1-S8 stairs | Where stairs discharge within a building, a fire separated corridor shall be provided that leads outside building. | F8 + 4 months | Factory will provide protection or alternative arrangement to allow safe passage from internal stair to outside, in accordance with proposals submitted previously to Accord for review |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits - Building#2-Ground floor (Mezzanine office area) – Store office area -common path 38 m | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. | 4 months | Facility has already taken corrective measure and alternative secondary exit has been provided. Facility will submit the design and evacuation map to the accord team for review and approval. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits - Building#2-Ground floor (Mezzanine office area) – Store office area -common path 38 m | Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | Facility will conduct a survey to review travel distance from all areas in the building to ensure the travel limit defined in pakistan accord building standard. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits - Building#2-Ground floor (Mezzanine office area) – Store office area -common path 38 m | Implement the plan previously reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F11 + 4 months | Facility will implement the Accord approved plan. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated- Building #1 – Exit#1 discharge is compromised | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect stair discharge routes Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes | 4 months | In CAP report of accord pakistan they just highlighted the storage of combustible material outside exit #1 of building # 1. Facility have removed combustible material to clear the escape route and there is no need of drawing moreover we will discuss to accord team in case of any further corrective action required. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated- Building #1 – Exit#1 discharge is compromised | Ensure external exit discharge routes are adequately fire separated from the rest of the building. | 4 months | Facility will conduct the survey to ensure that all discharge routes are fire separated as per the pakistan accord building standard. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated- Building #1 – Exit#1 discharge is compromised | Ensure external escape routes do not pass close to unprotected high-risk areas | F14 + 4 months | Facility have removed combustible material to clear the escape route and there is no need of drawing moreover we will discuss to accord team in case of any further corrective action required. |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Escape stair condition | There are no handrails – Building #1 – Stair S 7 | Prepare drawing showing proposed handrail installation and ensure implementation through out facility Provide handrails on exit stairs where handrails are missing | 4 months | Need discussion with accord team as observation mentioned in CAP report was not match with the recommended remedial plan or nor with the remediation plan. Factory will instal handrails on exit stairs where missing |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Number of exits | Single exit from some of the occupied floors - Building#2-Ground floor – Store office area – Single means of escape for people >30 people – common path 38 m There are areas with over 500 occupants that are only served by 2 exits - Building #2-Level 1-Canteen - Single exit for people >650 | Review each floor and area to ensure that the number of exits complies with Accord Building Standard. | 4 months | 1. Facility has already taken corrective measure and alternative secondary exit has been provided. Facility will submit the design and evacuation map to the accord team for review and approval. 2. Building # 2 canteen floor 2 emergency exits were already provided. However, facility will revisit the drawing with the consultant and make a plan, design or administrative control measures as per the pakistan accord standard. After the preparation of plan, design or administrative measures, this will submit to accord team for review and for further correction or commencing rectification works. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Number of exits | Single exit from some of the occupied floors - Building#2-Ground floor – Store office area – Single means of escape for people >30 people – common path 38 m There are areas with over 500 occupants that are only served by 2 exits - Building #2-Level 1-Canteen - Single exit for people >651 | Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Accord for review and approval prior to commencing rectification works. | 4 months | After the preparation of plan, design or administrative control measures, this will submit to accord team for review and for further correction or commencing rectification works. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Number of exits | Single exit from some of the occupied floors - Building#2-Ground floor – Store office area – Single means of escape for people >30 people – common path 38 m There are areas with over 500 occupants that are only served by 2 exits - Building #2-Level 1-Canteen - Single exit for people >652 | Implement the above plan as agreed with Accord. Exit numbers from all floors and parts of the building should comply with Accord Building Standard. | F18 + 4 months | Facility will implement the Accord approved plan. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Separation of shafts | Lift shafts are not fire separated – Building #1 – Level 1 lift shafts, building #2- Mezzanine floor & Level 1 lift shafts not separated | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors enclosing vertical shafts. Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Facility will consult with consultant and will prepare a plan & design as per the accord standard of all lift shafts and will submit to accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Separation of shafts | Lift shafts are not fire separated – Building #1 – Level 1 lift shafts, building #2- Mezzanine floor & Level 1 lift shafts not separated | Ensure that the proposed design modifications are implemented and operational on site. | F20 + 4 months | Facility will implement the Accord approved plan. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Separation of occupancies | Large office areas not fire separated from the production areas – Building #2 – Ground floor, Mezzanine, Building #1- level 1 | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building Proposed fire separation details (including fire rating of walls and doors) | 4 months | Facility will consult with Accord team Facility will prepare drawings showing proposed fire separating construction to high-risk areas and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Separation of occupancies | Large office areas not fire separated from the production areas – Building #2 – Ground floor, Mezzanine, Building #1- level 2 | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F22 + 4 months | Facility will implement the Accord approved plan. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building -- Building #1- Level 1, Building#2-Level 1, Building#2 – Ground floor Areas with excessive storage in production area does not meet miscellaneous in-process storage requirements (listed above) - Building#1-Ground floor | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need to be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Facility will consult with consultant and will prepare a plan & design as per the Accord standard of production storage and will submit to accord team for review and further commencing of the work. However, facility will consult with accord pakistan team regarding the fire separation of production and storage area. Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building -- Building #1- Level 1, Building#2-Level 1, Building#2 – Ground floor Areas with excessive storage in production area does not meet miscellaneous in-process storage requirements (listed above) - Building#1-Ground floor | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F24 + 4 months | Facility will implement the Accord approved plan. Facility will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Hazardous Materials | Chemicals storage | Large amounts of chemicals in production areas- Building #1– Ground floor – Production area | Develop a chemical handling strategy for the building. Identify dangerous chemicals, how they will be used and handled, the standards that will be followed, and the people responsible for the implementation of the strategy. Submit to Accord for review. | 4 month | There is a misunderstanding in this observation. Attached picture is of temporarily stone storage area which is not combustible. Moreover, this will be discussed with accord team for correction. |  |  |  | Pending Verification
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Hazardous Materials | Chemicals storage | Large amounts of chemicals in production areas- Building #1– Ground floor – Production area | Implement the chemical handling strategy on site as agreed with Accord. | F26 + 4 months | There is a misunderstanding in this observation. Attached picture is of temporarily stone storage area which is not combustible. Moreover, this will be discussed with accord team for correction. |  |  |  | Pending Verification
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Hazardous Materials | Gas storage | Gas storage areas are not fire separated from the rest of the building - Building#4-Ground floor (canteen area) | Prepare drawings showing gas storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of gas storage areas Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) Ventilation provisions | 4 months | Facility will consult with consultant and will prepare a plan & design as per the accord pakistan building standard and will submit to accord team for review and further commencing of the work. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Hazardous Materials | Gas storage | Gas storage areas are not fire separated from the rest of the building - Building#4-Ground floor (canteen area) | Implement the above plan on site. All gas storage areas to be compliant with Accord Standard. | F28+ 4 months | Facility will implement the Accord approved plan. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System Inadequate records of maintenance of Emergency lighting Inadequate records of maintenance of Fire Doors | Prepare maintenance schedule for all life safety systems. | 3 months | Facility will devise maintenance schedule for all life safety systems as per Accord standard. |  |  |  | Pending Verification
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System Inadequate records of maintenance of Emergency lighting Inadequate records of maintenance of Fire Doors | Prepare a schedule of proposed system maintenance. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | Facility will devise maintenance schedule for all life safety systems as per Accord standard. |  |  |  | Pending Verification
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System Inadequate records of maintenance of Emergency lighting Inadequate records of maintenance of Fire Doors | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep maintenance records. | F31 + 3 months | Facility will devise maintenance schedule for all life safety systems as per Accord standard. |  |  |  | Pending Verification
3 | 8 |  | 142 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
24-May-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Nishat Mills Ltd. (Apparel Division) Unit-2 , 2 Km Nishat Avenue, off 22 Km Ferozpure Road, Lahore, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 24-May-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Structural System | Lack of local stability | This is related to the Portal frame of building-1 Prefabricated shed, where the steel cable bracing between vertical member observed missing on site. | Factory to install the missing bracing cables as needed and ensure cables are tightened so that they can act in tension. | 6 months | Facility has taken the corrective action as per accord pakistan building standard. Missing bracing has been installed moreover, all loose bracing have been tighten as per the manufacturer guidelines to ensure the tension. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Structural Documentation | Documentation unavailable | This observation relates to buildings 3 and 4, where the structural drawings of both the buildings and architectural documentation of building 3 is unavailable. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built structural and architectural drawings. | 6 months | Facility will consult with consultant regarding the review of building 3 & 4 structural drawings. Moreover, architectural documentation is available and also provided to accord team during inspection. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5
3 | 8 |  | 112 | 421 | 6 | 5
3 | 8 |  | 113 | 421 | 6 | 5
3 | 8 |  | 114 | 421 | 6 | 5
3 | 8 |  | 116 | 421 | 6 | 5
3 | 8 |  | 117 | 421 | 6 | 5
3 | 8 |  | 118 | 421 | 6 | 5
3 | 8 |  | 119 | 421 | 6 | 5
3 | 8 |  | 120 | 421 | 6 | 5
3 | 8 |  | 121 | 421 | 6 | 5
3 | 8 |  | 122 | 421 | 6 | 5
3 | 8 |  | 123 | 421 | 6 | 5
3 | 8 |  | 124 | 421 | 6 | 5
3 | 8 |  | 125 | 421 | 6 | 5
3 | 8 |  | 126 | 421 | 6 | 5
3 | 8 |  | 127 | 421 | 6 | 5
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1