## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
23-Oct-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Mount Fuji Textiles Limited, Plot # D-146, D-148 Site Area Karachi 75700
[8 empty] | Date of Initial Inspection | [12 empty] | 23-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | DBs & Elec Protection Systems | Earthing system | This relates to the Block B (Weaving & Stitching) on level(s) L05 - 5th Floor. The earthing system isn't adequate, there are sections of the facility that has no earthing system installed. | Earthing cables should be extended from panels to sockets and equipment, using a suitable size and type of conductor, to provide a low-resistance path for fault currents to flow to the earth. Earthing connections should be provided for all panels, using proper clamps, lugs, and bolts, to connect the earth continuity conductor to the earth electrode. | 06 months | Earthing connections will be provided for all panels, using proper connectors. Now, we have installed earthing system according to standard. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | DBs & Elec Protection Systems | Earthing system | This relates to the Block B (Weaving & Stitching) on level(s) L05 - 5th Floor. The earthing system isn't adequate, there are sections of the facility that has no earthing system installed. | Sewing machines should be connected with three core cables (with earth cable), and the earth wire should be connected to the metal frame of the machine. | 06 months | All sewing machines will be connected with three core cables as required Now, we are maintaining 3 core cables on all electrical appliances and have installed the earthing system. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Earthing system | This relates to the Block B (Weaving & Stitching) on level(s) L05 - 5th Floor. The earthing system isn't adequate, there are sections of the facility that has no earthing system installed. | Socket outlets should be wired in three core cable (with earth cable), and the earth wire should be connected to the metal casing of the socket. | 06 months | Now, we are maintaining socket with 3 core cables on all electrical appliances and have installed the earthing system. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | Diagrams & Drawings | Electrical layout drawing | This relates to the Block B (Weaving & Stitching) on level(s) L05 - 5th Floor. The as built schematics do not show the details of the earthing system. | The as built schematics should show the details of the earthing system, such as the type, size, and location of the earth electrode, the size and type of the earth continuity conductor, the earthing lead, and the earthing connections. | 08 months | Factory will submit as-built schematics to Accord for review. We have installed earthing system and consulted with an engineering firm to develop detailed diagrams and technical specifications. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that the following panels displayed abnormally high temperatures, meaning it is highly likely a panel could cause fire ignition: - Block A (Home textiles) on level(s) L04 - 4th Floor. - Block A (Home textiles) on level(s) L01 - 1st Floor. - Block B (Weaving & Stitching) on level(s) L00 - Ground Floor, L03 - 3rd Floor. - Block E (Warehouse) on level(s) L03 - 3rd Floor and L02 - 2nd Floor - Block E (Warehouse) on levels L01 - 1st Floor, L02 - 2nd Floor - Block A (Home textiles) on level(s) L03 - 3rd Floor | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 1 month | We have thoroughly inspected all electrical panels and addressed the identified ab normality. Now, all electrical panels are normal temperatures. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that this panel displayed abnormally high temperatures in multiple locations, meaning it is highly likely a panel could cause fire ignition | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 6 months. | 1 month | We have established a schedule for thermography inspections to be conducted every three months. Factory will share schedule with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that this panel displayed abnormally high temperatures in multiple locations, meaning it is highly likely a panel could cause fire ignition | Carry out thermograph survey every 6 months. | 06 months | We have established a schedule for thermography inspections to be conducted every three months. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Block B (Weaving & Stitching) on level(s) . Outgoing circuits do not (individual) breaker protection. | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes. | 03 months | We have consulted an engineering firm to analyse installations, circuits, and breakers, identifying non-conformities. Attached is the proposal and quotation for your review. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Block B (Weaving & Stitching) on level(s) . Outgoing circuits do not (individual) breaker protection. | Replace cables with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 03 months | We are replacing mismatched breakers and ensuring that all new installations use the correct combination of cable and breaker sizes according to their load requirements. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of lint, dust and dirt. | 03 months | We have now maintained all panels to prevent the ingress of lint, dust, and dirt. |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from lint, dust and dirt. | 03 months | We have established a schedule for cleaning all electrical panels on a monthly basis. Factory will share schedule with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Earthing system | This relates to the Block F (Office & Canteen) on level(s) L00 - Ground Floor. Within the electrical panel a plastic cable connector has been used in place of a neutral bar. The neutral bar has exposed connections which are very close to coming in contact with the panel frame, which could result in an electrical fault within the panel. The panel frame doesn't have an earth connection to protect against contact with a live conductor. | Isolate and disconnect the cable terminal block. Replace the terminal block with terminal bar that is fixed in place and isolated from the panel body. | 06 months | We have removed highlighted panel. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Cabling & Wiring | Cables support and protection | This relates to the Block F (Office & Canteen) on level(s) L00 - Ground Floor. The battery connections are exposed. | Cover electrical connections using suitable insulating material. | 03 months | Now, we have provided covers for battery terminals. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Loop Connection | This relates to the Block F (Office & Canteen) on level(s) L01 - 1st Floor. Looped cable instead of busbar inside of electrical panels. | Remove cable and replace with a longer length of busbar. | 03 months | Now, we have removed highlighted panels |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Cabling & Wiring | Cables support and protection | This relates to the Block E (Warehouse) on level(s) L01 - 1st Floor. Cables are not correctly fixed in place to prevent movement. Protection isn't provided to prevent mechanical damage to cables. | Provide protection to prevent cables being walked on that could cause damage to the cables. | 03 months | Machines have now been shifted, and the wiring has been removed. |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Cabling & Wiring | Cables support and protection | This relates to the Block E (Warehouse) on level(s) L01 - 1st Floor. Cables are not correctly fixed in place to prevent movement. Protection isn't provided to prevent mechanical damage to cables. | Re-terminate all cabling in and out of the panel. Secure all cable to a method of cable containment (for example cable conduit). Provide missing Cable gland below the isolator | 03 months | Machines have now been shifted, and the wiring has been removed. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Block E (Warehouse) on level(s) L02 - 2nd Floor. Damaged electrical equipment has not been replaced. | Equipment should be isolated from the electrical distribution system (turned off). If the equipment is required to operate it should be replaced before doing so. | 02 months | Machines have now been shifted, and the wiring has been removed. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Cabling & Wiring | Cables support and protection | This relates to the Block F (Office & Canteen) on level(s) L00 - Ground Floor. Face plate on socket is not installed correctly. | Fix face plates into the correct position | 03 months | Now, fixxed face plates on correct position. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Block F (Office & Canteen) on level(s) L00 - Ground Floor. Breaker installed on wall with exposed electrical connections (breaker are not designed to be installed outside of panels) and adjacent to combustible material (curtain when closed). | Remove all combustible material from within and around all electrical equipment in the facility. Ensure that all electric circuitry is clear of combustible materials. | 03 months | We have removed combustible materials around the electrical panels. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Block F (Office & Canteen) on level(s) L00 - Ground Floor. Breaker installed on wall with exposed electrical connections (breaker are not designed to be installed outside of panels) and adjacent to combustible material (curtain when closed). | Clean all electrical rooms, removing any materials not required by or associated with the electrical systems. Create a cleaning schedule for electrical rooms and electrical equipment. | 03 months | We have removed combustible materials around the electrical panels. |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Block F (Office & Canteen) on level(s) L00 - Ground Floor. Breaker installed on wall with exposed electrical connections (breaker are not designed to be installed outside of panels) and adjacent to combustible material (curtain when closed). | Conduct periodic maintenance schedule and maintain the records. | 03 months | Factory will share schedule with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Diagrams & Drawings | Electrical layout drawing | An electrical load balance document was not available during the inspection. The absence of an electrical load balance document during an inspection indicates that there might not be a record of the distribution of electrical loads in the factory. This document is crucial as it helps prevent issues like overheating, power-quality problems, and energy loss that can occur with unbalanced loads. | Create an Electrical Load Balance Document: Engage an electrical engineer to conduct a thorough assessment of the electrical loads in the factory. This should include all equipment, machinery, lighting, and any other systems that use electricity. | 08 months | We have consulted an engineering firm to provide services for electrical load balancing. The attached quotation is provided for your review and guidance. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Diagrams & Drawings | Electrical layout drawing | An electrical load balance document was not available during the inspection | Keep the electrical load balance document updated and readily available for future inspections. This will ensure that the document can be easily accessed and reviewed during inspections. | 08 months | The electrical load balance document will be regularly updated, matched with on-site conditions, and readily available for future inspections |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Emergency Lighting | Provided but non-functional | This relates to emergency lighting throughout all buildings. - Emergency lighting provided but did not function in test – e.g., Block F Mosque and canteen had nonfunctioning lights, including in stairway - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs – e.g., not all stairs in Block F have emergency lighting, Ground Level of Block F - No emergency lighting in some rooms / areas | Provide maintenance on the emergency lighting system to ensure that the current installation is fully functional. Regularly test the emergency lighting system on each floor | 03 months | We have established a schedule for periodic testing of the emergency lighting system. Factory will share schedule with Accord for review. |  |  |  | Pending Verification
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Emergency Lighting | Provided but non-functional | This relates to emergency lighting throughout all buildings. - Emergency lighting provided but did not function in test – e.g., Block F Mosque and canteen had nonfunctioning lights, including in stairway - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs – e.g., not all stairs in Block F have emergency lighting, Ground Level of Block F - No emergency lighting in some rooms / areas | Provide additional emergency fixtures and system to supply adequate illumination along the means of egress from all areas in accordance with Pakistan Accord Building Code and NFPA 101. | 03 months | Emergency lighting system will be upgraded to meet Pakistani Accord Building Standard and maintained in proper working condition. |  |  |  | Pending Verification
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. Some of the related issues include: - New addressable fire alarm system being installed in Block A, but not yet functional. - No or incomplete coverage of fire alarm devices in some areas, such as Block A (mosque building, director office), Block B (boiler room, chiller room), Block C (most of the building ), Block D (Ground Level, Level 1), Block E (Ground Level, production on Level 2, offices on Level 3, workshops), and Block F (Ground Level - fire alarm room, fire pump room, offices, security room, Level 1 open rest area, Level 2 kitchen, Level 1, 2, and 3 dormitories) - Detectors not installed top of stairs throughout all buildings - Insufficient number of manual fire alarm box(es) throughout all buildings inspected, not always provided near exit doorways - Sounders inaudible due to low volume or high ambient noise in many areas | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 03 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | Pending Verification
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E26 +1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | Pending Verification
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E27 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E28 +5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E29 + 3 months | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | Pending Verification
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E39 + 3 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | Pending Verification
3 | 8 |  | 141 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 142 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 143 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 144 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 145 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 146 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 147 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 148 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 149 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 151 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 152 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
23-Oct-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Mount Fuji Textiles Ltd,Plot # D-146, D-148 Site Area Karachi 75700
[8 empty] | Date of Initial Inspection | [12 empty] | 23-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Exit capacity | Residential dormitories require more stringent life safety measures than industrial occupancies, and should comply with provisions that address sleeping risks, which were not sufficiently addressed for the Block F dormitory. | Alternative arrangements must therefore be sought for the dormitory as continuing the use of the building for this purpose is not appropriate. | 4 months | Dormitories have been relocated, Now Dormitories areas unoccupied. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Exit capacity | Residential dormitories require more stringent life safety measures than industrial occupancies, and should comply with provisions that address sleeping risks, which were not sufficiently addressed for the Block F dormitory. | If use of the building as a dormitory is to be reinstated then provide a design and related documentation to Accord for review before remediation works commence. Design must demonstrate compliance with the Pakistan Accord Building Standard, which largely relies on the life safety requirements outlined in the Pakistan Building Code - Fire Safety Provisions (2016). | 4 months | Dormitories have been relocated, Now Dormitories areas unoccupied. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Exit capacity | Residential dormitories require more stringent life safety measures than industrial occupancies, and should comply with provisions that address sleeping risks, which were not sufficiently addressed for the Block F dormitory. | Implement remediation design to comply with Pakistan Accord Building Standard for dormitory occupancy | F2 + 4 months | Dormitories have been relocated, Now Dormitories areas unoccupied. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed throughout all buildings on the majority of exit doors. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | We are in the process of developing a plan to replace the locking features with alternative locking options for security purposes after the shutdown of the department. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Factory will provide easy opening from inside mechanisms on all doors on escape routes. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Number of exits | Single means of egress is provided, but more than one means of escape is required. This was observed in - Block A: Mezzanine Office area to Ground Level - Block B: South stairway connects Levels 5, 4, and 3 but does not provide a direct exit - Block C: Middle area with old compressors and chiller circulation has one exit through a storage area - Block F: Ground Level office area - Block D: Level 1 has a single means of escape | Provide proposals for alternative means of egress from the areas identified to ensure there are sufficient number of exits in accordance with the Pakistan Accord Building Standard and submit to Pakistan Accord for review | 4 months | Factory will prepare drawings showing proposals and obstacles for alternative means of escape and submit to Accord for review prior to the rectification works Block A: We were unable to identify an alternative escape route. Block B: We are unable to identify direct escape exit stairway. Block C: We have identified location, will began work soon. Block F: We have identified a location, but an electrical control panel is present. We plan to relocate it and create an escape route. Block D: We have identified the escape route and will begin work soon |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Number of exits | Single means of egress is provided, but more than one means of escape is required. | Provide alternative means of egress from the areas identified by implementing proposals reviewed by Pakistan Accord and in accordance with the Pakistan Accord Building Standard | F6 + 4 months | Alternative means of escape will be will be completed, according to proposal previously reviewed by Accord. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | All exit stairways throughout all buildings inspected are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. Furthermore: - Storage was observed in exit stairways and exit passageways – e.g., Block A , Block E west stair, Block F exterior stairs - Automatic door closers are not installed/functioning in several locations – e.g., Block E east stair - Doors normally required to be kept closed are secured in the open position by being tied open or by obstructions being wedged between the door and door frame. | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as needed. Remove all combustible material from stairs | 2 weeks | Block A: Now, we have removed storage from stairways and exit passageways. We have provided training to employees to ensure that the emergency exit door remains secure and keep close. Additionally, we have removed all combustible materials from the stairs. |  |  |  | Pending Verification
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | All exit stairways throughout all buildings inspected are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs; - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | Factory will prepare drawings showing proposed fire separating construction and door assemblies, together with certifications to protect stairs, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Protection of stairs | All exit stairways throughout all buildings inspected are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1 - All doors into stairs need to be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. Note that the final exit door from a stair to outside the building do not need to be fire rated. - All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. | F9 + 4 months | Fire rated separation of stairs will be completed, including brickwork/ fire rated door assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Obstructions along means of egress which obstruct access to the emergency exit. - Temporary obstruction (storage) e.g., trucks parked immediately outside exit discharge points from Block E, crane inside south stair of Block E, storage areas not well managed and escape routes not maintained in Block A | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 2 weeks | We have addressed highlighted issues by clearing the obstructions from the escape paths to ensure safety. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit capacity | Obstructions along means of egress which obstruct access to the emergency exit. - Permanent obstruction e.g., crane and other obstructions in Block E south stair | Remove obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit\ capacity | 1 month | We have addressed highlighted issues by clearing the obstructions from the escape paths to ensure safety. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Number of exits | Separation of exits in Block A, where two exits appear to be interconnected, and therefore not sufficiently separated from each other to count as alternative exits | Exit access shall be arranged so that the distance between exits are sufficiently remote from each other to provide alternative exit routes. | 4 months | We have provided another exit routes. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Travel distance | Travel distances exceeding limits for non-sprinklered buildings, the travel distance exceeds 60m, e.g., south side of Block A Ground Floor and Block A Level 3 | After review, we are unable to locate an alternative escape route to shorten the evacuation distance. However, this area is designated for storage, and no operational tasks are carried out by workers in this section. | 4 months | Factory will prepare drawings showing proposals for ensuring escape paths that comply with Pakistan Accord Building Standards, and submit to Accord for review prior to the rectification works. Factory will implement solution based on previously reviewed proposals |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit access | This relates to exit access where the escape route passes through higher risk intervening spaces, observed on the north side of Level 2 in Block A and from the mechanical space in Block C, where exit access is via a storage room. | Escape routes shall be arranged so that it is not necessary to pass through any hazardous areas and to avoid travel through intervening spaces on the way to the exit, as per Pakistan Accord Building Standard. | 4 months | Factory will prepare drawings showing proposed modification to ensure escape routes do not pass through high-risk areas and submit to Accord for review prior to the rectification works. Factory will implement solution based on previously reviewed proposals |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. - Exit discharge pathways are exposed to unprotected openings. Exit discharge pathways are especially susceptible to exposure because of their narrow widths. - Block E south stair exit discharges directly across from unprotected Block B boiler room | Remove exterior storage within 3.05m horizontally and vertically of unprotected openings in building facade. | 1 month | Now, We have removed exterior storage. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. - Exit discharge pathways are exposed to unprotected openings. Exit discharge pathways are especially susceptible to exposure because of their narrow widths. - Block E south stair exit discharges directly across from unprotected Block B boiler room | Protect exit route at exterior of the building from unprotected openings to allow a safe, free and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standard. | F16 + 4 months | -We will expand width of exit passage. - Block E: The passage is 12 feet wide, exit discharge so far away from steam generator |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Escape stair condition | Handrails not being provided or being defective on one or both sides of exit stairs, which can cause falls during evacuation. Handrails were not provided on both sides of exit stairs in several locations including, Block A exterior stairway, Block F exterior stairway, and Block E south stairway which is missing fall protection as well. | Provide handrails on both sides of the exit stair in accordance with Pakistan Accord Building Standard | 1 month | We have installed handrails on both sides. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit signage | It was observed that there is insufficient exit signage throughout the inspected buildings – e.g., Block B production areas, Block E south stair not marked as an exit, Block F canteen. | Remove any misleading exit signage and/or floor markings and provide exit signage so access to exits are marked by approved readily visible signs along full length of the escape route | 1 month | We have painted floor marking and also installed illuminated exit signage on Block B, Block E & C=Block F. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Exit signage | It was observed that there is insufficient exit signage throughout the inspected buildings – e.g., Block B production areas, Block E south stair not marked as an exit, Block F canteen. | Provide exit signage so access to exits are marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | F19 + 2 months | Factory will provide exit signage complying with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3 |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Means of Escape | Escape doors | Sliding exit doors observed where only swinging doors provide an acceptable level of risk. This is highly prevalent throughout the buildings inspected | Replace sliding door(s) or incorporate panels with side hung swinging door(s) which are easy openable and swing in the direction of egress travel in accordance with the requirements of the Pakistan Accord Building Standard | 3 months | We have installed side-swinging doors in almost departments. The remaining installations are scheduled to be completed by December 24. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Sprinkler system | This relates to the Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor. Buildings B and E do not have an automatic sprinkler system and require them because of their height | (1) Submit design documentation for a sprinkler system along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24 | 4 months | Factory will appoint consultant and submit design documentation for suppression system (SUPS), including sprinkler system for Building B (with top floor higher than 60 ft) and standpipe system (Buildings A1, B and E) and supporting infrastructure, to Pakistan Accord for review before purchasing any new equipment. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Sprinkler system | Buildings B and E do not have an automatic sprinkler system and require them because of their height | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F22 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Sprinkler system | Buildings B and E do not have an automatic sprinkler system and require them because of their height | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS | F23 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and proceed with installation |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Sprinkler system | Buildings B and E do not have an automatic sprinkler system and require them because of their height | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F24 + 3 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Sprinkler system | Buildings B and E do not have an automatic sprinkler system and require them because of their height | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F25 + 3 months | Factory will advise Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Sprinkler system | Buildings B and E do not have an automatic sprinkler system and require them because of their height | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F26 + 3 months = 18 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Standpipe system | This relates to the standpipe system for firefighting operations. - Building B and E require a Class I standpipe system because both buildings are more than 50 feet in height measured from level of fire department access to lowest occupiable floor. - Building A1 requires a Class I standpipe system because the building is not sprinklered, is more than 2 storeys, and has a floor area greater than 2,325 m2 | Provide listed/approved Class I standpipe and accessories as per NFPA 14 and supporting infrastructure for the SUPS system | 18 months | Factory will provide a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Suppression | Fire pumps | This relates to the fire pumps and water supply which currently support the standpipe system. - Diesel fire pump out of service, did not operate. Also not set to automatic start. | Set diesel pump controller to automatic start. Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 20. | 18 months | Existing hydrant system is now being maintained with an automatic start features. |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Suppression | Fire pumps | This relates to the fire pumps which currently support the standpipe system. - Fire pump and control equipment not listed | Provide listed/approved fire pump, driver and controller, transfer switch equipment and accessories as part of supporting infrastructure for the SUPS system | 18 months | Factory will provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system |  |  |  | Pending Verification
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Suppression | Water supply | This relates to the water supply which currently support the standpipe system. - Arrangement of water supply and fire pump means the fire pump is in negative suction. On-site fire systems water supply volume not assessed. | Review arrangement of water supply and water storage requirements to cover supply requirements as part of supporting infrastructure for the SUPS system | 18 months | Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Separation of shafts | This relates to all lift shafts in the buildings inspected, which are not protected by fire and smoke resistant construction. Options to address this issue include providing a fire-rated lift lobby around lift openings on each floor, provide opening protective assemblies for each lift opening into the stair with 2-hr fire-rated construction and 1.5-hr opening protective assemblies e.g., a fire curtain, or other solution proposed by the factory and approved by Pakistan Accord. | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements for maintaining a fire rated floor separation. | 4 months | Factory will prepare drawings showing proposed fire separating construction to shafts and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Separation of shafts | This relates to all lift shafts in the buildings inspected, which are not protected by fire and smoke resistant construction. | Provide 2-hour fire rated construction, including 90-minute fire rated doors assemblies to lift shafts according to the layout and documents reviewed by Pakistan Accord. | F32 + 4 months | Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Different occupancy types not separated by fire and smoke resisting construction, include: - Block B production areas and mechanical spaces (e.g., Level 2 chillers) -Block D storage and production areas, - Block E Level 1 storage and production area - Block F dormitories and canteen | Identify different occupancies that need to be separated from each other according to the Pakistan Accord Standard, and develop a layout plan showing how areas will be separated. Present proposal for separation to Accord for review before commencing any works | 4 months | We are consulting with an engineering firm to install fire curtains in all lifts. Once the plan is received, it will be shared with Accord. |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. | Provide fire rated separations between different occupancy types in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F34 + 4 months | Fire rated separation of occupancies will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Storage | Storage observed in production areas. Miscellaneous (in process) storage in non-storage occupancies, does not need to be fire separated from the production area where - storage areas do not exceed 10 percent of the floor area - storage areas do not exceed 2.45m (8ft) in height (non-sprinklered buildings), 2.65m (sprinklered) - storage areas do not exceed 23m² (250ft²) in one area (non-sprinklered buildings), 93 m² (sprinklered) - storage areas are separated from other storage areas by at least 3m (10ft) | Manage storage in non-storage occupancies so that it is distributed in such a way as to meet miscellaneous storage limitations therefore not needing any fire rated separation. | 4 months | Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations and how larger storage areas need to be separated, and submit to Accord for review. We have relocated excess storage from the department to the warehouse and instructed to all HODs to ensure that storage does not exceed 10%. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Storage | Storage observed in production areas. | Where storage cannot be arranged to meet the requirements given above, then provide storage areas with fire rated enclosures in accordance with Pakistan Accord Building Standards | F36 + 4 months | Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Rated Construction | Separation of high-risk areas | This relates to the need to separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Electrical room not separated by fire and smoke resisting construction – e.g., Block C | Separate electrical room by 2-hr fire rated construction. | 4 months | Factory will prepare drawings showing proposed fire separating construction to high-risk areas and submit to Accord for review prior to the rectification works. |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Rated Construction | Separation of high-risk areas | This relates to the need to separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Fire pump room not separated by fire and smoke resisting construction; it also presents a hazard to nearby exit discharge from the upstairs dormitories – Block F | Separate pump room/house by 2-hr fire rated construction or 50-ft (5.3m) separation from adjacent buildings. | F38 + 4 months | Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Fire Rated Construction | Separation of high-risk areas | This relates to the need to separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Rooms with boilers and/or steam generators not separated by fire and smoke construction – Block B | Separate room with boiler(s) and/or steam generator(s) by 2-hr fire rated construction. | 4 months | Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Fire Rated Construction | Separation of high-risk areas | This relates to the need to separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Generator room not separated by fire and smoke resisting construction – e.g., Block C | Separate generator room by 2-hr fire rated construction and remove portable generators from production and storage areas. | F40 + 4 months | Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Hazardous Materials | Chemicals storage | This relates to bulk storage of flammable and combustible liquids and/or solids in generator rooms (Block C), roof and Level 1 warehouse of Block A | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. | 4 months | We have posted Material Safety Data Sheets (MSDS) for all chemicals, including their identifications. Factory will share inventory of MSDS sheets with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F43 | Hazardous Materials | Diesel storage | This relates to bulk storage of flammable and combustible liquids and/or solids in generator rooms (Block C), roof and Level 1 warehouse of Block A | Interior diesel storage (maximum 1265 litres on ground level) is permitted if it is fire separated from other areas by 1-hr fire rated construction and stored in accordance with other requirements of NFPA 30. Diesel storage is permitted within generator rooms and fire pump rooms if adequately stored and that room is separated from adjacent occupancies. | 4 months | We have removed excess diesel from the generator area. |  |  |  | Pending Verification
3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
23-Oct-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Mount Fuji Textiles Limited, Plot # D-146, D-148 Site Area Karachi 75700
[8 empty] | Date of Initial Inspection | [12 empty] | 23-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | This relates to the Building B (Weaving & Stitching) on level(s) Ground Floor. Apparently high column stresses at Ground floor for the observed loading. Additional floor in building as compared to original design. | - Appoint a qualified and competent Structural Engineer to carry out structural assessment on columns in Building B. - Structural Engineer to review design, loads and columns stresses in columns throughout the building. Submit the assessment results and the proposed remedial works (if any) to Pakistan Accord for review. | 3 months | Factory to appoint a civil engineering firm to provide existing concrete cylinder strength reports from tests taken during construction or if those unavailable, contract an approved laboratory to determine the concrete strength by taking at least 4 No. 100 diam cores in Building B. Actual no. and diameters of reinforcement in Ground Floor columns to be assessed by Ferroscanning. Factory will submit reports on concrete strength and reinforcement to Accord for review. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | This relates to the Building B (Weaving & Stitching) on level(s) Ground Floor. Apparently high column stresses at Ground floor for the observed loading. Additional floor in building as compared to original design. | - Appoint a qualified and competent Structural Engineer to carry out structural assessment on columns in Building B. - Structural Engineer to review design, loads and columns stresses in columns throughout the building. Submit the assessment results and the proposed remedial works (if any) to Pakistan Accord for review. | 3 months | Based on the results for actual strength of concrete and Ferroscan for reinforcement of columns at Ground Floor level, factory consultant ( civil engineering firm) to review the stresses in the columns, and submit the assessment results and the proposed remedial works (if any) to Pakistan Accord for review . |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | This relates to the Building B (Weaving & Stitching) on level(s) Ground Floor. Apparently high column stresses at Ground floor for the observed loading. Additional floor in building as compared to original design. | Review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. | 6 months | Based on the assessment and proposed remedial works (if any) civil engineering firm will produce safe load plans for all floors of Building B. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | This relates to the Building B (Weaving & Stitching) on level(s) Ground Floor. Apparently high column stresses at Ground floor for the observed loading. Additional floor in building as compared to original design. | Complete the remedial works as required. | S2 + 3 months | If any remedial works are required as a result of the assessment for Building B, then the factory will implement the remedial works, according to the proposals for remediation submitted earlier to Accord . |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | This relates to the Building E (Warehouse) on level(s) L00 - Ground Floor. No safe load plans posted; storage up to 2.4m high observed in a number of locations. Column stresses appear high at Ground floor level. | - AA17 - Relocate the floor storage to ground floor temporarily until Structural Engineer completes the assessment. - Submit the assessment results and the proposed remedial works (if any) to Pakistan Accord for review. | 1 month | Factory to appoint a civil engineering firm to provide existing concrete cylinder strength reports from tests taken during construction or if those unavailable, contract an approved laboratory to determine the concrete strength by taking at least 4 No. 100 diam cores in Building E. Actual no. and diameters of reinforcement in Ground Floor columns to be assessed by Ferroscanning. Factory will submit reports on concrete strength and reinforcement to Accord for review. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Potential Overstress | Highly stressed columns | This relates to the Building E (Warehouse) on level(s) L00 - Ground Floor. No safe load plans posted; storage up to 2.4m high observed in a number of locations. Column stresses appear high at Ground floor level. | Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the identified columns and submit concrete strength data to Pakistan Accord for review. | 3 months | Based on the results for actual strength of concrete and Ferroscan for reinforcement of columns at Ground Floor level, factory consultant ( civil engineering firm) to review the stresses in the columns, and submit the assessment results and the proposed remedial works (if any) to Pakistan Accord for review . |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Potential Overstress | Highly stressed columns | This relates to the Building E (Warehouse) on level(s) L00 - Ground Floor. No safe load plans posted; storage up to 2.4m high observed in a number of locations. Column stresses appear high at Ground floor level. | Review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. | S6 +3 months | Based on the assessment and proposed remedial works (if any) civil engineering firm will produce safe load plans for all floors of Building E. Factory will redistribute loads if necessary to comply with safe load plans limits. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Potential Overstress | Highly stressed columns | This relates to the Building A (Home textiles) on level(s) L00 - Ground Floor. Potentially overstressed columns at ground floor level of buildings. | Building Engineer to review the design, loads, and column stresses of the columns highlighted in the blue area in the report. Submit the assessment results to Pakistan Accord for review and propose remedial works if required. | 3 months | Factory to appoint a civil engineering firm to provide existing concrete cylinder strength reports from tests taken during construction or if those unavailable, contract an approved laboratory to determine the concrete strength by taking at least 4 No. 100 diam cores in Building A. Actual no. and diameters of reinforcement in Ground Floor columns to be assessed by Ferroscanning. Factory will submit reports on concrete strength and reinforcement to Accord for review. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Potential Overstress | Highly stressed columns | This relates to the Building A (Home textiles) on level(s) L00 - Ground Floor. Potentially overstressed columns at ground floor level of buildings. | Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the identified columns and submit concrete strength data to Pakistan Accord for review. | 3 months | Based on the results for actual strength of concrete and Ferroscan for reinforcement of columns at Ground Floor level, factory consultant ( civil engineering firm) to review the stresses in the columns, and submit the assessment results and the proposed remedial works (if any) to Pakistan Accord for review . |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Potential Overstress | Highly stressed columns | This relates to the Building A (Home textiles) on level(s) L00 - Ground Floor. Potentially overstressed columns at ground floor level of buildings. | Complete the remedial works as required. | S8 + 3 months | Based on the assessment and proposed remedial works (if any) civil engineering firm will produce safe load plans for all floors of Building B. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Potential Overstress | Highly stressed columns | This relates to the Building A (Home textiles) on level(s) L00 - Ground Floor. Potentially overstressed columns at ground floor level of buildings. | Review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. | 6 months | If any remedial works are required as a result of the assessment for Building B, then the factory will implement the remedial works, according to the proposals for remediation submitted earlier to Accord . |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Cracking | Column | This relates to the Building F (Office & Canteen) on level(s) L01 - 1st Floor. Column cracking observed locally. | Section of plaster finish to the column to be removed. The extent and cause of cracking to be investigated by the Building Engineer. Building Engineer to assess RC column capacity, submit to Pakistan Accord for review and propose remedial works if required. | 2 months | Factory engineer will assess RC column capacity and produce report, submit to Pakistan Accord for review and propose remedial works if required |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Cracking | Column | This relates to the Building F (Office & Canteen) on level(s) L01 - 1st Floor. Column cracking observed locally. | Complete the remedial works as required. | S12 + 4 months | Factory will complete any remedial works if required, in accordance with proposal reviewed earlier by Accord. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Other Damage/Defects | Corrosion of structural steel | This relates to the Building C (Generator) on level(s) L99 - Roof. Corrosion and deformation/ twisting of structural element supporting roof in Building C. | Structural engineer to investigate corrosion and deformation in room beam/gutter. Submit the findings to Accord for review. Propose remedial works (if required) to Pakistan Accord for review, once agreed, implement the remedial measures. | 6 months | We have consulted with a civil engineering firm that will assess corrosion and deformation of roof support and submit assessment report to Accord for review |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Cracking | Beams | This relates to the Building A (Home textiles) on level(s) L03 - 3rd Floor. Cracking in the slab soffit and in some RC beams is observed at multiple locations in the building. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, in such cases, Building Engineer to investigate cause of cracking and identify appropriate remediation. Investigation shall include confirmation of reinforcement in the beams and design assessment based on the as-constructed building and loading. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | We have filled visible cracks before publishing the report. If any new cracks appear, we will investigate and take appropriate action. |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Cracking | Beams | This relates to the Building A (Home textiles) on level(s) L03 - 3rd Floor. Cracking in the slab soffit and in some RC beams is observed at multiple locations in the building. | Carry out remediation works as required. | S15 + 4 months | We have filled visible cracks before publishing the report. If any new cracks appear, we will investigate and take appropriate action. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Cracking | Slabs | This relates to the Building A (Home textiles) on level(s) L03 - 3rd Floor. Cracking in the slab soffit and in some RC beams is observed at multiple locations in the building. | Building Engineer to investigate the cause of slab cracks. Investigate if cracks are only in the render. If cracks are within RC slab, in such case, Building Engineer to propose the remedial works, and once reviewed by Accord, implement the remedial works. | 6 months | We have filled visible cracks before publishing the report. If any new cracks appear, we will investigate and take appropriate action. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Cracking | Beams | This relates to the Building F (Office & Canteen) on level(s) L00 - Ground Floor. Cracking to edge beam in Ground floor storage area. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, in such cases, Building Engineer to investigate cause of cracking and identify appropriate remediation. Investigation shall include confirmation of reinforcement in the beams and design assessment based on the as-constructed building and loading. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | We have filled visible cracks before publishing the report. If any new cracks appear, we will investigate and take appropriate action. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S19 | Cracking | Beams | This relates to the Building F (Office & Canteen) on level(s) L00 - Ground Floor. Cracking to edge beam in Ground floor storage area. | Carry out remediation works as required. | S18 + 4 months | We have filled visible cracks before publishing the report. If any new cracks appear, we will investigate and take appropriate action. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Structural Design | Non-engineered structure | This relates to the Building A (Home textiles) on multiple levels. Electrical ducts cored through the RC beams. | Building Structural Engineer to carry out detailed survey of the beams and record the locations and numbers of longitudinal and shear reinforcement which are compromised due to electrical duct coring. Building Structural Engineer to verify the design of beams due to reduced area of longitudinal or shear reinforcement at the affected locations based on the above survey. Submit proposed remedial works following the survey findings & assessment results to Pakistan Accord for review. Proposed remedial works must ensure that all exposed reinforcement is adequately covered for fire and durability. | 3 months | Factory will consult with a civil engineering firm to verify the design and capacity of the existing structure and propose strengthening works, if needed, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Structural Design | Non-engineered structure | This relates to the Building A (Home textiles) on multiple levels. Electrical ducts cored through the RC beams. | Complete the remedial works as required. | S20 + 3 months | Factory will complete remedial works if necessary, in accordance with proposal submitted earlier to Accord fpr review |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S22 | Structural Design | Drawings differ from as-built | This relates to the Building A and Building B on multiple levels. The steel structure at the roof level of Buildings A and B is not captured on the as-built drawings. Mezzanine at 4th floor of Building A and partial infill slab at 1st floor Building A are also not captured. | Appoint a qualified and competent Structural Engineer to update as-built drawings as part of assessment of columns in Building A and B. Prepare accurate as-built drawings which reflect as-constructed building. | 6 months | Factory will appoint a civil engineering firm to update as-built drawings as part of assessment of columns in Building A and B . |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S23 | Structural Design | Lack of safe load plans | This relates to all buildings on all floors. No safe load plans posted in the factory. | Building Engineer to produce loading plans for all floors within the factory giving consideration to floor capacity and column capacity. Loading to be actively managed by Factory Management. | 6 months | Factory will provide safe loading plans for all floors within the factory giving consideration to floor capacity and column capacity |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S24 | Other Damage/Defects | Spalling concrete | This relates to the Building A (Home textiles) on level(s) L03 - 3rd Floor. Damaged concrete elements are noted at some locations with exposed reinforcement. | Provide in-situ patch repair to ensure that the concrete element’s reinforcement have adequate cover for fire and durability. Propose the remedial works, and once reviewed by Accord, implement the remedial works. | 6 months | We have consulted with a civil engineering firm to assess damaged concrete and make good where necessary . |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S25 | Other Damage/Defects | Corrosion of structural steel | This relates to the Building A (Home textiles) on level(s) L04 - 4th Floor. Corrosion to the steel frame which supports the goods lift. | Suitable corrosion protection repairs to be made under direction of Building Structural Engineer. | 3 months | Factory will make suitable corrosion protection repairs |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S26 | Cracking | Non structural | This relates to the Building A (Home textiles). Long diagonal crack is observed in one of the façade wall. | Propose the remedial works, and once reviewed by Accord, implement the remedial works. | 3 months | We have filled visible cracks before publishing the report. If any new cracks appear, we will investigate and take appropriate action. |  |  |  | Pending Verification
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1