## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
04-Dec-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Al-Karam Towel Industries (Pvt.) Ltd. Unit-III at D-7, Super Highway, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 04-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | This relates to the whole facility: The Single Line Diagrams highlight a number of design issues with regards to cables being undersized compared to the circuit breakers protecting them. | Consult a qualified engineer to review and update the entire Single Line Diagrams and rectify design issues. | 6 months | We are working in accordance with the Accord International standards. Factory will complete SLD and ensure matching with electrical system and identification (cables, breakers, panel & BBT info) |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | This relates to the whole facility: As-built Layout drawings were not updated. | Consult a Qualified Engineer complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. | 8 months | Related to sub category 1, splitting would be done after correcting SLD. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Sub-station room layout drg | This relates to the whole facility: - Thermographic Inspection Report were provided but need to be updated. - Insulation Resistance Testing report was not provided. - Earth testing report was provided having results within standard limits | Thermographic, Insulation Testing & Earth Testing report shall be prepared. | 3 months | All Test Reports are available. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | Diagrams & Drawings | Electrical layout drawing | This relates to the whole facility: Maintenance record was not provided | Maintenance records shall be provided and maintained periodically. |  | Maintenance records are Available. |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the whole facility: Lightning protection system is not installed in the facility. Any document related to LPS assessment was not presented. | Risk assessment for Lightning Protection System should be carried out by qualified engineer and design system accordingly if required | 6 months | Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review. If required, Factory will install new LPS system as per design previously reviewed by Accord. Reports are available, Need to go through again. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | This relates to the whole facility: Abnormal temperature found in different Distribution Boards throughout the facility. | Figures showing max. temperature over 104 °C need immediate rectification action which could be load redistribution, connection tightening, replacement of faulty equipment etc. | 1 month | We have rectified and resolved this issue. There are no Abnormal Temperature in the whole facility now. (DONE) |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Hot Spots | This relates to the whole facility: Abnormal temperature found in different Distribution Boards throughout the facility. | Inspect the electrical equipment fed from the panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, replacing faulty components, or be moved to alternative phase to address neutral. | 1 month | We have rectified and resolved this issue. There are no Abnormal Temperature in the whole facility now. (DONE) |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | This relates to the whole facility: Abnormal temperature found in different Distribution Boards throughout the facility. | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 6 months. | E7 + 6 months | Working on this point. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Circuit breakers | This relates to the whole facility: Undersized cables were found with larger size circuit breakers which is not going to protect the cable. This was a recurring issue in most of the DBs. | Replace breaker or cables with correct cable or breaker sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 3 months | We are working in accordance with the Accord International standards. However, it will take some time to resolve this NC. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L03 - 3rd Floor: Bus comb bar of one Phase seems Loose. | Bus comb bar need to be rectified and tightened, if required. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | Main Building: Door earth found missing in some Distribution Boards. Sizing of earth cable shall follow as per Pakistan Accord standards. In weaving area, it couldn't be verified that earth connections in the DBs existed due to closed front metal sheets. | All doors in the DBs must be connected with earth system. Sizing of earth cable shall be followed as per International standards. | 1 month | We have resolved this issue. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Earthing system | Main Building: Door earth found missing in some Distribution Boards. Sizing of earth cable shall follow as per Pakistan Accord standards. In weaving area, it couldn't be verified that earth connections in the DBs existed due to closed front metal sheets. | Earthing cables should be extended from panels to equipment, using a suitable size and type of conductor, to provide a low-resistance path for fault currents to flow to the earth. This will ensure that any exposed metal parts of the electrical system are at the same potential as the earth and will not cause electric shock to anyone who touches them. | 6 months | We have resolved this issue. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L03 - 3rd Floor: Rusting Screws and burnt signs found in DB at 3rd floor. | Replace rusting screws as shown in below mentioned images. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L03 - 3rd Floor: Rusting Screws and burnt signs found in DB at 3rd floor. | Burnt signs should be addressed after finding out the root cause, appropriate remedial action is required to avoid it in future. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L03 - 3rd Floor: Rusting Screws and burnt signs found in DB at 3rd floor. | Inspect the equipment throughout the facility and perform appropriate remedial action, if required. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L03 - 3rd Floor: Broken Power Socket found on 3rd floor stitching area. | All damaged and broken receptacles shall be replaced | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Circuit breakers | Main Building on level(s) L04 - 4th Floor. - There are few locations in the facility where damaged electrical equipment (breakers) have not been replaced. - One breaker blue phase seems past burnt traces and one connector at roof DB. | Damaged equipment shall be replaced and any burnt sign should be inspected for the root cause and perform appropriate remedial action. | 3 months | We have resolved this issue and keenly observing the root cause of such problems in future. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L04 - 4th Floor: In outdoor area on the roof, MDB Roof and adjacent sub DBs are installed without any protection of external elements and there are signs of water ingress and damage within the electrical panel. | IP rated protection is required for these DBs to avoid any potential hazard in extreme external condition. | 2 months | We would create room to protect the DBs from External Conditions. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L03 - 3rd Floor: Un-tied cable glands, broken PVC shrouds, loose screws were found in DB. Roof DB Neutral link seems damaged | Cable glands shall be tightened. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L03 - 3rd Floor: Untied cable glands, broken PVC shrouds, loose screws were found in DB. Roof DB Neutral link seems damaged- | Cable shrouds shall be replaced and loose screws shall be removed. Replace neutral link if needed. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L04 - 4th Floor: Loose wiring found in conference room, mosque fans | Loose wiring shall be avoided in future works. | 3 months | We have resolved this highlighted issues at maximum, work is in progress. |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L04 - 4th Floor: Loose wiring found in conference room, mosque fans | All type of wiring should be done in appropriate cable containment arrangement. | 3 months | We have resolved this highlighted issues at maximum, work is in progress. |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Cabling & Wiring | Splicing of cables | Main Building on level(s) M01 - Mezzanine: PVC Tape Joints were found for AC having no isolating switch. | Replace the affected cables with -continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or -use joint boxes and appropriate connectors to joint cables. | 4 months | We have resolved this highlighted issue. Factory will replace pVC jointed wiring in all areas of the building |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Cabling & Wiring | Splicing of cables | Main Building on level(s) M01 - Mezzanine: PVC Tape Joints were found for AC having no isolating switch. | Install a socket outlet suitable for the equipment's electrical requirements. Enclose and protect any exposed wires using conduit, cable trunking, or other appropriate means to prevent contact and minimize the risk of electrical shock. Securely terminate and connect the equipment wires to the newly installed socket outlet. Ensure that wiring is properly insulated, color-coded, and follows standard electrical practices. | 4 months | Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review. If required, Factory will install new LPS system as per design previously reviewed by Accord. Reports are available, Need to go through a |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) M01 - Mezzanine: Lint, Dust & Dirt found in some distribution boards | All DBs must be cleaned and maintained. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) M01 - Mezzanine: Lint, Dust & Dirt found in some distribution boards | Periodic maintenance shall be done. Ensure that electrical panels are cleaned, inspected and free from Lint, dust and dirt. | 1 month | Periodic maintenance are maintaining. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) M01 - Mezzanine: Lint, Dust & Dirt found in some distribution boards | Develop a periodic maintenance record of DBs and cable trays. | 1 month | Periodic maintenance records will be produced an shared with Accord |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | DBs & Elec Protection Systems | Circuit breakers | Main Building on level(s): MCBs are being used for switching of lighting circuits. | Switching through breakers shall be avoided in future. | 3 months | As per KIK customer NCs, that, remove all switching buttons & should be install breakers therefore, factory had been changed all switching buttons replace to breakers and also all distribution boards. Factory to investigate where MCBs are being used for switching |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | DBs & Elec Protection Systems | Circuit breakers | Main Building on level(s): MCBs are being used for switching of lighting circuits. | Push button or any other appropriate switches can be used for switching purpose. | 3 months | Factory to install switches to avoid switching through breakers throughout Main Building |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Cables support and protection | Main Building on level(s): In different areas, subpar 2 pin power plugs , missing with earth pin, were used. power plugs (male/female) are joined together for taking supply to run equipment without any fixing arrangement. | These should be replaced by power plugs fulfilling standard requirements. Hanging joints through power plugs (M/F) without any appropriate fixing arrangement. | 1 month | Factory will replace 2 pin power plugs with standard power plugs |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) M01 - Mezzanine: In conference room, lint and dust found in floor box. | Ensure that floor boxes are cleaned, inspected, and free from dust and lint. Seal all openings in floor boxes (using plates and cable glands) to prevent the ingress of dust and dirt. | 1 month | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) M01 - Mezzanine: In conference room, lint and dust found in floor box. | Prepare a periodic maintenance schedule. | 1 month | We have prepared master plan of monthly maintenance and maintenance are being performed on monthly basis. |  |  |  | Pending Verification
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) M01 - Mezzanine: Combustible material found in LT Room. | Remove all combustible material from within and around all electrical panels in the facility and ensure that all electric circuitry is clear of combustible materials. | 3 months | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) M01 - Mezzanine: Combustible material found in LT Room. | Remove combustible material away from electrical devices | 3 months | We have resolved this highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) M01 - Mezzanine: Combustible material found in LT Room. | Conduct periodic maintenance and maintain the records. | 3 months | Records are maintaining. |  |  |  | Pending Verification
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Emergency Lighting | Provided but insufficient | Emergency lighting throughout the building: - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs (5) – lux levels are too low in general - No emergency lighting in some rooms / areas (6) – e.g., weaving, Level 2 packing, warehouse, accessory store | Submit design for an emergency lighting system that meets Accord Pakistan Building Standards for review. | 3 months | Factory will prepare an emergency lighting design and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Emergency Lighting | Provided but insufficient | Emergency lighting throughout the building: - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs (5) – lux levels are too low in general - No emergency lighting in some rooms / areas (6) – e.g., weaving, Level 2 packing, warehouse, accessory store | Provide additional emergency fixtures to supply adequate illumination along the means of egress to comply with Pakistan Accord Building Standards and NFPA 101. | E36 + 3 months | Factory will provide an emergency lighting system providing adequate illumination along the means of egress to comply with Pakistan Accord Building Standards and NFPA 101 |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Fire detection and alarm system (FADS) not being consistent with acceptable standards. Some of the related issues include: - Fire detection and alarm system is not a listed system. - Incomplete coverage of fire alarm devices in some areas, with detection devices missing from the following (non-exhaustive list of spaces) – kitchen, and workshops at mezzanine level, - dust collector room, yarn storage, some individual offices, Director offices, sizing and warping department, inspection room at Level 2. - detectors incorrectly installed on Level 4 (too far from ceiling) - Detectors not installed above suspended ceiling – e.g., above office on Level 4, main LT room - Detectors not installed top of stairs - Fire detection and alarm cabling is not listed fire rated - Sounders inaudible due to low volume or high ambient noise – e.g., low sound in warehouse on Level 1 and sounder near stair 4 not working | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E38 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E39 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E40 + 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E41 + 3 months | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | [10 empty] | E43 | Diagrams & Drawings | Single Line Diagram (SLD) | This relates to the whole facility: The Single Line Diagrams highlight a number of design issues with regards to cables being undersized compared to the circuit breakers protecting them. | Consult a qualified engineer to review and update the entire Single Line Diagrams and rectify design issues. | 6 months | We are working in accordance with the Accord International standards. Factory will complete SLD and ensure matching with electrical system and identification (cables, breakers, panel & BBT info) |  |  |  | In Progress
3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
04-Dec-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Al-Karam Towel Industries (Pvt.) Ltd. Unit-III at D-7, Super Highway, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 04-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed (non-exhaustive): - along the single means of escape from interior storage areas in warehouse Level 4 - exits doors from office, first aid, childcare rooms - ancillary offices Weaving on Ground Level - workshops on mezzanine level. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | We have removed the locking devices from doors on all egress path. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | We have taken corrective action and resolved the highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Doors on all escape routes, including those leading to outside or away from the building, must swing in the direction of travel to an emergency exit. On Level 1, there is a door along a main hallway on southeast side which serves exit access from both sides and should therefore be double swing. | Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard | 3 months | We have taken corrective action and resolved the highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Sliding exit doors observed where only swinging doors provide an acceptable level of risk at (non-exhaustive): Level 4 Warehouse, Store, Exit Stair Level 1, Sanitary Room, etc. | Replace all sliding door(s) with side hung swinging door(s) which swing in the direction of egress travel | 4 months | We have taken corrective action and resolved the highlighted issue. |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Combustible materials stored in stairway | Remove all combustible materials stored in stairways. | 1 month | As per pointed out by auditor that Our EHS team removed all combustible material from stairway area. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as needed. | 2 months | As per pointed out that removed all materials from exit & opening doors, and in this connection, prepared automatic closing mechanisms as per standard. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Lift shafts which are not protected by fire and smoke resistant construction and open into protected escape stairs, e.g., access to north-northeast stair is via unprotected cargo lift lobby and lift room is unprotected, opening directly into the stair. Note access to lift machine rooms was not possible - Penetrations into/through exit stair protective enclosure - Equipment and services (e.g., electrical equipment, ducts) not serving stair inside stair | Provide a fire rated separation between the stair and the conduit, duct, etc., or relocate services so that they no longer penetrate the exit enclosure. Close any gaps with listed products with the appropriate fire rating. Remove equipment and services not serving stairway from stairway or provide construction to separate equipment and service by construction having a fire resistance rating not less than that required for the exit enclosure. Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements for review. | 4 months | Factory will prepare drawings showing proposed fire separating construction, including all components needed to provide full fire rated separation to protect stairs (walls, doors, etc) and and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. | Provide fire-rated separation between staircase enclosure and lift in accordance with the Pakistan Accord Building Standard, implementing the previously reviewed design proposal, including: - fire doors with self-closing and self-latching devices, and push-bar panic hardware where required - if fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system. | F7 + 4 months | Fire rated separation of stairs will be completed, including brickwork/ all fire rated assemblies, according to proposal previously reviewed by Accord. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit access | Exits not being permitted to discharge through interior building areas unless the building is protected throughout by an automatic sprinkler system and several other conditions are met, in accordance with the Pakistan Accord Building Standard. This was observed from the office area on northwest side of Mezzanine Level which has exit discharge via production area below. | Provide a fire rated passage to connect exit stairway discharge to the outside, such that the exit discharge leads to a free and unobstructed way to the exterior of the building, readily visible and identifiable from the point of discharge from the exit. | 4 months | Factory will prepare drawing showing proposal for protecting access to building exit or alternative arrangement to ensure safe egress from internal stairway and submit to Accord for review prior to any rectification works. Protected access to exit will be provided, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed in: - Office area in east corner of Level 1 has exit access via lift lobby and storage warehouse - Main production area on Ground Level exit access via storage area The interior discharge is not permitted through a storage or other hazardous occupancy by the Pakistan Accord Building Standard, even if the building is protected throughout by an automatic sprinkler system. | Propose modifications to exit from office and production areas that meet all the requirements for a sprinklered building and submit to Pakistan Accord for review. | 4 months | Factory will prepare drawing showing proposal for alternative access to building exit that does not pass through a higher risk area, and submit to Accord for review prior to any rectification works. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed in: - Office area in east corner of Level 1 has exit access via lift lobby and storage warehouse - Main production area on Ground Level exit access via storage area | Arrange exit access as per reviewed proposal so that it meets all requirements for exit access as per Pakistan Accord Building Standard. | F10 + 4 months | Exit access will be provided, according to proposal previously reviewed by AccordAs per pointed out by auditor that Factory has started the work. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Escape stair condition | Headroom along means of escape being less than 2,050mm. This was observed along the exterior exit discharge pathway in Northwest of the building | Remove or relocate obstruction so 2.05m minimum height is maintained along the escape route. | 3 months | As per pointed out by auditor, that work has been done. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit capacity | Obstructions along means of egress which reduce exit capacity. Two observations were made: - Permanent obstruction reducing exit capacity - Temporary obstruction (storage) reducing exit capacity | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 1 month | As per pointed out by auditor, that work has been done. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit capacity | Obstructions along means of egress which reduce exit capacity. Two observations were made: - Permanent obstruction reducing exit capacity - Temporary obstruction (storage) reducing exit capacity | Remove permanent obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit capacity | 3 months | As per pointed out that removed all obstructions, and whereas, factory has no permanent obstructions. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Travel distance | Common path of travel exceeding the limit of 23m in the Level 2 checking area. | Propose alternative exiting arrangements to reduce the common path travel distance to be in accordance with the Pakistan Accord Building Standard and submit to Pakistan Accord for review. | 4 months | Factory will prepare drawing showing proposal for limiting common path travel distance to within limits, and submit to Accord for review prior to any rectification works. |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Travel distance | Common path of travel exceeding the limit of 23m in the Level 2 checking area. | Provide exit arrangement previously reviewed by the Accord. | F15 + 4 months | Exit arrangement will be completed, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior to public way being exposed to unprotected openings. Exit discharge pathways on the southwest and northwest sides of the building being especially susceptible to exposure because of their narrow widths. | Remove exterior storage within 3.05m horizontally and vertically of unprotected openings and in a way that does not obstruct escape paths. | 1 month | As per pointed out by auditor, that Factory has closed unprotected opening in a way of escape paths. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior to public way being exposed to unprotected openings. Exit discharge pathways on the southwest and northwest sides of the building being especially susceptible to exposure because of their narrow widths. | Propose means for providing protected routes from exits and escape stairs away from the building and submit to the Pakistan Accord for review. | 4 months | Factory will prepare drawing showing proposal for protecting external routes from building exits, to ensure safe passage away from the building,and submit to Accord for review prior to any rectification works. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior to public way being exposed to unprotected openings. Exit discharge pathways on the southwest and northwest sides of the building being especially susceptible to exposure because of their narrow widths. | Protect exit route at exterior of the building from unprotected openings to allow a safe, free and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standard. | F18 + 4 months | External routes from building exits will be protected, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Exit signage | Exit signage. It was observed that there is insufficient exit signage throughout the building. Additionally, note the offices on the Mezzanine Level have many intervening rooms without sufficient exit signage that occupants must navigate before reaching a clear exit access corridor. | Remove any misleading exit signage and/or floor markings and provide exit signage so access to exits are marked by approved readily visible signs along full length of the escape route | 2 months | As per visit & review that Factory has removed misleading exit signage & provided approved readily visible sign all areas. |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Means of Escape | Exit signage | Exit signage. It was observed that there is insufficient exit signage throughout the building. Additionally, note the offices on the Mezzanine Level have many intervening rooms without sufficient exit signage that occupants must navigate before reaching a clear exit access corridor. | Provide exit signage so access to exits are marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | Exit signage will be provided as per requirements of BCP |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Sprinkler system | Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor. The building does not have an automatic sprinkler system and requires one. | (1) Submit design documentation for a standpipe and sprinkler system along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24 | 4 months | Factory will appoint consultant and submit design documentation for suppression system (SUPS), including standpipe system and supporting infrastructure, to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F22 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS | F23 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and proceed with installation |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F24 + 3 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F25 + 3 months | Factory will advise Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F26 + 3 months = 18 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Fire pumps | Fire pumps and water supply which currently support the hydrant / standpipe system. - Electric pump controller not set to automatic start. - Jockey pump controller not set to automatic start. | Set electric and jockey pump controller to automatic start. Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 25. | 18 months | Factory will provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Suppression | Standpipe system | Standpipe system for firefighting operations. - Building does not have a Class I standpipe system but requires one because the building is more than 50 feet in height measured from level of fire department access to lowest occupiable floor. - Insufficient number of risers - Insufficient number of standpipe hose connections - Standpipe risers and class 1 connections are not provided in protected staircase enclosures | Provide a Class I standpipe system as per NFPA 14 as part of the SUPS approval process.. | 18 months | Factory will provide a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Separation of shafts | Multiple passenger and cargo lift shafts which penetrate floor that are not protected by fire and smoke resistant construction opening at various locations on all floors in the building | Submit proposal for fire protection of lift shaft openings to Pakistan Accord for review. | 4 months | Factory will prepare drawings showing proposed fire separating of passenger and cargo lifts, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Separation of shafts | Multiple passenger and cargo lift shafts which penetrate floor that are not protected by fire and smoke resistant construction opening at various locations on all floors in the building | Separate lift shaft by fire-rated construction, implementing the previously reviewed design proposal | F30 + 4 months | Fire rated separation of the lift shafts will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required, observed between Ground Level and Mezzanine Level. | Submit design documentation to the Pakistan Accord giving proposals for providing fire protection to openings between floors. | 4 months | Factory will prepare drawings showing proposed fire separating method, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required, observed between Ground Level and Mezzanine Level. | Maintain fire rated floor separation by protecting the openings with a fire rated enclosure as per proposals reviewed by Pakistan Accord. | F32 + 4 months | Fire rated separation at floor openings will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types (i.e., training room and prayer area should be separated from production areas) by fire and smoke resisting construction and opening protective assemblies. | Propose design and layout showing how different occupancies can be rearranged and/or enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | Factory will prepare drawings showing proposed fire separating construction for separation between training room and submit to Accord for review prior to the rectification works |  |  |  | Pending Verification
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types (i.e., training room and prayer area should be separated from production areas) by fire and smoke resisting construction and opening protective assemblies. | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | F35 + 4 months | Fire rated separation will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Storage | Miscellaneous (in process) storage in non-storage occupancies are acceptable where (for a sprinklered building): - in process storage areas do not exceed 3.66m (12ft) in height - in process storage areas do not exceed 93m² (1000ft²) in one area - in process storage areas are separated from other storage areas by at least 3m - combined areas of in-process storage does not exceed 10% of the floor area | Manage storage in non-storage production occupancies so that each pile is less than 3.66 m (12ft) in height and less than 93m2 (1,000 ft2) in any one area, and each pile is separated by a minimum of 3.0 m (10 ft) from other storage piles, and total area of temporary storage less than 10% floor area. (for a sprinklered building) | 1 month | As per visit & review, that factory is working, in this storage areas & will manage as required standard. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Storage | Miscellaneous (in process) storage in non-storage occupancies are acceptable where (for a sprinklered building): - in process storage areas do not exceed 3.66m (12ft) in height - in process storage areas do not exceed 93m² (1000ft²) in one area - in process storage areas are separated from other storage areas by at least 3m - combined areas of in-process storage does not exceed 10% of the floor area | Propose design and layout showing how storage can be rearranged to meet with miscellaneous storage limitations or enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | Factory will prepare drawings showing proposed fire separating construction for storage areas where in-process storage limitations cannot be met, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Rated Construction | Storage | Miscellaneous (in process) storage in non-storage occupancies are acceptable where (for a sprinklered building): - in process storage areas do not exceed 3.66m (12ft) in height - in process storage areas do not exceed 93m² (1000ft²) in one area - in process storage areas are separated from other storage areas by at least 3m - combined areas of in-process storage does not exceed 10% of the floor area | Where storage areas can not be re-arranged to meet in-process storage limitations, separate with 2-hr fire-rated construction and 1.5-hr opening protective assemblies. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated | F37 + 4 months | Fire rated separation to large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Electrical room not separated by fire and smoke resisting construction | Separate electrical room by 2-hr fire rated construction. | 4 months | In this connection, factory have electric room separately , by fire rated construction. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Fire pump room not separated by fire and smoke resisting construction that could be negatively affected during a fire incident | Separate pump room by 2-hr fire rated construction | 4 months | In this connection factory have centralized fire pump in unit-1 , Therefore, our civil team is working in this unit. |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Hazardous Materials | Chemicals storage | Storage, handling, and use of flammable and combustible liquids and/or solids - Bulk storage of flammable and combustible liquids and/or solids. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. | 3 months | As per pointed out by auditor that Our procurement has collected MSDS sheets of all stored chemicals, according to NFPA requirements and arranged stacking limit storage quantities. |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Hazardous Materials | Gas storage | Gas cylinders inside a storage area on Level 4 warehouse: Up to two (2) gas cylinders (each 50 kg maximum) are permitted to be stored in an interior control area if the cylinders are adequately secured and the room is appropriately ventilated and protected as per NFPA 58. Ventilation must be direct to outside meaning the room needs to have at least one exterior wall, which cannot be adjacent to exterior exits or exterior exit discharge pathways. Protection refers to 2-hr fire rated separation of the room with cylinders and assuring the cylinders and their storage room is not within 3.05 meters of an escape route or exit. | Provide area for safe storage of gas cylinders complying with requirements of NFPA 58. | 3 months | As per requirements that factory provided safe storage area. |  |  |  | Pending Verification
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
04-Dec-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Al-Karam Towel Industries (Pvt.) Ltd. Unit-III at D-7, Super Highway, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 04-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment using observed loading on the structure, some internal columns at the Ground Floor level appear to be overstressed for the applied load. | Building Structural Engineer to review design, loads and columns stresses in the shaded area as identified in the report. Building Engineer to verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the identified columns. Submit data for concrete strength to Pakistan Acord for review | 6 months | Factory will commission an approved laboratory to determine actual strength of concrete either by 100mm diameter cores, or by providing existing cylinder strength data taken from the construction period. Submit results to Accord for review. Once the strength of concrete has been established, then factory Structural Engineer to review design, loads and columns stresses in areas identified in report, and submit assessment to Accord for review |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment using observed loading on the structure, some internal columns at the Ground Floor level appear to be overstressed for the applied load. | Review safety factor in columns with actual concrete strength and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. | 6 months | Using actual strength of concrete derived from core tests or construction period data, factory Structural Engineer to update safe load plans and submit to Accord |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Column | Cracks were observed on a 1100mm wide RC column at ground floor level which may be attributable to to plastering over the non-structural wall and column. This needs to be investigated on site to confirm. | Remove the plaster from the face of column where cracks are formed to investigate if the cracks are within the RC column or between the interface of non-structural walls and column. If cracking is found to penetrate the RC column, then the extent and cause of cracking to be investigated by the Building Structural Engineer. Assess RC column capacity and propose strengthening details if required, and submit findings to Pakistan Accord for review. | 3 months | As per Instructions of structural engineer that our civil team removed plaster from the face of column and investigated and assessed this column. Factory will share assessment report with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Column | Cracks were observed on a 1100mm wide RC column at ground floor level which may be attributable to to plastering over the non-structural wall and column. However, due to potential hazards associated with column cracking, this needs to be investigated on site to confirm. | Implement column remediations if required in accordance with proposed details reviewed by Pakistan Accord. | S3+3 months | In this connection, Our civil team remediated as per instructions of structure consultant. Factory will share assessment report with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Cracking | Beams | Consistent and repeated beam cracking was observed on RC beams at some locations of Mezzanine, 2nd and 3rd Floor levels. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams Building Engineer to investigate the cause of cracking and identify appropriate remediation. Submit the design assessment to the Pakistan Accord for review. | 3 months | Our civil engineer removed plaster from the beams at the highlighted locations of cracks and investigate we found that cracks do not penetrate the RC beams. properly plastered the highlighted area. Factory will share assessment report with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Cracking | Beams | Consistent and repeated beam cracking was observed on RC beams at some locations of Mezzanine, 2nd and 3rd Floor levels. | Carry out remediation works if required. | S5+3 months | Our civil engineer removed plaster from the beams at the highlighted locations of cracks and investigate we found that cracks do not penetrate the RC beams. properly plastered the highlighted area. Factory will share assessment report with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Loading | Uncontrolled loading | Locations observed where loading appeared to be uncontrolled and in excess of typical design load capacity for industrial buildings. No safe load plans were found anywhere in factory. | - Building Structural Engineer to review actual design load capacity and produce safe loading plans for all floors within the factory giving consideration to floor capacity and column capacity. - Load plans to be displayed in factory and loading to be actively managed by Factory Management. | 6 months | Based on updated safe load plans developed after determining the actual strength of concrete, load management capacity plans will be developed and shared with Accord. Load management plans will be displayed on every floor. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural Design | Drawings differ from as-built | Discrepancies were observed between the structural drawings and as-built structure on site. | Building Structural Engineer to survey the building, collect information and produce accurate and complete as-built structural documentation. | 6 months | As per pointed out by auditor, that As-built Structure is available on site. Therefore, we are required more technical advices in this observation. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Other Damage/Defects | Moisture ingress | Water ingress and leakage is causing corrosion to slab reinforcement, spalling & cracking to the bottom surface, resulting in ongoing damage to the RC slabs. This will cause long-term deterioration of the structure unless preventative measures are taken. | Building Engineer to inspect the areas which is experiencing water leakage. Submit a proposal for any remedial works required to the Pakistan Accord for review to prevent further damage. Complete the repair works. | 6 months | As per our engineer, that factory is working on this issues and assessing the highlighted areas of water leakages and ingress. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5
3 | 8 |  | 120 | 421 | 6 | 5
3 | 8 |  | 121 | 421 | 6 | 5
3 | 8 |  | 122 | 421 | 6 | 5
3 | 8 |  | 123 | 421 | 6 | 5
3 | 8 |  | 124 | 421 | 6 | 5
3 | 8 |  | 125 | 421 | 6 | 5
3 | 8 |  | 126 | 421 | 6 | 5
3 | 8 |  | 127 | 421 | 6 | 5
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1