## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
26-Oct-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Kings Apparel, Plot no, 22, Mehran Town Sector 16 Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 26-Oct-2023, 27-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that many electrical panels displayed abnormally high temperatures in multiple locations, meaning it is highly likely a panel could cause fire ignition. These high temperatures or hot spots were identified as a pervasive and systemic issue. Separately, due to the general poor condition of the electrical panels, it was decided that the internal arc flash covers would not be removed for the safety of the Kings Apparel electrician. Therefore, with these covers in place the visual and thermographic survey of the panels were limited | Hire a qualified and experienced electrical engineer to carry out a full thermographic inspection of the entire factory including all buildings and covered areas. The electrical engineer should decide on a safe, short term, course of action to for each hot spot, which is likely to include switching off circuits immediately. | 6 months | We have hired an Electrical Engineer and have begun addressing the issues as per the provided list. We inspected all areas and departments, identified and rectified all faults. We have also checked and balanced the load, and the temperature is now within the normal range. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that many electrical panels displayed abnormally high temperatures in multiple locations, meaning it is highly likely a panel could cause fire ignition. These high temperatures or hot spots were identified as a pervasive and systemic issue. | The electrical engineer should then investigate each instance of high temperature readings to identify the cause of the abnormal temperatures (e.g., cable termination, cable size) and recommend an appropriate solution. | 1 month | We have reviewed the points highlighted by the Accord team, traced the root cause, we will rectify the temperature issue one by one and update accordingly |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Hot Spots | Improper cable joints (cable connectors) are being used and these have been seen to have abnormally high temperatures. | Hire a qualified and experienced electrical engineer to carry out a full thermographic inspection of the entire factory including all buildings and covered areas. The electrical engineer should decide on a safe, short term, course of action to for each hot spot, which is likely to include switching off circuits immediately. | 1 months | We have addressed the point highlighted by the Accord team by tracing the root cause and rectifying the issue. We replaced a connector with a ferrule and properly secured its joint. The temperature of our panel is now normal.we also see all our firm and rectify issue one by one and update accordingly |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Hot Spots | Improper cable joints (cable connectors) are being used and these have been seen to have abnormally high temperatures. | The electrical engineer should then investigate each instance of high temperature readings to identify the cause of the abnormal temperatures (e.g., cable termination, cable size) and recommend an appropriate solution. | E3 + 1 month | We have addressed the point highlighted by the Accord team by tracing the root cause and rectifying the issue. We replaced a connector with a ferrule and properly secured its joint. The temperature of our panel is now normal.we also see all our firm and rectify issue one by one and update accordingly |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | Abnormal Temperatures noted on socket connections to portable equipment. | Hire a qualified and experienced electrical engineer to carry out a full thermographic inspection of the entire factory including all buildings and covered areas. The electrical engineer should decide on a safe, short term, course of action to for each hot spot, which is likely to include switching off circuits immediately. | 1 month | We have addressed the point highlighted by the Accord team by tracing the root cause and rectifying the issue. We reduced the load on the socket, and the temperature is now normal.further we also check our complete facility and rectify issues one by one and update accordingly |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Abnormal Temperatures noted on socket connections to portable equipment. | The electrical engineer should then investigate each instance of high temperature readings to identify the cause of the abnormal temperatures (e.g., cable termination, cable size) and recommend an appropriate solution. | E5 + 1 month | We have reviewed the point highlighted by the Accord team, traced the root cause, and resolved the issue by reducing the load on the socket. The temperature is now normal. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | Earthing cables are not extended from panels to sockets and equipment | Hire a qualified and experienced electrical engineer to carry a full design of an earthing system for the entire building. | 3 months | We have hired a qualified and experienced electrical engineer and started working on the earthing system. We will submit design of an earthing system for the entire building to Accord for review. |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | The as built schematics do not show the details of the earthing system. | Provide as built schematics to Pakistan Accord for review, showing the details of the earthing system, such as the type, size, and location of the earth electrode, the size and type of the earth continuity conductor, the earthing lead, and the earthing connections. | 6 months | We are currently working on the plant's earthing system. We have completed the Single Line Diagrams (SLD) for the main substation and genset room further we move on department and we also required 6 to 7 earth pit and show the vendor wait for quotation after that we move on to new point and connect all our facility soon. Factory will provide as built schematics to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Earthing system | The as built schematics do not show the details of the earthing system. | Install a new earthing systems across the facility in compliance with Pakistan Accord Building Standard and reviewed documentation. | 4 months | Factory will provide a new or upgraded earthing system according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical cupboards are being used to store combustible materials. Combustible material found within multiple electrical panels. | Remove all combustible material from within and around all electrical panels in the facility. Ensure that all electric circuitry is clear of combustible materials. | 2 months | We have removed all combustible materials from the panels highlighted by the Accord team and addressed the issue. All panels are now free of combustible materials. |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical cupboards are being used to store combustible materials. Combustible material found within multiple electrical panels. | Create a cleaning schedule for electrical rooms and electrical equipment. Clean all electrical rooms, removing any materials not required by or associated with the electrical systems. | 3 months | We have established a cleaning schedule for all MCC rooms and the substation room in the plant, and we monitor this schedule on a daily basis. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | Electrical cupboards are being used to store combustible materials. Combustible material found within multiple electrical panels. | Conduct periodic maintenance and maintain the records. | 3 months | We check all electrical cupboards on a daily basis and verify that no combustible materials are present. We will conduct the periodic maintenance and maintain the records for review. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Loop Connection | There is cross-circuiting (Looping, Bunching at Molded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in several locations in the facility. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels. For any future work avoid looping and bunch of cable at MCCB/MCB or bus bar terminal, use individual circuit and overcurrent device for every incoming and outgoing circuit at the distribution boards. | 3 months | We have addressed the point highlighted by the Accord team, traced the root cause, and found that several breakers were faulty and not functioning, which caused the multi-loop issue on the panel. We have prepared a PR for the necessary materials, department by department. Once we receive the materials, we will address and rectify the issue one by one.and update accordingly |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | The electrical panel located beside the standby generator is not in a suitable condition to be used, there are several connections taken from the same breaker, cables are improperly jointed and there are signs that the panel has dealt with several electrical faults in the past. | Replace the damaged breaker with a new one that meets the required specifications and is in good working condition. Conduct a thorough inspection of the affected circuit to ensure no other components or wiring were damaged by the fault. | 3 months | We have reviewed the point highlighted by the Accord team and contacted the vendor for a quotation for the panel. This matter is currently under discussion with senior management. We will address and rectify the issue as soon as possible. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | Evidence of vermin remains with electrical panels is present. In all cases the vermin appear to have been electrocuted and the remains of the animal have not been removed, nor have efforts been made to prevent the ingress of vermin in the electrical equipment. | Shut down the equipment and remove the remains of the vermin. | 2 months | We have addressed the point highlighted by the Accord team by removing all vermin materials from the panel and rectifying the issue. Additionally, we inspect the panel daily as part of our ongoing observation. |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | Evidence of vermin remains with electrical panels is present. | Ensure covers and cable seals provided within panel to help to prevent vermin from entering the panel. | 2 months | We have covered all openings in the panel and are monitoring it daily. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Adequate accessibility | There are instances where sockets are improperly connected to the electrical systems. | Replace connections / cables with a manufactured product in compliance with a recognised product standard. | 2 months | We have addressed all the points highlighted by the Accord team and resolved the issues. Additionally, we have organized all sockets properly and verified the load distribution. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Circuit breakers | There are several locations throughout the facility where damaged electrical equipment (breakers) has not been replaced. | Equipment should be isolated from the electrical distribution system (turned off). If the equipment is required to operate it should be replaced before doing so. | 1 month | We have checked the point highlighted by accord team so we trace a root cause and found that there are a lot of breakers are faulty so we make PR of that material department wise whenever we received a material we will rectify this issue one by one. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Cabling & Wiring | Colour coding | It was noted in several locations throughout that facility that the incorrect cables colours are being used. In a lot of these cases green and yellow cables (reserved for the earthing system) is being used as a live conductor. | If there is a mix of old and new wiring colours, the cables should be clearly marked with the relevant colour codes to prevent incorrect application of the phase and neutral. | 3 months | We have checked the point highlighted by accord team so we trace a root cause and found that incorrect colour are used so we make PR of that material department wise whenever we received a material we will rectify this issue one by one. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Cabling & Wiring | Colour coding | It was noted in several locations throughout that facility that the incorrect cables colours are being used. In a lot of these cases green and yellow cables (reserved for the earthing system) is being used as a live conductor. | Green / Yellow Cables (earth cables) should not be used as a live conductor. Replace these cables with the cable of the correct colour. | E19 + 1 month | We have checked the point highlighted by accord team so we trace a root cause and found that incorrect colour are used so we make PR of that material department wise whenever we received a material we will rectify this issue one by one and update accordingly |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method (tape). | No more flexible cables be cut and taped in the facility. Replace the affected cables with - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. | 4 months | We have checked the point highlighted by accord team and we replaced all cables with standard cables and proper dressed its joint now all cables are properly dressed. |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Lint & dust inside panel board | In the majority of the electrical rooms, it was noted that the rooms cleanliness was not being maintained. | Initiate a regular maintenance and cleaning schedule for all electrical room. Ensure that electrical rooms are cleaned, inspected, and free from lint, dust and dirt. | 1 month | We make a schedule for cleaning of all mcc room and substation room of plant and monitor it on daily basis |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Cabling & Wiring | Cables support and protection | It was noted in several location where electrical cables were not installed correctly and not provided adequate protection from physical damage. | Provide protection to prevent cables being walked on that could cause damage to the cables. | 2 months | We have discussed this case with the vendor, take a quotation, and consulted with senior management. We will resolve this issue as soon as possible. |  |  |  | Pending Verification
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Cabling & Wiring | Cables support and protection | It was noted in several location where electrical cables were not installed correctly and not provided adequate protection from physical damage. | Re-terminate all cabling in and out of the panel. Secure all cable to a method of cable containment (for example cable conduit). | E23 + 1 month | We have reviewed the points highlighted by the Accord team and have addressed each issue one by one. Now we take a quotation from vendor and discuss with senior management we resolve this issue asap and update accordingly |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Circuit breakers | Breakers are designed to be used inside electrical panels with physical protection to the exposed live connections. In several instances throughout the facility breakers are being used as switches to equipment. | The devices are to be changed for a suitable switching device i.e., fused switched isolator. | 3 months | We have addressed all the points highlighted by the Accord team and resolved the issues. Now all breakers are at proper cover and insulated from other supply |  |  |  | Pending Verification
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | DBs & Elec Protection Systems | Panel/cabling/busbar | At the external rear gate on level(s) L00 - Ground Level the electrical panel is not externally rated and is showing signs of water ingress and rusting. | Replace the panel with a panel designed to be located outside, water ingress protection or provided with physical barriers to prevent water reaching the existing panel. | 4 months | We have discussed this case with the vendor, obtained a quotation, and consulted with senior management. We will resolve this issue as soon as possible. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Cabling & Wiring | Cables support and protection | Building 6 – Back buildings on level(s) L00 - Ground Level, Driver office - electrical equipment installed without protective covers or separation. | Replace the panel with a properly designed and constructed panel with covers and access. | 2 months | We have resolved the issue, and all equipment is now covered with protective sheets. |  |  |  | Pending Verification
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Cabling & Wiring | Cables support and protection | Main LT room on level(s) L02 - Second Floor. Exposed live connections on the generator batteries | Cover electrical connections using suitable insulating material. | 2 months | We have resolved the issue, and all equipment is now covered with protective sheets. |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | DBs & Elec Protection Systems | Panel/cabling/busbar | There are several instances throughout the facility where electrical safety devices where not correctly installed and fixed within panels. | Install equipment correctly in existing electrical panels. | 2 months | We have reviewed all the points highlighted by the Accord team and have resolved the issue. All equipment is now in its prescribed location. |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Diagrams & Drawings | Electrical layout drawing | An electrical load balance document was not available during the inspection. | Create an Electrical Load Balance Document: Engage a certified electrical engineer to conduct a thorough assessment of the electrical loads in the factory. This should include all equipment, machinery, lighting, and any other systems that use electricity. | 6 months | We are currently working on the electrical load balancing document. We have completed the single-line diagram (SLD) for the genset and substation room. Next, we will proceed to each department and create the SLDs one by one. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Diagrams & Drawings | Electrical layout drawing | An electrical load balance document was not available during the inspection. | Keep the electrical load balance document updated and readily available for future inspections. This will ensure that the document can be easily accessed and reviewed during inspections. | E30 + 2 months | We are currently working on the electrical load balancing document. We have completed the single-line diagram (SLD) for the genset and substation room. Next, we will proceed to each department and create the SLDs one by one. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Diagrams & Drawings | Electrical layout drawing | The Utility Building on level(s) L00 (Ground Floor): The facility does not have updated ‘As built Electrical Layout Drawings’ (Showing outlets for light, fan, appliances, motors, etc.). | Provide updated Electrical layout drawing that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. | 6 months | We are working on the electrical load balancing document. We have completed the single-line diagram (SLD) for the genset and substation room. Now, we are moving on to each department to create the SLDs one by one. |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Emergency Lighting | Provided but non-functional | This relates to emergency lighting throughout all buildings. - Building 5 – no emergency lights in some rooms / areas, e.g., Building 5 stairway - All buildings - emergency lighting provided but did not function in test; emergency lighting does not operate unless the main breaker for the area is tripped; insufficient/no battery backup; several lights did not function at all or only functioned for a very short time during the test; adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs; no emergency lighting in some rooms / areas | Provide emergency lighting system that automatically turns on within 1s of the failure of the normal lighting supply and is capable of continuous operation for a minimum duration of 1 h and 30 minutes, as per NFPA 101. | 6 months | We are actively addressing this issue in collaboration with our HSE team. We are verifying all emergency lighting equipment within our facility, checking their operation, working conditions, and overall health, one by one. We are continuously working on this and will provide regular updates to the Accord team. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Emergency Lighting | Provided but non-functional | This relates to emergency lighting throughout all buildings. | Provide additional emergency fixtures to supply adequate illumination along the means of egress. | 6 months | We will provide additional emergency fixtures to supply adequate illumination along with means of egress. |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. It is not a listed system and does not provide alarm and notification features consistent with acceptable standards. A non-exhaustive list of related issues observed include: - Buildings 1,2, 3, 4, 5 and Ancillary buildings – no or insufficient automatic fire and/or smoke detectors . - Security / engineering block had low fire alarm audibility - All buildings - centralized fire alarm system provided to cover all buildings which was not listed, not compliant with NFPA 72; audible signals for fire alarm notification are not distinctive from audible signals used for other purposes | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | We will submit the design documentation for upgrading the current system or installing a new replacement system to Pakistan Accord for review before purchasing any new equipment. The design documentation will include detailed drawings, technical data sheets, and product certifications for all listed equipment, demonstrating full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72. This will ensure that all proposed changes meet the necessary standards before implementation |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E35 + 1 months | We will submit documentation to Pakistan Accord confirming that a Letter of Credit (L/C) has been opened for the import of any components required for the Fire Alarm and Detection System (FADS) design submitted earlier. This will ensure that the necessary components are secured and will facilitate the timely implementation of the FADS upgrade or replacement. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E36 + 4 months | We will submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. This will ensure that all necessary materials are in place and ready for the effective implementation of the Fire Alarm and Detection System (FADS). |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E38 + 5 months | We will submit the "as built" documentation of the system to Pakistan Accord for their review. |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E38 + 3 month | The factory will notify Pakistan Accord upon the completion of the Fire Alarm and Detection System (FADS) installation, indicating that it is ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the design documentation previously reviewed. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E39 + 3 months | We will provide full testing and commissioning (T&C) certification from the Fire Alarm and Detection System (FADS) installer. We will also arrange for the system installer, factory technical personnel, and Pakistan Accord technical team to be present for a final T&C demonstration verification on site. Upon successful completion of this T&C verification inspection, the remediation of the FADS system will be considered complete. |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
26-Oct-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Kings Apparel, Plot no, 22, Mehran Town Sector 16 Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 26-Oct-2023, 27-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed at the following locations (non-exhaustive): - Ancillary buildings - exit doors for Ground Level and Storage area on Level 1 of Sales Warehouse, Chemical storage adjacent to Printing Department, Maintenance Workshops - Building 1 - exits at Ground Level, bridge on Level 2 and 3 - Building 2 - Level 4 women's canteen - Building 3 - bridge on Level 2 and 3, gates in stairway, metal free zones | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 2 weeks | Lockable mechanisms on doors/gates of Ground level Sales warehouse, Chemical Storage, metal free zones will be removed. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Lockable mechanisms on doors/gates of Ground level Sales warehouse, Chemical Storage, metal free zones will be removed. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Number of exits | Single means of egress is provided, but more than one means of escape is required. This was observed in: - Ancillary buildings - Level 1 of Sales Warehouse, mezzanine of the Printing Department - Building 1 - office areas Additionally, a common path of travel exceeding 23 meters was observed from the mezzanine of the Printing Department in the Ancillary Buildings / Back Buildings, which triggers the requirement for an additional means of escape from mezzanines. | Provide alternative means of egress from the areas identified, including from the mezzanine of the Printing department, to ensure there are sufficient exits to accommodate the occupant load and travel distance requirements, in accordance with the Pakistan Accord Building Standard | 4 months | Although the mezzanine of printing department is rarely used, but a secondary exit will be provided as per the Pakistan Accord Building Standard taking care the travel distance requirement. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to all inspected buildings: - All buildings - automatic door closers are not installed/functioning in several locations, and doors normally required to be kept closed are secured in the open position by being tied open or by obstructions being wedged between the door and door frame. | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as needed. | 2 weeks | We have removed the ropes from all fire doors that keeps the door opened, and. Where needed automatic door closing mechanism will be repaired. |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to all inspected buildings: = Ancillary buildings - exterior stair from Level 1 of the Sales Warehouse exposed to window opening - Building 1 - exit stairs without fire rated construction, non-fire rated doors, exterior stair shared with bldg. 2 exposed to vents and windows - Building 2 - exit stairs without fire rated fire doors, exterior stairs shared with bldg. 3 exposed to vents and windows - Building 3 - exit stairs not adequately protected, non-fire rated doors, exterior stair shared with bldg. 4 exposed to vents and windows - Building 4 - exterior stairs shared with bldg. 3 exposed to vents and windows - Building 5 - exit stairs not adequately protected (incl. glass windows, doors), penetration into exit stair protective enclosure | Provide a fire rated separation between the stair and the conduit, duct, etc., or relocate services so that they no longer penetrate the exit enclosure. Close any gaps with listed/approved products with the appropriate fire rating. Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | We will provide a fire rated separation between stairs and the conduit, duct, etc., or relocate operations so that they no longer penetrate the enclosure. We will submit the design documentation to the Pakistan Accord showing the planned changes to meet the requirements. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. | Provide fire rated protective enclosure to the staircase in accordance with Pakistan Accord Building Standard and previously reviewed design; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F5 + 4 weeks | We will provide a fire rated separation between stairs and the conduit, duct, etc., or relocate operations so that they no longer penetrate the enclosure. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Lift shafts which open into protected escape stairs in Building 1 (south stairway), Building 3 (interior stairway), and Building 5 (interior stairway). Options to address this issue include providing a fire-rated lift lobby around lift openings on each floor, provide opening protective assemblies for each lift opening into the stair with 2-hr fire-rated construction and 1.5-hr opening protective assemblies e.g., a fire curtain, or other solution proposed by the factory and approved by Pakistan Accord. | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | We will provide a fire rated separation between stairs and lifts shafts which open into protected escape stairs in building 1 and other areas as identified in the assessment. Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Lift shafts which open into protected escape stairs in Building 1 (south stairway), Building 3 (interior stairway), and Building 5 (interior stairway). | Provide fire-rated separation between staircase enclosure and lift in accordance with the Pakistan Accord Building Standard, implementing the previously approved design proposal. | F7 + 4 months | We will provide a fire rated separation between stairs and lifts shafts which open into protected escape stairs in building 1 and other areas as identified in the assessment. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Travel distance | Travel distances exceeding limits in Building 1 - Ground Level. | Provide alternative exiting arrangements to reduce the travel distances to be in accordance with the Pakistan Accord Building Standard (if sprinklers are provided in these buildings, confirm whether distances still excessive) | 4 months | We will provide alternative existing arrangements to reduce the travel distances to be in accordance with the Pakistan Accord Building Standard. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed in Building 5 - exit access from offices and canteen through higher risk intervening spaces (production and storage areas of Building 3) | Exit access shall be arranged so that it is not necessary to pass through any hazardous areas and to avoid travel through intervening spaces as per Pakistan Accord Building Standard. | 4 months | Factory will prepare drawings showing proposal for protecting access to exit or alternative arrangement to ensure safe egress from internal stairway and submit to Accord for review prior to any rectification works. Alternative access will be completed, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit discharge | Exits discharge pathways (between building exit discharge and access to a public way) which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to all inspected buildings: - Ancillary buildings – exterior exit discharge pathway north of ancillary buildings is not protected from exterior storage areas, gas intake valve, and exterior boiler; exterior exit discharge pathway north, south, and east of ancillary buildings is exposed to unprotected openings to interior storage and workshop areas, as well as a drying area; exterior exit discharge west of ancillary buildings is exposed to exterior generator and unprotected openings to a K-electric electrical room and storage areas. | Remove exterior storage within 3.05m horizontally and vertically of unprotected openings Ensure escape routes outside the building protected by fire rated barrier or with sufficient distance from unprotected storage and other high risk areas | 4 months | We will remove exterior storage within 3.05m horizontally and vertically of unprotected openings, and ensure the routes outside the building protected with sufficient distance from unprotected storage and other high risk areas. Factory will prepare drawings showing proposal for protecting external discharge routes or alternative arrangement and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit discharge | Exits discharge pathways (between building exit discharge and access to a public way) which are not protected from adjacent hazards by fire and smoke resistant construction | Exit discharge pathways to be protected from non rated walls and unprotected openings as per the Pakistan Accord Building Standard. | F12 + 4 months | Protection to external discharge routes will be completed, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Escape doors | This relates to issues where doors along means of escape may not be easily operable, for example, in the ancillary buildings, a push bar is installed at the incorrect height in the Incoming Store & Warehouse, and the northwest door of Finished Goods Warehouse is indicated as an exit on the posted exit plans, but due to its size, it is not easily openable by all occupants | Provide push bar at appropriate height as per NFPA 101. Provide exterior fire-rated swinging-type exit door that is easily openable by all occupants in the Finished Goods Warehouse in accordance with NFPA 101. | 3 months | Push will be relocated to appropriate height in incoming store, The door of big size in finished goods warehouse is not for exit purpose, that is opened only for loading unloading of container, for exit discharge other exit is used, will update the evacuation plan. and that door will be replaced with a swinging type. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit capacity | Obstructions along means of egress which reduce exit capacity. - Ancillary buildings - temporary obstruction (storage) along means of egress in Incoming Store & Warehouse reducing exit capacity; storage along exit discharge pathways adjacent to Finished Goods Warehouse reducing exit capacity | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 2 weeks | All the obstruction have been cleared from the paths immediately and a monitoring checklist has been designed to review its effectiveness. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit capacity | Obstructions along means of egress which reduce exit capacity. - Building 3, 4, 5 - exterior stair serving these buildings has a permanent obstruction (structural beam) directly across from where it discharges at ground level as well as a temporary obstruction, reducing exit capacity | Submit evacuation calculations for Buildings 3, 4, and 5, to demonstrate the required widths for this means of escape. | 4 months | We will review the evacuation calculation and all the temporary and permanent obstruction will be removed. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit capacity | Obstructions along means of egress which reduce exit capacity. - Building 3, 4, 5 - exterior stair serving these buildings has a permanent obstruction, reducing exit capacity | As per results of evacuation calculations, remove obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit capacity in accordance with Pakistan Accord Building Standard | F15 + 1 month | We will review the evacuation calculation and all the temporary and permanent obstruction will be removed. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Escape stair condition | Handrails not being provided or being defective on one or both sides of emergency exit stairs, which can cause falls during evacuation. It was observed that - Building 5 - handrails are not provided on both sides of the stairway on all levels - Ancillary buildings - handrail along the exterior stairway serving the Sales Warehouse is damaged | Provide handrails on both sides of the exit stair in accordance with Pakistan Accord Building Standard | 1 month | We will provide handrails on both sides of exit stairs in building 5 and Handrails for sales warehouse will be repaired. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit signage | Insufficient exit signage, which was observed, for example, in the - Ancillary buildings - Printing Department and Finished Goods Warehouse. | Provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits. | 3 months | Sufficient exit signage will be provided throughout in accordance with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor. This relates to Buildings 1, 2, 3, 4, and 5. - Building 1: height needs to be confirmed, . If this building is determined to be above 50 ft, then an automatic sprinkler system will be required. - Building 2: height exceeds 50 feet, therefore an automatic sprinkler system is required throughout - Building 3: roof of not currently occupied and therefore the measurement of building height is to the top of the Level 3 slabh is less than 50 feet. - Building 4: height exceeds 50 feet - Building 5: height exceeds 50 feet | (1) Submit design documentation for a sprinkler system along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24 | 4 months | We have enquired about automatic sprinkler system from different vendors,and wait from their quotation we update when received quotation. Factory will appoint consultant and submit design documentation for suppression system (SUPS), including standpipe system and supporting infrastructure, to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlieR | F19 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS | F20 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and proceed with installation |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F21 + 3 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F22 + 3 months | Factory will advise Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 50 feet in height to highest occupiable floor | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F23 + 3 months = 18 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Standpipe system | Standpipe system for firefighting operations serving all buildings inspected. It was observed that there is an insufficient number of standpipe hose connections throughout the facility. Note the standpipe near the exterior boiler was missing a hose valve meaning a fire hose cannot be connected to the standpipe in the event of a fire emergency. | Provide hose connection for standpipe at Boiler area | 18 months | Factory will provide the design for a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14, as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Standpipe system | Standpipe system for firefighting operations serving all buildings inspected. It was observed that there is an insufficient number of standpipe hose connections throughout the facility. | Provide listed/approved Class I standpipe and accessories as per NFPA 14 as part of supporting infrastructure for the SUPS system | 18 months | Factory will provide a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Fire pumps | Fire pumps and water supply which currently support the hydrant / standpipe system across all building inspected. Key issues include diesel pump controller and jockey pump controller were not set to automatic start, and the fire pump and fire pump control equipment is not listed. Additionally, the arrangement of water supply and fire pump means the fire pump is in negative suction | Set diesel pump controller and jockey pump controller to automatic start. Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 20. | 18 months | Factory will provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20, as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Fire pumps | Fire pumps and water supply which currently support the hydrant / standpipe system across all building inspected. Key issues include diesel pump controller and jockey pump controller were not set to automatic start, and the fire pump and fire pump control equipment is not listed. Additionally, the arrangement of water supply and fire pump means the fire pump is in negative suction | Provide listed/approved fire pump, driver and controller, transfer switch equipment and accessories as part of supporting infrastructure for the SUPS system | 18 months | Factory will provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Suppression | Water supply | Fire pumps and water supply which currently support the hydrant / standpipe system across all building inspected. | Review water storage requirements to cover supply requirements as part of supporting infrastructure for the SUPS system | 18 months | Factory will ensure fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system. We have 2 tanks of 60,000 gallons each for SUPS, We will review the requirements for water storage, if necessary, will provide further tanks for fire pumps. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required. Observations relate to the following issues in Buildings 3 and 4. - Building 3 - opening connects Levels 1, 2, and 3 - Building 4 - conveyor connects Ground to Level 1; cargo lift connects all floors | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory will prepare drawings showing proposal for protecting floor openings, and submit to Accord for review prior to the rectification works We will close the openings in floors. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required. Observations relate to the following issues in Buildings 3 and 4. - Building 3 - opening connects Levels 1, 2, and 3 - Building 4 - conveyor connects Ground to Level 1; cargo lift connects all floors | Provide fire rated protective enclosure to the staircase in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F30 + 4 months | Protection of floor openings will be completed, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Separation of shafts | Openings in floors where fire rated separations are required. Observations relate to the following issues in Building 2. - cargo lift connects all floors | Prepare drawings showings proposed fire separation details of vertical shafts according to Building Code of Pakistan Table 8.6.3.1. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors enclosing the shafts - Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will prepare drawings showing proposed fire separating construction to shafts and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Separation of shafts | Openings in floors where fire rated separations are required. Observations relate to the following issues in Building 2. - cargo lift connects all floors | Provide 2-hour fire rated construction, including 90-minute fire rated doors assemblies to lift shafts according to the layout and documents reviewed by Pakistan Accord. | F32 + 4 months | Fire rated separation of shafts will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. - Ancillary buildings – different occupancies are not separated including in the Sales Warehouse building (storage, production, office, and chemical storage), Printing Department building (production not separated from exterior or interior storage, including chemical storage, and production not separated from compressor area), Leftover Fabric Store is open to maintenance workshops, the electrical room and exterior generator are not adequately separated from each other or other areas, the Printing Department and Finished Goods Warehouse are connected by a large sliding steel door, - Building 1 – different occupancies are not separated from each other including the Ground Level production area being open to the Mezzanine office and lab areas - Building 2 – different occupancies are not separated from each other including Ground Level Fabric store not being separated to production area and Level 4 mechanical space, storage, and canteen all being open to each other - Building 3 – production and storage areas are not separated from Building 3 office areas on upper levels. - Building 4 – different occupancies are not separated from each other including Level 1 storage which is open to production areas - Building 5 – offices are not separated from Building 3 production and storage areas on upper levels. - All buildings | Identify different occupancies that need to be separated from each other according to the Pakistan Accord Standard, and develop a layout plan showing how areas will be separated. Present proposal for separation to Accord for review before commencing any works | 4 months | We will identify the different occupancies to be separated according to accord pakistan standard and will develop a layout plan showing how areas will be seperated. Factory will prepare drawings showing proposed fire rated construction for separation of occupancies and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. | Provide fire rated separations between different occupancy types in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F34 + 4 months | Fire rated separation of occupancies will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Ancillary buildings - Electrical room marked as 'K-Electric Station' on plan not separated by fire and smoke resisting construction - Building 1 - Electrical rooms in Building 1 on Ground Floor and Level 1 not separated by fire and smoke resisting construction; rooms with boilers and/or steam generators not separated by fire and smoke construction on Ground Level and Level 2 terrace (room also include chillers); generator room on south end of building not separated by fire and smoke resisting construction | Provide fire rated separations between high-risk plant areas and adjacent areas in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | 4 months | We will identify the different occupancies to be separated according to accord pakistan standard and will develop a layout plan showing how areas will be seperated and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Ancillary buildings - exterior generator not separated from adjacent occupancies by fire and smoke resisting construction | Exit discharge pathway to be protected from exterior generator with a fire rated barrier. | F36 + 4 months | We will remove the standby generator from the exterior, which is only used in case of emergencies. Fire rated separation of other high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Hazardous Materials | Chemicals storage | Bulk storage of flammable and combustible liquids and/or solids stored in production and storage areas, and along exterior pathways. - Ancillary buildings - Printing Department chemical storage area; Chemicals stored in exterior pathways north and east of ancillary buildings; Sales Warehouse Building had unmarked room storing various chemicals and room was locked. - Building 1 - chemicals stored on an elevated platform in dyeing area; chemical storage on south side of Level 1; chemicals stored in exterior pathways between Buildings 1 and 2 - Building 4 - chemical storage area on Ground Floor | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. | 4 months | We have collected the MSDS sheets for all chemicals and the storage requirements for chemicals are under process, soon will provide a sufficient chemical storage area as per pakistan building code NFPA 30. Factory will share MSDS sheets with Accord |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Hazardous Materials | Chemicals storage | Bulk storage of flammable and combustible liquids and/or solids stored in production and storage areas, and along exterior pathways. | Propose remedial measures to meet these requirements and present to Accord for review | F38 + 4 Months | Factory will share proposals for separation of chemicals in accordance with the Pakistan Building Code and NFPA 30. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Hazardous Materials | Chemicals storage | Bulk storage of flammable and combustible liquids and/or solids stored in production and storage areas, and along exterior pathways. | Implement upgraded storage arrangement for chemicals once reviewed by Accord | 8 months | Separation of chemicals as per requirements of NFPA 30 will be completed, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Hazardous Materials | Gas storage | Presence of a gases inside and around the buildings inspected. - Ancillary building – gas inlet north of ancillary buildings, which is not the property of the factory but does present an explosion/blast risk. The factory’s adjacent storage may obscure observation of any loose connections, valves, or meters in the vicinity where leaks could occur. - Building 2 - LPG gas cylinders used in kitchen on Level 4 | Remove storage obscuring gas supply infrastructure. | 2 weeks | LPG gas cylinder has been removed, it was temporarily brought into factory for canteen purpose. |  |  |  | Pending Verification
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Hazardous Materials | Gas storage | Presence of a gases inside and around the buildings inspected. | Up to two (2) gas cylinders (each 50 kg maximum) are permitted to be stored in an interior control area if the cylinders are adequately secured and the room is appropriately ventilated and protected as per NFPA 58. Ventilation must be direct to outside meaning the room needs to have at least one exterior wall, which cannot be adjacent to exterior exits or exterior exit discharge pathways. Protection refers to 2-hr fire rated separation of the room with cylinders and assuring the cylinders and their storage room is not within 3.05 meters of an escape route or exit. | 1 Month | LPG gas cylinder has been removed, it was temporarily brought into factory for canteen purpose. |  |  |  | Pending Verification
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
26-Oct-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Kings Apparel, Plot no, 22, Mehran Town Sector 16 Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 26-Oct-2023, 27-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Cracking | Column | This relates to the Building 3 on level(s) L00 - Ground Floor. Column cracking in various locations in ETP area at Ground Floor. A number of columns here have previously been jacketed due to the appearance of cracking. Low concrete cover (less than 30mm to the links, including render) was observed in one column when ferro scanned during the inspection. | Structural Engineer to investigate all columns at Ground floor in Building 3 to identify the nature and extent of cracking. Carry out a detailed assessment of all columns in Building 3 and verify the capacity of the columns, taking account of the extent of cracking. - Propose the remediation works if required to Pakistan Accord for review. Consider concrete jacketing solution as per adjacent columns. - Remove/ restrict building 3 loading or occupancy as deemed necessary as an outcome of the assessment. | 3 months | A detailed assessment will be carried out to verify the capacity of the columns. Proposals for remedial works if necessary will be provided in a report and shared with Accord for review. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Cracking | Column | This relates to the Building 3 on level(s) L00 - Ground Floor. Column cracking in various locations in ETP area at Ground Floor. A number of columns here have previously been jacketed due to the appearance of cracking. Low concrete cover (less than 30mm to the links, including render) was observed in one column when ferro scanned during the inspection. | Implement remediation works as per reviewed proposal | S1 + 3 months | Factory will implement retrofitting which will be subject to assessment previously reviewed by Accord. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Loading | Uncontrolled loading | This relates to the Ancillary buildings on level(s) L01 - First Floor. No safe load plans posted. | Structural engineer to investigate and consider temporary reduction/ removal of loading. | 1 month | We will adjust the loading to suit based on the initial assessment is completed. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Loading | Uncontrolled loading | This relates to the Ancillary buildings on level(s) L01 - First Floor. No safe load plans posted. | Structural Engineer to prepare accurate as-built drawings of the structure and assess load capacity of the building. | 3 months | Safe load plans will be designed after the assessment and the same will be posted on the right location. Assessment time is 6 months for complete facility and the remediation time is 3 months for this activity. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Loading | Uncontrolled loading | This relates to the Ancillary buildings on level(s) L01 - First Floor. No safe load plans posted. | Carry out any necessary remediation works. - Structural Engineer to prepare the safe loading plans for the building, giving consideration to floor and column capacity. - Load plans to be displayed and loading actively managed by Factory Management. | S4 + 3 months | Safe load plans will be designed after the assessment and the same will be posted on the right location. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Spalling concrete | This relates to the Ancillary buildings on level(s) L00 - Ground Floor. Deterioration to the concrete elements is observed in the ancillary buildings. | Structural Engineer to advise on any immediate temporary measures from a safety perspective and propose appropriate repair solution. Submit the proposed remedial works to the Pakistan Accord for review. | 2 months | Removal of spalling area, re-plastering the area with Repair Mortar by RESSICHEM Remedial works evidences will be shared with Pakistan Accord for Review. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Other Damage/Defects | Spalling concrete | This relates to the Ancillary buildings on level(s) L00 - Ground Floor. Deterioration to the concrete elements is observed in the ancillary buildings. | Complete remediation works as required. | S6 + 4 months | Removal of spalling area, re-plastering the area with Repair Mortar by RESSICHEM Remedial works evidences will be shared with Pakistan Accord for Review. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Potential Overstress | Highly stressed columns | This relates to the Building 1 on level(s) L00 - Ground Floor. Potentially eight no. overstressed columns at ground floor level, supporting the overhead water tank plus three no. smaller perimeter columns (approximately sq.300mm) | Building Engineer to review design, loads and columns stresses in area identified in the image. Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the identified columns and submit concrete strength data to the Pakistan Accord for review. | 6 months | Factory will provide concrete cylinder strength reports from tests taken during construction or contract an approved laboratory to determine the concrete strength by taken at least 4 No. 100 diam cores, and submit reports on concrete strength to Accord for review. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Potential Overstress | Highly stressed columns | This relates to the Building 1 on level(s) L00 - Ground Floor. Potentially eight no. overstressed columns at ground floor level, supporting the overhead water tank plus three no. smaller perimeter columns (approximately sq.300mm) | Review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. | 6 months | Based on actual concrete strength and reinforcement details Factory develop safe loading plans for all floors, and submit to Accord for review. Factory will display load capacity plan on every floor and moreover each floor load plan will provide to floor manager . |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Cracking | Walls | This relates to the Building 1 on level(s) L00 - Ground Floor. Boiler room in between Building 1 and 3. Cracking may have affected stability of wall. | Structural engineer to investigate and propose remediation, including any immediate temporary works required. Submit the proposed remedial works to the Pakistan Accord for review. | 2 months | Re-plastering the area with Repair Mortar for walls by RESSICHEM. Submit the proposed remedial works to the Pakistan Accord for review. |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Cracking | Walls | This relates to the Building 1 on level(s) L00 - Ground Floor. Boiler room in between Building 1 and 3. Cracking may have affected stability of wall. | Complete remediation works. | S10 + 4 months | Remedial works will be completed in accordance with proposals previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Cracking | Beams | This relates to the Building 4 on level(s) all floors. At various locations in Building 4, beam cracking is observed. Beams are supporting long span secondary beams and in many cases, cracking may be associated with insufficient top steel in the beams. | Structural Engineer to investigate cause of cracking and identify appropriate remediation. Investigation shall include confirmation of reinforcement in the beams and design assessment based on as-constructed building and loading. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Cracking | Beams | This relates to the Building 4 on level(s) all floors. At various locations in Building 4, beam cracking is observed. Beams are supporting long span secondary beams and in many cases, cracking may be associated with insufficient top steel in the beams. | Complete remediation works as required. | S12 + 4 months | Factory will complete remediation works as required. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Cracking | Slabs | This relates to the Building 3 on level(s) L02 - Second Floor. In Building 3, cracks are observed in the third floor slab soffit. The cracks appear to be flexural cracks and related to the services penetrations. | Structural Engineer to investigate cause of cracking and identify appropriate remediation. Submit the proposed remedial works to the Pakistan Accord for review. | 2 months | 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Cracking | Slabs | This relates to the Building 3 on level(s) L02 - Second Floor. In Building 3, cracks are observed in the third floor slab soffit. The cracks appear to be flexural cracks and related to the services penetrations. | Carry out remediation works as required. | S14 + 4 months | Factory will complete remediation works as required. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Structural System | Lateral stability system | This relates to the Building 2 on level(s) L04 - Fourth Floor. Unbraced steel structure. Fans suspended from bottom chord vibrate trusses. | Structural engineer to propose appropriate stability system for steel structure. Submit the proposed remedial works to the Pakistan Accord for review. | 3 months | 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Structural System | Lateral stability system | This relates to the Building 2 on level(s) L04 - Fourth Floor. Unbraced steel structure. Fans suspended from bottom chord vibrate trusses. | Carry out remediation works. | S16 + 4 months | Factory will complete remediation works as required. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Structural Design | Non-engineered structure | This relates to the Building 4 on level(s) L04 - Fourth Floor. Steel structure at roof level does not appear to have been engineered and has no apparent stability system. | Structural engineer to check the structure and propose additional reinforcement and stability system, if required. Submit the proposed remedial works to the Pakistan Accord for review. | 3 months | 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S19 | Structural Design | Non-engineered structure | This relates to the Building 4 on level(s) L04 - Fourth Floor. Steel structure at roof level does not appear to have been engineered and has no apparent stability system. | Carry out remediation works. | S18 + 3 months | Factory will complete remediation works as required. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Structural Design | Non-engineered structure | This relates to the Ancillary buildings on level(s) L00 - Ground Floor. Unbraced steel structure at the ancillary buildings. | Structural engineer to check the structure and propose additional reinforcement and stability system, if required. Submit the proposed remedial works to the Pakistan Accord for review. | 3 months | 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Structural Design | Non-engineered structure | This relates to the Ancillary buildings on level(s) L00 - Ground Floor. Unbraced steel structure at the ancillary buildings. | Carry out remediation works. | S20 + 3 months | Factory will complete remediation works as required. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S22 | Other Damage/Defects | Spalling concrete | This relates to the Building 3 on level(s) L00 - Ground Floor. Beam spalling is observed at the ETP, Building 3. | Structural Engineer to propose appropriate repair solution to provide sufficient cover to reinforcement. Submit the proposed remedial works to the Pakistan Accord for review. Carry out remediation works. | 3 months | Structural engineer will propose repair solution to provide sufficient cover to reinforcement and 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S23 | Other Damage/Defects | Spalling concrete | This relates to the Building 3 on level(s) L00 - Ground Floor. Beam spalling is observed at the ETP, Building 3. | Structural Engineer to propose appropriate repair solution to provide sufficient cover to reinforcement, and have this implemented. Submit the proposed remedial works to the Pakistan Accord for review. Carry out the remediation works. | S22 + 3 months | Structural engineer will submit the proposed remedial works to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S24 | Other Damage/Defects | Spalling concrete | This relates to the Building 1 on level(s) L00 - Ground Floor. Concrete spalling at movement joint at Building 1. | Structural Engineer to propose appropriate repair solution to provide sufficient cover to reinforcement and have this implemented. Submit the proposed remedial works to the Pakistan Accord for review. Carry out the remediation works. | 6 months | Structural engineer will submit the proposed remedial works to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S25 | Other Damage/Defects | Spalling concrete | This relates to the Building 2 on level(s) L02 - Second Floor. At building 2, spalling of the third floor slab is observed which may impact the flexural capacity of the slab. | Structural Engineer to propose appropriate repair solution and have this implemented. Submit the proposed remedial works to the Pakistan Accord for review. Carry out the remediation works. | 3 months | Factory will carry out the remediation works. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S26 | Other Damage/Defects | Spalling concrete | This relates to the Building 2 on level(s) L02 - Second Floor. At building 2, spalling of concrete elements is observed. | Structural Engineer to propose appropriate repair solution to provide sufficient cover to reinforcement and have this implemented. Submit the proposed remedial works to the Pakistan Accord for review. Carry out the remediation works. | S25 + 3 months | 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S27 | Other Damage/Defects | Spalling concrete | This relates to the Ancillary buildings on level(s) L00 - Ground Floor. At the ancillary buildings, spalling of the roof slab is observed which may impact the flexural capacity of the slab. | Structural Engineer to propose appropriate repair solution and have this implemented. Submit the proposed remedial works to the Pakistan Accord for review. Carry out the remediation works. | 6 months | 6 month required to conclude the assessment of complete facility and 3 months required for retrofitting which will be subject to assessment. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S28 | Loading | Uncontrolled loading | This relates to all buildings. No safe load plans anywhere in factory. Uncontrolled loading in various locations. | - Structural Engineer to review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. - Load plans to be displayed in factory and loading actively managed by Factory Management. | 6 months | Based on actual concrete strength and reinforcement details Factory develop safe loading plans for all floors, and submit to Accord for review. Factory will display load capacity plan on every floor and moreover each floor load plan will provide to floor manager . |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S29 | Structural System | Connection details | This relates to the Building 1 on level(s) L03 - Third Floor. Connection of column base in unclear - no holding down bolts evident to column in red. | Structural Engineer to investigate and provide fixing to column base if necessary. | 6 months | Factory will investigate holding down bolt requirements and provide additional fixings as necessary |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1