## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
20-Mar-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Klash Private Ltd. (Unit 2) Plot # 28 117 JB Near Paharange Drainage Millat Road Dhanola Faisalabad, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 20-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | Substation room drawings do not include the electrical switchgear. The provided drawings only depicts the civil architectural plans only. | Consult a qualified electrical engineer to provide detail as-built electrical drawings including the switchgear and other equipment including cable route, trenches, ladder, trays and supports. | 3 months | We will hire qualified electrical engineer for provide as built electrical drawings & will share with Accord. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | The provided drawings for single line diagram does not depict the sufficient information of the electrical system There were no single line diagrams showing how the overall system is connected. | Consult a qualified electrical engineer to update the Single Line Diagram to include information on all panels, distribution boards and on sub-distribution boards. Ensure all relevant details are accurately depicted to maintain the integrity and safety of the electrical system. | 6 months | We will hire qualified electrical engineer for update Single Line Diagram to include missing information regarding all panels & DBs in drawings & will share with Accord. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | The electrical layouts lacks sufficient information about the facility's electrical system and does not accurately represent the current on-site electrical infrastructure. | Consult a qualified electrical engineer to provide drawings for complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. Risk assessment for Lightning Protection System should be carried out by qualified engineer and design system accordingly if required. | 8 months | We will hire qualified electrical engineer for provide as built electrical drawings & will share with Accord. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | It is observed that the installed circuit breaker do not provide adequate protection for connected cables . - 250A breaker was installed for a 70 Sq.mm cable powering the office block feeder tag L9 | Evaluate the breaker rating with respect to the cable sizes. The rating of the breaker must not be more than the cable ampacity further adjustable setting of breaker (if any) must be selected to allow current within the cable ampacity after derating factor implementation. | 3 months | The rating of the breaker will be evaluated and replaced where necessary |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed abnormally high temperatures in multiple locations, among those observed were the following (non-exclusive): - Building 2A - Building 2B | Inspect the electrical panels to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 1 month | We will conduct internal inspection regarding Thermographic testing for abnormal temperature which may be cause by loose connection overloaded circuits etc. Once inspection will be done, will share record with Accord for review |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed abnormally high temperatures in multiple locations, among those observed were the following (non-exclusive): - Building 2A - Building 2B | Create a schedule to have a thermograph survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. Carry out independent thermographic survey. | E5 + 6 months | We will create schedule of thermographic survey which will be carried out by qualified person bi-annually. It will be shared with Accord as well. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | It was observed that the cables from the earth pit are directly connected to panels and machines without an earth test bar.some distribution boards observed in | Consult a qualified electrical engineer to design and evaluate the earthing system. Submit the design to Pakistan Accord for review prior to completing the installation of the earthing system The grounding system should be provided for all facility panels, distribution boards, equipment, and cable trays. Separate earth bar of appropriate size shall be installed in electrical panels and distribution. The size of the earth conductor should comply with IEC standards. Additionally, ensure that the earth pits are located appropriately for easy accessibility. | 6 months | We will consult a qualified electrical engineer to design earthing system. Once design is completed, will share with Accord for review. |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | It was observed in lift distribution board that earthing bus bar was missing earthing bus bar. The earth cables inside the non-perforated cable trays above the production line in the halls have tape joints. | Consult a qualified electrical engineer to design and evaluate the earthing system. Submit the design to Pakistan Accord for review prior to completing the installation of the earthing system The grounding system should be provided for all facility panels, distribution boards, equipment, and cable trays. Separate earth bar of appropriate size shall be installed in electrical panels and distribution. The size of the earth conductor should comply with IEC standards. Additionally, ensure that the earth pits are located appropriately for easy accessibility. | 6 months | We will consult a qualified electrical engineer to design earthing system. Once design is completed, will share with Accord for review. |  |  |  | Pending Verification
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Circuit breakers | Electrical panels and distribution boards were discovered to feature cables that are undersized compared to the circuit breaker ratings, Breakers installed were observed that did not provide adequate protection for connected cables . - 250A breaker was installed for a 70 Sq.mm cable powering the office block feeder tag L9 | Consult a certified electrical engineer provide Insulation test reports of individual main cables to the Panels and distribution boards to Pakistan Accord. Consult a certified electrical engineer to assess the cable ratings with respect to the running load and the circuit breakers and make corrections as required by means of breaker rating adjustment or cable rating correction. The IP rating of the panels/Distribution boards must be in compliance with the IEC-61439 standards. All measurements should be taken to ensure compliance to standards this may include replacing the panels/Distribution boards. Further the placement shall be such to allow for necessary clearance around for ease of maintenance. | 3 months | We will consult with qualified engineer for insulation test reports of individual main cables to the panel and distribution boards & reports will shared with Accord. |  |  |  | Pending Verification
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Loop Connection | At numerous locations there were multiple cable connections originating from a single breaker, as well as instances of cables being looped multiple times within the distribution boards. Observed in the LV panel breaker having feeder tag F1.05 | Multiple connection from single point is strongly not recommended. This connection must be removed for outgoing circuit wires and with the panels/Distribution boards. Separated breaker should be installed for each outgoing circuit. | 3 months | We will start working regarding removing of multiple connection from single point. We will sort out these type of issues till deadline & evidence will be shared with Accord. |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. Specifically inside stitching hall ( Unit ) distribution boards | The IP rating of the panels/Distribution boards. must be incompliance with the IEC-61439 standards. All measure should be taken to ensure compliance to standards this may include replacing the panels/Distribution boards. | 3 months | We will check & replace panels & DBs which are non-compliance with IEC-61439. Once all check & replaced, evidence will be shared with Accord. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Lint & dust inside panel board | Lint and dust found in most of the distribution boards and panels specifically at the lift panels | Schedule maintenance should be carried out for cleaning of panels and distribution boards. All measure should be taken to ensure the removal of dust, dirt, and any other sort of containment inside the panels. | 1 month | We will share maintenance & cleaning schedule of panels & DBs with Accord team. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning arrestor was installed however the risk assessment and the design drawing were missing for the lightning protection system. | Consult a qualified electrical engineer to provide risk assessment report for lightning protection as per the IEC 63205 Standards and submit to Pakistan Accord prior to any modification on site in this regard. Consult a qualified electrical engineer to design the lightning protection system as per the IEC 62305 standards. The design drawings shall be submitted to Pakistan Accord prior to installation on site. | 6 months | We will hire qualified electrical engineer to conduct risk assessment for lightning protection as per the IEC 63205 standards & will submit to Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. Some of the related issues include: - Incomplete coverage of fire alarm devices in some areas specifically kitchen - type of detection devices not appropriate - conventional non listed panel installed -Fire cable not listed. -Detection devices non listed - Sounders inaudible due to low volume, or without distinctive audible signals. | (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | We will consult with 3rd party and submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E14 + 1 month | If any new listed components need to be purchased we will submit documentation to the Pakistan Accord showing that an L/C has been opened for import |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Fire Alarm & Detection System (FADS) | Detectors | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation | E15 + 4 months | Once all materials have been in housed we will advise Pakistan Accord that all materials are available on-site for installation. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Fire Alarm & Detection System (FADS) | Fire Alarm Panel | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E16 + 5 months | Once installation is complete we will submit full "as-built" documentation of the system to the Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Fire Alarm & Detection System (FADS) | Manual Call Points | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E17 + 3 months | We will advise Pakistan Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Fire Alarm & Detection System (FADS) | Alarm Sounders | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E18 + 3 months | We will provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Emergency Lighting | Provided but insufficient | During the test it has been found that the few of the emergency lights in the factory area are non-functional further the number of lights was found to be insufficient to illuminate the escape routes as per the standard requirements. observed in stiching hall units | Consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements. Submit the design to Pakistan Accord prior to installation. All emergency lights must be listed and in proper working condition | 3 months | We will discuss with qualified engineer regarding design emergency lighting system as per NFPA standard. Once design will be finalized, it will be shared with Accord for further proceeding. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Emergency Lighting | Independent power source | It has been observed that the emergency lights have been energized by utilizing the nearby light and power circuits.and does not have independent circuits risking the continuous power supply reliability and hindrance in testing of each light for maintenance and record. | The circuit for emergency lighting with built-in battery must be isolated from general lighting and power. Each zone should have its own dedicated emergency lighting circuit. The lights shall be provided with switches, it must not be operated from the breaker. | 6 months | Once new emergency lights will be installed as per new design, it will be isolated from general lighting & Power. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Emergency Lighting | General Lighting | It was observed that most of the factory area lights are being switched on and off directly from the circuit breakers. Operating a circuit breaker directly from the breaker itself is unsafe and not recommended. This | Lighting should not be switched off at the breakers instead, it should be controlled via light switches for individual and group of lights. | 3 months | We will start working regarding lighting switched off at the breakers. Once it will be done, will be shared with Accord. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | It has been observed that the powerhouse specifically the generator area ,Transformer room and HT room lacks sufficient illumination,Ventilation of the transformer was provided using pedestal fan unsafely. | Lights fixtures in the LV room should be added to enhance the illumination. Consult a Qualified Engineer to install an exhaust mechanism in the LV room to improve air circulation. Also to upgrade the existing ventilation system that can provide sufficient air changes for the room. Ensure that the new system is properly sized and designed to meet the ventilation requirements of the LV room. | 3 months | We will consult with qualified engineer regarding installation of new exhaust mechanism in the LV room & will update to Accord team. |  |  |  | Pending Verification
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Generator, Transformer & Sub-Station Room | Transformer arcing horn | It is observed that the arcing horn were not provided on the transformer further the alarm/indication for Buchholz relay was missing. | The transformer should be equipped with arcing horns and Buchholz relay indication at the LV panel. | 3 months | We will install arcing horns & Buchholz relay indication at the LV panel. |  |  |  | Pending Verification
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Cabling & Wiring | Cables support and protection | It is observed from the inspection that at the numerous locations that cables are laid without appropriate support and dressing.specifically dressing of wire inside the trays at the stitching units. | All cables must be contained within cable trays and conduits, properly dressed, and organised as per the standards. All cables must be contained within suitable enclosures, properly dressed, and organised as per the BS 7671 standard. | 3 months | We will start working related cables trays and conduits dressing & organize as per standards. Once working will be done will share evidence with Accord. |  |  |  | Pending Verification
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Cabling & Wiring | Cable trench and channel cleanliness | It was observed that the cable trenches and channel were significantly contaminated with lint and dust. The significant accumulation of dust in cable trenches and channels is a cause for concern, as it can lead to various operational issues and safety hazards. -Observed in generator and LV room trench. | The cable trenches must be kept clear of debris and dirt, and any open trenches must be covered to prevent entry by rodents and other contaminants. | 2 months | We will clear all cable trenches from debris & dirt & open trenches will also be covered. Once it will be completed, will share evidence with Accord. |  |  |  | Pending Verification
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Cabling & Wiring | Splicing of cables | It has been observed on the numerous location cables are openly laid on floor, undressed and unmanaged and connected to socket without earth connection. Further the wires inside the non-perforated cable trays typically at all halls (named Units-XX, where XX denotes unit number) are laid undressed. | All the unmanaged cable shall be dressed as per the BS-7671 .Develop and enforce a facility-wide electrical safety protocol that mandates the use of power plugs for all equipment. Conduct regular safety audits and provide training sessions to staff to reinforce the importance of using proper power plugs and adherence to electrical safety standards. | 4 months | We will managed all cable which were found undressed & unmanaged during inspection. Once all cables issues are resolved, evidence will be shared with Accord. |  |  |  | Pending Verification
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Cabling & Wiring | Colour coding | It was noted that within various panels and distribution boards, the phase of the cables could not be determined based on their colour coding at multiple locations e.g lift panels and Cables at LV room panels | Each cable must be colour coded according to the respective phase colour. further colour sleeves must be applied on buss bars for phase identification. | 2 months | We are following colour coding requirement during installation of new electrical panel & DB. For existing DB will issues will be sorted out within the timeline. |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Cabling & Wiring | Fixtures | It is observed that the number of sockets in the facility were found broken specifically at the stitching halls | All power receptacles must be connected to the main earth bar with an earth cable to ensure proper grounding. Additionally, any broken receptacles must be replaced with IP-rated covers specifically for wet and outdoor areas. | 3 months | We will replace all broken & existing receptacles which are not complying with standards asap. After completion of work, evidence will be shared with Accord. |  |  |  | Pending Verification

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
20-Mar-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Klash Private Ltd. (Unit 2) Plot # 28 117 JB Near Paharange Drainage Millat Road Dhanola Faisalabad, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 20-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point -Main gate escape doors. -Most of the doors on emergency escape routes found lockable (Building 1, Building 2a and Building 2b, Building 3). | Remove all locking devices from doors on all egress routes that could prevent opening from inside | 2 weeks | We are Working on Lockable mechanisms NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 and will share solution with you |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point -Main gate escape doors. -Most of the doors on emergency escape routes found lockable (Building 1, Building 2a and Building 2b, Building 3). | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | We are Working on Lockable mechanisms NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 and will share solution with you |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | It is observed that doors on escape routes are swinging in the wrong direction (inwards). This is not always achieved, as observed (list not exhaustive): -Building 1 3rd Floor, -Building 2 2nd Floor and -Building 3 3rd Floor | Escape doors to be side hung doors that swing in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | we will open door outward direction NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 and will share solution with you |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | It is observed that doors on escape routes are swinging in the wrong direction (inwards). This is not always achieved, as observed (list not exhaustive): -Building 1 3rd Floor, -Building 2 2nd Floor and -Building 3 3rd Floor | Ensure that doors can swing in the direction of escape and are easily opening in compliance with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | we will open door outward direction NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 and will share solution with you |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Escape doors | Sliding doors at emergency exits. This is not always achieved, as observed (list not exhaustive): - Building 1, Production area. -Building 1, 1st floor praying area. -Building 1, Emergency Stair S-1. | Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | We will remove sliding doors and install Swing Door |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | List of stairs that were observed as non-compliant during the inspection (non-exhaustive): - Building 1, Emergency stair S-1, S-2 and S-3. - Building 2, Emergency stair S-4 and S-5. - Building 3, Emergency stair S-8 and S-9. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs; - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | We will discuss Experts Engineer and share the drawing |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | List of stairs that were observed as non-compliant during the inspection (non-exhaustive): - Building 1, Emergency stair S-1, S-2 and S-3. - Building 2, Emergency stair S-4 and S-5. - Building 3, Emergency stair S-8 and S-9. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: -All doors into stairs should be fire resisting doors with self-closing mechanisms. -Penetrations through doors are not permitted. -All fire doors require self-closers -Doors into stairs should be kept closed (but not locked) at all times. | F6 + 4 months | We will procure and in house all components needed to provide full fire rated separation of stairs according to the proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Per Pakistan Accord Building Standard, exit stairs should be adequately protected. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. Note that the final exit door from a stair to outside the building does not need to be fire rated. - All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. - Where stairs discharge within a building, a fire separated corridor shall be provided that leads outside building. | 8 months | We will provide fire rated separation of stairs according to the proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit capacity | Obstructions along means of egress which reduce exit capacity : Temporary obstruction (storage) reducing exit capacity (e.g. Building 3 Production floors). | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 2 weeks | Clear issue |  |  |  | Pending Verification
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit capacity | Obstructions along means of egress which reduce exit capacity : Temporary obstruction (storage) reducing exit capacity (e.g. Building 3 Production floors). | Remove obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit capacity | 4 months | Work in Progress |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit signage | All buildings (1, 2a, 2b and 3) have insufficient signage across the buildings. -Missing exit signs at stair discharge routes. -Missing exit signs in corridors and circulation areas. -Missing exit signs in production areas. -Electrically powered exit signs are not a tested and listed system. | Ensure to remove misleading direction arrows from the means of egress. | 1 month | We replace wrong direction with correct Direction see attached picture |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit signage | All buildings (1, 2a, 2b and 3) have insufficient signage across the buildings. -Missing exit signs at stair discharge routes. -Missing exit signs in corridors and circulation areas. -Missing exit signs in production areas. -Electrically powered exit signs are not a tested and listed system. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standards And BCP 10.15.1, 10.15.2 and 10.15.3 | F11+ 2 = 3 months | Work in Progress |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit signage | All buildings (1, 2a, 2b and 3) have insufficient signage across the buildings. -Missing exit signs at stair discharge routes. -Missing exit signs in corridors and circulation areas. -Missing exit signs in production areas. -Electrically powered exit signs are not a tested and listed system. | Ensure that all exit signage is checked periodically and in good working condition. | 3 months | electrical department area insurance the exit sign in good condition |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Suppression | Fire pumps | This facility has own fire pumps system which supplies Klash Unit 1 facility as well. The following deficiencies were observed on site: - All pumps and controllers are non-listed. | Submit the fire pumps, controllers and equipment’s technical details that comply with Pakistan Accord and NFPA 20 standards to Pakistan Accord for review before purchasing the equipment. Prepare documentation showing technical details of how equipment will rectified to comply with NFPA 20. Submit proposed system design and details of the equipment to Pakistan Accord for review before undertaking remedial works. | 4 months | We are working on it and will submit a design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Fire Suppression | Fire pumps | All pumps and controllers are non-listed. | Provide the required listed fire pumps, controllers and equipment that operate at positive suction as per documentation reviewed by Pakistan Accord. | 18 months | We will provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Suppression | Standpipe system | Per Pakistan Accord Building Standard a Class-I standpipe systems is required in the building. The system should be designed and installed in accordance with NFPA 14. The following deficiencies have been observed on site, including (list not exhaustive): 1. Standpipes located randomly not near exit stairs. 2. Insufficient number of risers in all buildings. 3. Insufficient number of standpipe hose connections. | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24 | 4 months | We will discuss with fire safety, electrical expert team. After their recommendation will submit design documentation for a Suppression System (SUPS), including standpipe system and supporting infrastructure, to Pakistan Accord for review before purchasing any new equipment. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F16 + 1 month | If any new listed components need to be purchased we will submit documentation to the Pakistan Accord showing that an L/C has been opened for import |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS | F17 + 4 months | Once all materials have been in housed we will advise Pakistan Accord that all materials are available on-site for installation. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F18 + 3 months | Once installation is complete we will submit full "as-built" documentation of the system to the Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F19 + 3 months | We will advise Pakistan Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F20 + 3 months = 18 months | We will provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Separation of shafts | Shafts should be enclosed in fire resisting construction to maintain compartmentation between floors. The following deficiencies has been observed Building 1: Lift Shafts at all floors are not Separated from Production / Storage Areas | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: -Locations of fire rated walls and doors enclosing vertical shafts. Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | We will prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Separation of shafts | Building 1: Lift Shafts at all floors are not Separated from Production / Storage Areas | Provide 2-hour fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord. | F22 + 4 months | We will provide 2-hour fire rated protection to lift shafts |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Separation of high-risk areas | Electrical rooms are not fire separated from Electric workshop (e.g. Ground Floor Building 2b near S-5). | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms etc.) - Locations of fire rated walls and doors to protect these rooms; - Details of proposed fire walls and fire doors (e.g. door listing, self-closers, door opening direction); | 4 months | We will prepare drawings showing the proposed fire separation details of Electrical rooms. These shall be submitted to Accord for review |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Separation of high-risk areas | Electrical rooms are not fire separated from Electric workshop (e.g. Ground Floor Building 2b near S-5). | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord | F24 + 4 months | We will provide 2-hour fire rated construction including 90-minute fire rated doors assemblies to Electrical rooms |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Rated Construction | Separation of high-risk areas | Generator room is not fire separated and should not be used for any activities such as pray etc (e.g. Ground Floor Building 2b). | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms etc.) - Locations of fire rated walls and doors to protect these rooms; - Details of proposed fire walls and fire doors (e.g. door listing, self-closers, door opening direction); | 4 months | We will prepare drawings showing the proposed fire separation details of Generator room. These shall be submitted to Accord for review |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Separation of high-risk areas | Generator room is not fire separated and should not be used for any activities such as pray etc (e.g. Ground Floor Building 2b). | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord | F26 + 4 months | We will provide 2-hour fire rated construction including 90-minute fire rated doors assemblies to Generator rooms |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Rated Construction | Floor openings | Building 1, 1st Floor praying area side exhaust fan openings from Store area. | Maintain fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | We will prepare drawings showing the proposed changes to maintain fire rated floor separation. These shall be submitted to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Floor openings | Building 1, 1st Floor praying area side exhaust fan openings from Store area. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord | F28 + 4 months | We will provide fire rated separation between floors by implementing the plan reviewed previously by Accord |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Hazardous Materials | Chemicals storage | Storage of chemicals in Building 2 at Ground floor chemical store under the stairs. | Remove chemicals from under the escape stair | 2 weeks | We Have Remove Chemicals under the Stair |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Hazardous Materials | Chemicals storage | Chemical storage areas should be fire separated from the rest of building, with adequate ventilation. The following deficiencies were observed (list not exhaustive): Storage of chemicals in Building 2 at Ground floor chemical store under the stairs. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. | 4 months | We will discuss Experts Engineer and provide drawings showing the proposed fire rated separations and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Hazardous Materials | Chemicals storage | Storage of chemicals in Building 2 at Ground floor chemical store under the stairs. | Implement the above plan on site. All chemical storage areas to be compliant with Accord Pakistan Building Standard | F31 + 4 months | After drawing review we will implement above plan |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Hazardous Materials | Gas storage | Up to two (2) gas cylinders (each 50 kg maximum) are permitted to be stored in an interior control area if the cylinders are adequately secured and the room is appropriately ventilated and protected as per NFPA 58. Ventilation must be direct to outside meaning the room needs to have at least one exterior wall, which cannot be adjacent to exterior exits or exterior exit discharge pathways. LPG cylinder in admin kitchen area no ventilation | Protect gas storage areas with 2-hr fire rated separation of the room with cylinders and assure that the cylinders and their storage room is not within 3.05 meters of an escape route or exit. | 3 months | we removed cylinder LPG from Canteen |  |  |  | Pending Verification
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Hazardous Materials | Diesel storage | Interior diesel storage (maximum 1265 litres on ground level) is permitted if it is fire separated from other areas by 1-hr fire rated construction and stored in accordance with other requirements of NFPA 30. Diesel storage is permitted within generator rooms and fire pump rooms if adequately stored and that room is separated from adjacent occupancies.. The following deficiencies have been observed related to diesel storage on site(list not exhaustive): Storage of flammable and combustible liquids in Building 2 at Ground floor, near diesel generator, and in machine maintenance room | Prepare drawings showing the proposed Diesel storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all Diesel storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms | 4 months | We will discuss Experts Engineer and provide drawings showing the proposed fire rated separations for Diesel storage areas and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Hazardous Materials | Diesel storage | Storage of flammable and combustible liquids in Building 2 at Ground floor, near diesel generator, and in machine maintenance room | Implement the above plan on site. All diesel storage areas to be compliant with Pakistan Accord Building Standard. | F34 + 4 months | After drawing approval we will implement above plant |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Safety Management | Records of systems maintenance | Fire safety systems should be adequately maintained to ensure they will operate effectively in and event of and emergency. Maintenance records for the following were not available or inadequate (list not exhaustive): - Fire Pumps - Standpipes - Emergency lighting - Fire Extinguishers - Fire Doors | Prepare maintenance schedule for all life safety systems | 3 months | Please see attached schedule |  |  |  | Pending Verification
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Safety Management | Records of systems maintenance | Maintenance records for all life safety systems were not available or inadequate | Prepare a schedule of proposed system maintenance. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | Work in Progress |  |  |  | Pending Verification
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Safety Management | Records of systems maintenance | Maintenance records for all life safety systems were not available or inadequate | Ensure all systems are being maintained as per the schedule agreed with Accord . Keep maintenance records | F37 + 3 months | Work in Progress |  |  |  | Pending Verification
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Safety Management | Records of system testing | Fire safety systems should be adequately tested to ensure they will operate effectively in and event of and emergency. Records of testing for the following were not available or inadequate (list not exhaustive): - Fire Pumps - Standpipes - Emergency lighting - Fire Extinguishers - Fire Doors | Prepare testing schedule for all life safety systems | 3 months | Work in Progress |  |  |  | Pending Verification
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Fire Safety Management | Records of system testing | Maintenance records for all life safety systems were not available or inadequate | Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | Work in Progress |  |  |  | Pending Verification
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Fire Safety Management | Records of system testing | Maintenance records for all life safety systems were not available or inadequate | Ensure all systems are being tested as per the schedule agreed with Accord . Keep test records | F40 + 3 months | Work in Progress |  |  |  | Pending Verification
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
20-Mar-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Klash Private Ltd. (Unit 2) Plot # 28 117 JB Near Paharange Drainage Millat Road Dhanola Faisalabad, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 20-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns of building 2a and building 2b as highlighted in the report, appear to be highly stressed for the applied load. Heavy floor build-up is observed over the entire floor area at all floor levels. | Factory Engineer to review design, loads and columns stresses in area identified in the report. | 3 months | Factory have appointed external structural engineer to review design/load and columns stresses. Factory is in process to carry out the core testing of columns of building 2a and building 2b. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns of building 2a and building 2b as highlighted in the report, appear to be highly stressed for the applied load. Heavy floor build-up is observed over the entire floor area at all floor levels. | Verify in-situ concrete stresses either by 100mm dia. cores or existing cylinder strength data for the identified columns. | 3 months | Factory have appointed external structural engineer to review design/load and columns stresses. Factory is in process to carry out the core testing of columns of building 2a and building 2b. Factory will take sample of core testing in highlighted columns of buildings-2a and 2b and check on number and diameter of the reinforcing bars in the column and send for testing. Factory will share test result of core testing with Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal ground floor columns of building 2a and building 2b as highlighted in the report, appear to be highly stressed for the applied load. Heavy floor build-up is observed over the entire floor area at all floor levels. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity | S1 + 3 months | Factory will produce and actively manage loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Structural Documentation | Undocumented extension | The as-built structural drawings provided do not match in some areas as observed on site and need to be updated to include the following discrepancies (non-exhaustive): - A small horizontal extension is observed in the building 2b which is not indicated on the layouts - The roof of building 2a supports a OHWT and RC canteen rooms and fiberglass lightweight shed that are not indicated on the layouts. - Roof layout of buildings 1 and 2a were not available - Building 1 roof comprises of a portion covered with Load bearing slab brick tiles supported by T-iron over Steel trusses not documented in the drawings - Internal stair core and external steel stairs are not shown on the structural drawings | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | factory is in process to get as built drawing from architect structural engineer and include all the below missing information in these drawings. - A small horizontal extension is observed in the building 2b which is not indicated on the layouts - The roof of building 2a supports a OHWT and RC canteen rooms and fiberglass lightweight shed that are not indicated on the layouts. - Roof layout of buildings 1 and 2a were not available - Building 1 roof comprises of a portion covered with Load bearing slab brick tiles supported by T-iron over Steel trusses not documented in the drawings - Internal stair core and external steel stairs are not shown on the structural drawings |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5
3 | 8 |  | 114 | 421 | 6 | 5
3 | 8 |  | 116 | 421 | 6 | 5
3 | 8 |  | 117 | 421 | 6 | 5
3 | 8 |  | 118 | 421 | 6 | 5
3 | 8 |  | 119 | 421 | 6 | 5
3 | 8 |  | 120 | 421 | 6 | 5
3 | 8 |  | 121 | 421 | 6 | 5
3 | 8 |  | 122 | 421 | 6 | 5
3 | 8 |  | 123 | 421 | 6 | 5
3 | 8 |  | 124 | 421 | 6 | 5
3 | 8 |  | 125 | 421 | 6 | 5
3 | 8 |  | 126 | 421 | 6 | 5
3 | 8 |  | 127 | 421 | 6 | 5
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1