## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
19-Mar-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Klash Pvt.Ltd Unit# 4-5 Plot No. 25 117 JB Near Paharange Drainage Millat Road Dhanola Faisalabad, Punjab
[8 empty] | Date of Initial Inspection | [12 empty] | 19-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | Single-line diagrams attached to the distribution boards did not match the current state of the circuits. | Consult a qualified engineer to design the single-line diagram as per the current installation of the distribution boards and rectify design issues. | 6 months | We are reviewing our all Distribution boards regarding the issues & after internal inspection, we will consult external 3rd party regarding preparation of Single Line Diagram. Factory will submit SLD with earthing layout matched to field, match substation up to LT panel board and identification information with SLD |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | Insufficient information is given in the electrical layout drawing. | Consult a Qualified Engineer to complete electrical layout drawings that depict the location and specifications of all electrical equipment and outlets to match the existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are visible and up to date with the current electrical installation. | 8 months | We will check our all drawings regarding insufficient information in electrical layout with the coordination of electrical consultant. We will complete electrical layout drawings that depict the location and specifications of all electrical equipment and outlets to match the existing installation |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Circuit breakers | Circuit breaker ratings were oversized compared to the cables connected. circuit breaker terminals were seen as rusted. This was observed at the MDBs and Ltroom of production buildings B2, B3, and B4. | Circuit breakers should be installed as per the current carrying capacity of the cables. Replace rusted terminals with new ones. Also, develop a periodic maintenance program to, protect your electrical network from such issues. | 3 months | We will review all circuit breaker which are oversized. Once internal inspection complete, the rating of the breaker will be evaluated and replaced where necessary will start working accordingly. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Hot Spots | Abnormal temperatures were observed on circuit breakers and various other switching devices throughout the facility. This issue was observed at the MDBs and LDBs of buildings B1, B2, B3, and B4. | If the breaker or cable temperature is significantly higher than the limits, turn off the power to the affected circuits or the entire electrical panel if necessary. Check if the circuits are overloaded by running too many appliances simultaneously or if the breaker is heating the cable. If this is the case, redistribute the load or consider installing additional circuits to handle the electrical demand. | 1 months | 1. We have checked circuit breakers that were observed abnormal temperatures during inspection. 2. Further we will check all circuits internally regarding abnormal temperature. Once inspection will complete will start maintenance accordingly. 3. Further we will share internal maintenance Plan regarding circuit inspection abnormal temperature with Accord. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Earthing system | The main termination from the earth pit was not present. The distribution of earth from the earth pit to the floor distribution was missing, and the bonding mechanism was not as per standard. Cable trays, distribution boards, inner sheets, as well as metallic gates or cages were not provided with equipotential bonding. Multi-looping was found on earth termination busbars inside distribution boards. This was observed at every building including B1, B2, B3, B4. | Consult with a qualified engineer who can assess the facility's requirements and design an earthing system that meets safety standards and regulatory requirements. Refer to BS-7671. Develop a periodic maintenance program to inspect and test the system to ensure its continued effectiveness. Over time, soil conditions and other factors can affect the performance of the earthing system, so regular maintenance is essential to keep it in good working order. | E4 + 6 months | We will share design regarding earthing with Accord for further proceeding. Once Accord will final & approve design, we will start working accordingly. Further we will share our internal maintenance schedule regarding inspection of earthing system with Accord as well. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Panel/cabling/busbar | It is noted in the distribution panels specifically the lift room of each building including, open wiring, cabling issues, abnormal temperatures, dust, cable joints, and improper installation of circuit breakers. | Ensure that lift room is free from unwanted material/scrapes. Remove anything combustible Install a proper IP-rated electrical panel for the lift room with proper termination of cables, circuit breakers, and contactors. The wiring of the panels shall be rectified in accordance to the BS-7671 wiring guide. | 6 months | We will check all electrical panels regarding removing of unwanted material /scraps or other combustible materials & will complete our working. Once corrective action completed, will share evidence with Accord till deadline. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Multiple Connections | It was noticed in the panel in the facility, there was a multi-looping of wires. This was observed at each MDB of the building including B1, B2, B3, and B4. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or new distribution boards adjacent to existing panels if there is no space for new circuits. | 3 months | We will check all electrical panels regarding multi-looping of wires & will complete our working till deadline. Once corrective action complete, will share with Accord. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Adequate accessibility | Insufficient space for the electrical panel was noted as it occurred repeatedly throughout the facility. This was observed at B1 1st floor, B4 2nd floor, and B3 1st floor. | Inspect the facility for inadequate accessibility of electrical panels and remove everything that is blocking the area around it. Develop a periodic maintenance program to ensure that each distribution panel has enough space to reach. | 1 months | We will check all electrical DP's & if some found blocked will remove blockage. Further corrective action will be shared with Accord. Further we will develop our inspection maintenance schedule & will share with Accord asap. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Lint & dust inside panel board | It was observed in the distribution panels and power boards that were full of dust, lint, and fluffs. This was observed at LDBs and LT room of the building B4, B3, and B2. | Inspect your electrical system and clean areas that are exposed to fluff and dust. Close any unwanted ingress for the prevention of lint and dust. Develop a periodic maintenance program to clean and clear all the electrical systems from fluff and dust. | 1 months | We will check all electrical panels regarding removing of unwanted material fluffs or other combustible materials & will complete our working till deadline. Once corrective action completed, will share with Accord. Further we will develop periodic maintenance schedule & will share with Accord |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was installed on the building B4 roof, but there were no separate earth pits installed for it. Furthermore, no document related to risk assessment and proposed design was present on the day of the inspection. | Consult a qualified engineer and conduct a risk assessment to evaluate the vulnerability of the facility. Seek guidance from qualified lightning protection professionals or engineers who specialize in designing and installing lightning protection systems. The lightning protection system must comply with IEC-62305 standards for design and installation. | 6 months | We will consult & hire consultant regarding conducting of risk assessment of lightning protection. Once risk assessment is done, will submit drawings with proposed design to Accord for review. Factory will procure and in- house all components needed and install the LPS system. Once installed and tested Factory will provide Accord with sas-built drawings of the LPS system. Once all materials have been in housed we will advise Pakistan Accord that all materials are available on-site for installation. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | Fire Alarm & Detection System (FADS) | Fire Alarm Panel | An addressable FADS is installed | Provide the design documents of fire alarm system and certificates of listing (FACP, MCP, detectors, sounder with flashers, fire rated cable). | Step1: 3 months Step2: 1 months Step 3: 4 months Step 4: 5 months Step5: 3 months Step 6: 3 months | (1) We will consult with 3rd party and submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. (2) If any new listed components need to be purchased we will submit documentation to the Pakistan Accord showing that an L/C has been opened for import (3) Once all materials have been in housed we will advise Pakistan Accord that all materials are available on-site for installation. (4) Once installation is complete we will submit full "as-built" documentation of the system to the Pakistan Accord for review. (5) We will advise Pakistan Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. (6) We will provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | Fire Alarm & Detection System (FADS) | Alarm Sounders | Several locations were lacking in audibility, and some didn't have a sounder. This was observed at every building including B1, B2, B3, B4. | Consult a qualified engineer and assess the current state of the fire alarm system. Identify areas where the audibility is low and the potential causes of the issue. Consult with fire safety experts or professional fire alarm system installers to assess the situation and determine the most appropriate solutions for improving audibility that comply with NFPA-72. | E11 + 1 months | Low audibility will be addressed as part of the FADS system upgrading |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Fire Alarm & Detection System (FADS) | Detectors | It was observed that smoke detectors were not installed in some areas. This includes building B1 basement corridor, office areas for both buildings B1 and B2, 3rd floor of building B1 stitching station. | Inspect the facility where smoke detectors are needed. Install smoke detectors where needed according to the requirements that comply with NFPA-72. Do keep in mind that the equipment you are installing should be listed. | E12 + 1 months | Full coverage of smoke detectors following NFPA-72 standards will be addressed as part of the FADS system upgrading |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Emergency Lighting | No emergency lighting | It was observed that several locations were missing emergency lights. This includes building B2 (3rd floor), and fabric store building B1. | Inspect the facility in terms of blind spots where emergency lights are needed. Install emergency lights where needed according to the requirements that comply with NFPA-101 standards. | 3 months | We will do inspection regarding installation of new emergency lights, once inspection is complete, will share design with Accord before installation of new emergency lights. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Emergency Lighting | Provided but non-functional | Emergency lights were not working on buildings B1 1st floor and B2 1st floor. It was observed that the backup power supply of emergency lights was not sufficient. Emergency lights were either too dim or not working. The battery backup was too low. | Inspect the facility and replace batteries and/or lights that are not working sufficiently. Inspect the facility where emergency lights are needed. Install emergency lights where needed according to the requirements that comply with standards. Do keep in mind that the equipment you are installing should be listed. Develop a periodic maintenance program to check and inspect your emergency light backup power to avoid any issues related to the backup supply. | 2 months | We will rectify all non-functional emergency lights which were highlighted during inspection & will share evidence with Accord. Further we will do inspection regarding installation of new emergency lights, once inspection is complete, will share design with Accord before installation of new emergency lights. Further we have attached product listed certificate regarding emergency lights for Accord review. Kindly check & advise if ok |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Emergency Lighting | Independent power source | It was observed that every building in your facility is equipped with an emergency lighting system, but the circuit dedicated to it is not independent instead it was wired by the common supply of floors. | Install a separate independent circuit for an emergency lighting system that complies with the required standards. | 6 months | We have attached design regarding installation of new emergency light for Accord review, once it will be approved & go ahead from Accord, will install the IPS. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Cabling & Wiring | Splicing of cables | It was observed that the HT-cable installation was not appropriate from the incoming side of the VCB. The termination of HT on the transformer side was also not covered with terminal caps. LV side of the transformer was attached to the BTD section which was also not covered. This was observed at every building including B1, B2, B3, B4. | Install HT cable in such a manner that the excessive amount of cable should be laid in the trench rather than laid openly beside the vacuum circuit breaker. Conduct a thorough inspection of all cable terminations to identify any signs of poor connection, such as loose or corroded terminals, inadequate insulation stripping, improper tightening of screws or bolts, and proper lugs termination in every stranded cable. Establish a routine inspection and maintenance schedule to check cable joints for signs of damage, overheating, or corrosion. Replace any damaged or deteriorated joints promptly to prevent further issues. | 4 months | We will start inspection regarding cable termination to identify any signs of poor connection. Once inspection is complete will start working accordingly & will share maintenance schedule with working evidence with Accord. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Cabling & Wiring | Fixtures | It was observed that several three-phase receptacles were installed on the ground beside a cable tray and some are left inside the electrical panel lying freely on the metal sheets. This issue was observed in LT panels, Compressor room DBs, and production floors of buildings B2 and B1. | Every two-pin plug should be replaced with a three-pin plug which has a proper earth wire connected to it. Ensure that all power receptacles are fixed properly in place and their cables are protected as well. | 3 months | We will start inspection regarding two-pin plug within the premises, once internal inspection will be completed, will start working accordingly. Further we will rectify all receptacles issues within timeline & will share with Accord. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Cabling & Wiring | Cables support and protection | It was observed that the cables were not laid properly on cable trays. This was observed at every building including B1, B2, B3, B4. | Refer to BS-7671 for providing proper cable support and protection. Every cable should be supported with either a cable trunk or cable ladder depending upon the position and location of cables. | 3 months | We will check all cable trays regarding cable laid issues & will sort out these issues within timeline. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Cabling & Wiring | Cable trench and channel cleanliness | The cable trenches of almost every panel were found to be covered in dirt. This was observed at every building including B1, B2, B3, B4. | Refer to BS-7671 for proper wiring and installation of cables. Trenches, specifically panel trenches should be cleaned and closed. | 2 months | We will check all cable trenches & panels regarding dirt etc. & it will be sorted out within timeline. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Cabling & Wiring | Colour coding | Several panels were found with color coding issues. This was observed at every building including B1, B2, B3, B4. | Only use color code that complies with standards for any new work. Begin by identifying each cable and labeling them accordingly, especially if they deviate from the standard color coding. Use durable and visible labels to indicate the function or purpose of each cable. Reinstall cables that clearly show the difference in phases by using different colored cables color-coded markers, tags, or sleeves to visually distinguish cables that deviate from the standard color coding. | 2 months | We are following color coding requirement in new installation of work now. Further we will check & rectify color coding issues which were highlighted during inspection within timeline. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
19-Mar-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Klash Unit 4 & 5- Plot No 25 117 J.B Near Paharang Drainage Millat Town Millat Road Dhanola, Faisalabad, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 19-Mar-2024, 21-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in all buildings. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard | 2 weeks | We are Working on Lockable mechanisms NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 and will share solution with accord. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in all buildings. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | We are Working on Lockable mechanisms NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 and will share solution with you |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Doors on escape route swinging opposite to the direction of travel in building 2 level ground main gate and side gate and building 4 level 1 and level ground. | Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard. | 3 months | We will Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Sliding exit doors serving the place with more than 10 occupants in building 4 level ground, 1 & 2 and building 3 basement. | Replace sliding doors or provide a pocket door in the sliding panel with side hung swinging doors which swing in the direction of egress travel | 3 months | We will change the direction of all escape doors which provide easily opening mechanisms with Accord Building Standard Section 1 Clauses 1.4 and 1.5. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Number of exits | Number of exits provided are less than the required in level 3 canteen area. | Propose strategy to ensure the sufficient means of escape within acceptable travel distances are available from all buildings and submit to Pakistan Accord for review. | 4 months | We will share drawing work after discussion with engineering team. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Number of exits | Number of exits provided are less than the required in level 3 canteen area. | Provide alternative means of egress from the areas identified to ensure there are sufficient number of exits to accommodate the occupant load and travel distance requirements, in accordance with the Pakistan Accord Building Standard. | F5 + 4 months | After sending the drawing if you approved then we provide the means of egress required to comply with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Exit stairways of building 1 S2, S3; building 2 S2, S4; building 3 S1, S2; building 4 S5 are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Remove fire load from stairs | 2 weeks | All Stairs Fire Load Removed see attached Picture |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Exit stairways of building 1 S2, S3; building 2 S2, S4; building 3 S1, S2; building 4 S5 are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs; - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | After Engineer discussion proper drawing will be share |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | Exit stairways of building 1 S2, S3; building 2 S2, S4; building 3 S1, S2; building 4 S5 are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. - All doors into stairs need to be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. Note that the final exit door from a stair to outside the building do not need to be fire rated. | F8 + 4 months | Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | Exit access of escape routes through unprotected openings and higher risk areas including building 3 lower ground and building 2 basement corridor. | Exit access shall be arranged so that it is not necessary to pass through any higher risk areas and to avoid travel through intervening spaces as per Pakistan Accord Building Standard. Propose strategy to ensure the safe means of escape and submit to Pakistan Accord for review | 4 months | After Engineer discussion proper drawing showing proposed fire alternative means of escape and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Exit access of escape routes through unprotected openings and higher risk areas including building 3 lower ground and building 2 basement corridor. | Provide safe means of exit access by 2-hr fire-rated construction with 1.5-hr opening protective assemblies where required by Pakistan Accord Building Standard. | F10 + 4 months | Safe means of exit access will be completed, including brickwork/ fire rated assemblies where required, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit access | Exit access through areas having headroom clearance less than 2050 mm including building 3 S2 and building 4 S2, S3. | Fix headroom height safety signage and padding around underside of lintel where door height is less than 2.05 m on the escape route. | 2 weeks | Head Room Pending installed and safety sign installed |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit access | Exit access through areas having headroom clearance less than 2050 mm including building 3 S2 and building 4 S2, S3. | Propose modifications to ensure adequate headroom at required locations on the escape route or propose alternative paths that comply with Pakistan Accord Standard and present to Pakistan Accord for review. | 4 months | Factory will prepare drawings showing proposed modifications where here are headroom problems and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit access | Exit access through areas having headroom clearance less than 2050 mm including building 3 S2 and building 4 S2, S3. | Implement measures to ensure adequate clear height under doorway or provide alternative escape route as required after Accord review. | F13 + 4 months | Factory will implement measures to ensure safe escape routes according to proposal submitted to Accord for review |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit capacity | Obstruction along means of egress in building 2 level 2 and building 4 level 3 and level 2. | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 2 weeks | All Escape Path Clear see attached Picture |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit capacity | Obstruction along means of egress in building 2 level 2 and building 4 level 3 and level 2. | Remove obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit capacity. | 2 weeks | obstruction Removed |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Escape stair condition | Handrails not provided on one or both sides of all exit stairs in building 1 and 2. | Provide handrails on both sides of the exit stair in accordance with Pakistan Accord Building Standard | 4 months | in progress |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Travel distance | Travel distance in building 1 level 1 storage area and level ground imported goods area exceeds 23m. | Provide a safe escape path from the south-east corner past the construction works. | 4 months | Emergency Door Installed at imported goods Area travel distance less then 23m |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Travel distance | Travel distance in building 1 level 1 storage area and level ground imported goods area exceeds 23m. | Design the floor evacuation maps/ escape routes complying with Pakistan Accord building standards and submit to Pakistan Accord for review before upgrading works begin. | 4 months | Factory will prepare drawings showing proposed modifications to escape routes and submit to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Travel distance | Travel distance in building 1 level 1 storage area and level ground imported goods area exceeds 23m. | Implement the escape routes as per drawings & design reviewed by Pakistan Accord and maintain it at all times. | F19+ 4 months | Factory will implement measures to ensure compliance with travel distances according to proposal submitted to Accord for review |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Means of Escape | Exit signage | Exit signage insufficient for guiding occupants to exit locations throughout the facility. | Remove misleading direction arrows from the means of egress. | 2 weeks | All Unit check sign and removed wrong direction sign installed the correct direction sign |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Means of Escape | Exit signage | Exit signage insufficient for guiding occupants to exit locations throughout the facility. | Provide exit signage complying with Building Code of Pakistan Standard where signage is missing. | 3 months | Exit Signage in progress |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Means of Escape | Exit signage | Exit signage insufficient for guiding occupants to exit locations throughout the facility. | Ensure that all exit signage is checked periodically and in good working condition. | 3 months | Electrical Team by following NFPA 110 will checked on monthly and annually basis. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Standpipe system | Insufficient number of class 1 standpipe connections provided throughout facility. | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24 | 4 months | We will discuss with fire safety, electrical expert team. After their recommendation will submit design documentation for suppression system (SUPS), including standpipe system and supporting infrastructure, to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Standpipe system | Insufficient number of class 1 standpipe connections provided throughout facility. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F24 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened ly. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Standpipe system | Insufficient number of class 1 standpipe connections provided throughout facility. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS | F25 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site for installation |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Standpipe system | Insufficient number of class 1 standpipe connections provided throughout facility. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F26 + 3 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Standpipe system | Insufficient number of class 1 standpipe connections provided throughout facility. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F27 + 3 months | Factory will advise Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Suppression | Standpipe system | Insufficient number of class 1 standpipe connections provided throughout facility. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F28 + 3 months = 18 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Suppression | Fire pumps | Fire pumps and control equipment comprising non-listed equipment. | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and following steps (1) to (6) above. | 18 months | We will provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Separation of occupancies | Building 4 level 1 office and production is not fire separated by opening protective assemblies. | Propose design and layout showing how different occupancies can be rearranged and/or enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | We will prepare drawings showing proposed fire separating construction or re-arrangement of different occupancies and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Separation of occupancies | Building 4 level 1 office and production is not fire separated by opening protective assemblies. | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | F31 + 4 Months | Separation of occupancies will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Storage | Miscellaneous in process storage found exceeding allowable limits and dedicated storage area not separated by fire rated construction in building 1 level 1, level 3 & ground; building 2 level 1, 2, 3; building 3 basement, level 3; and building 4 level ground. | Identify all designated storage areas. Rearrange in process storage in Production areas, where possible to meet in-process storage limitations described above. For all storage areas where storage cannot be managed within in-process storage limitations described above, prepare drawings showings proposed fire separation details of storage areas. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors. Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | We will prepare drawings showing proposed arrangement of in-process storage and fire separating construction where necessary and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Storage | Miscellaneous in process storage found exceeding allowable limits and dedicated storage area not separated by fire rated construction. | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | F33 + 4 Months | Fire rated separation of storage areas will be completed, including brickwork/ fire rated assemblies, and in-process storage arranged to suit limitations, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Separation of high-risk areas | Building 4 level ground LT room and compressor area not separated by fire rated construction. | Enclose electrical distribution boxes with steel doors. | 4 months | Building 4 level-1 electric room steel door install |  |  |  | Pending Verification
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Separation of high-risk areas | Building 4 level ground LT room and compressor area not separated by fire rated construction. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms etc.) - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | We will discuss with Engineer Team and prepare drawings showing proposed fire separating construction of high-risk areas and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Separation of high-risk areas | Building 4 level ground LT room and compressor area not separated by fire rated construction. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F36 + 4 Months | Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Rated Construction | Atrium | Building 2 Ground Floor has storage of cartons within a large volume un-compartmented space, four storeys high, covered roof and open corridors used for escape in upper floors. | Prepare drawings showing the proposed fire separation and means of escape from all areas bordering on the atrium and submit to Pakistan Accord for review. | 4 months | We will share further detail after discussion with Engineer Team and provide drawings showing proposals for separation of the atrium and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Rated Construction | Atrium | Building 2 Ground Floor has storage of cartons within a large volume un-compartmented space, four storeys high, covered roof and open corridors used for escape in upper floors. | Provide fire rated construction including opening protection assemblies i.e. fire doors and alternative means of escape according to the layouts and documents reviewed by Pakistan Accord. | F38 + 4 Months | Fire rated protection of the atium will be completed according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Hazardous Materials | Chemicals storage | Storage of chemicals found in building 2 and 4 which are not stored in fire rated enclosure and not stored per Pakistan Accord Building standard. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30 and hazardous material management according to NFPA 400, Hazardous Materials Code, 2013. | 4 months | in progress |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
19-Mar-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Klash Pvt. Ltd. (Units 4 & 5) - Plot No 25 117 J.B Near Paharang Drainage Millat Town Millat Road Dhanola, Faisalabad Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 19-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, building 4, C-4 columns at the Ground floor level appear to be overstressed, subject to the applied combined loads (Axial + Moment). | Verify in-situ concrete stresses either by 100mm dia. cores or existing cylinder strength data for the identified columns or 100mm dia. cores from 4 columns and submit the results to Accord. | 2 months | Factory has conducted core testing to identified columns or 100mm dia. cores from 4 columns in Building 4. Factory has conducted Core testing of said columns. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, building 4, C-4 columns at the Ground floor level appear to be overstressed, subject to the applied combined loads (Axial + Moment). | Verify the rebar size of the identified column by exposing the rebar on the surface of column in a small patch to determine whether rebar size is 20mm or 25mm, along with the ferro-scan to check the number of bars in the column and submit the data with pictorial evidence to Pakistan Accord for review. | 2 months | Factory has exposed the rebar on the surface of column in a small patch to determine whether rebar size 20mm or 25mm, along with the ferro-scan to check the number of bars Factory has conducted Ferro scanning of said columns. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, building 4, C-4 columns at the Ground floor level appear to be overstressed, subject to the applied combined loads (Axial + Moment). | Factory Engineer to review design, loads and columns stresses subject to the results of the concrete strength & identification of rebars size actions. | 3 months | Factory's appointed structural engineer is in process to review design,loads and columns stresses subject to the results of the concrete strength & identification of rebars size actions. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment, building 4, C-4 columns at the Ground floor level appear to be overstressed, subject to the applied combined loads (Axial + Moment). | Propose remedial solution if necessary, considering the stresses, subject to the result of concrete strength and rebar size and share the data with Pakistan Accord for review. | S3+1 month | Once factory's structural engineer will review and advise regarding results and further action subject to the result of concrete strength and rebar size will share with accord team for review. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | Based on an initial assessment, building 4, C-4 columns at the Ground floor level appear to be overstressed, subject to the applied combined loads (Axial + Moment). | Carry out remediation works if any and produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | S4+3 months | Once factory's structural engineer will review and advise regarding results and further action subject to the result of concrete strength and rebar size will share with accord team for review. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural Documentation | Differs from as-built structure | Relates to the building 4. C-4 Columns from Ground floor to first floor size reduction is observed. | Structural Engineer to confirm measurements, analyse the columns in detail and determine whether remedial works are required for the columns. Submit the analysis results to Pakistan Accord for review, followed by the proposal of remediation of the columns if required. | 6 months | Once factory's structural engineer will review and advise regarding results and further action subject to the result of concrete strength and rebar size will share with accord team for review. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural Documentation | Differs from as-built structure | Relates to the building 4. C-4 Columns from Ground floor to first floor size reduction is observed. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation and implement the remediation action if needed and as reviewed with Pakistan Accord. | 6 months | Once factory's structural engineer will review and advise regarding results and further action subject to the result of concrete strength and rebar size will share with accord team for review. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural Documentation | Undocumented modification | Relates to the buildings Building-1 and Building-2. As built structural drawings needs to be updated , the shape of columns of the structural drawings in highlighted area are not matching with Site layout and Architectural Drawings of building 1 & 2. | Building Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | Once factory's structural engineer will review and advise regarding results and further action subject to the result of concrete strength and rebar size will share with accord team for review. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 119 | 421 | 6 | 5
3 | 8 |  | 120 | 421 | 6 | 5
3 | 8 |  | 121 | 421 | 6 | 5
3 | 8 |  | 122 | 421 | 6 | 5
3 | 8 |  | 123 | 421 | 6 | 5
3 | 8 |  | 124 | 421 | 6 | 5
3 | 8 |  | 125 | 421 | 6 | 5
3 | 8 |  | 126 | 421 | 6 | 5
3 | 8 |  | 127 | 421 | 6 | 5
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1