## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
10-May-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Denim-E (Pvt) Ltd. (Unit-2), Plot#19, Sector 27, Korangi Industrial Area Karachi, Sindh, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-05-10
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | During the inspection It was observed that the single line diagram available on site lacked sufficient details and was not up-to-date. | Engage a qualified electrical engineer to develop comprehensive electrical single line diagrams for the entire facility. Ensure all components and connections are accurately represented. | 6 months | Factory will engaged a qualified electrical engineer to develop single line diagram and submit to Accord for review. Once completed factory will ensure a match between SLD and site condition |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked essential electrical layout drawings, including small power layouts, lighting layouts, and containment layouts. | Engage a qualified electrical engineer to develop comprehensive electrical layout drawings. To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. | 8 months | Factory will engaged a qualified electrical engineer to develop single line diagram and submit to Accord for review. Once completed factory will ensure a match between SLD and site condition |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Main Building on level(s) M01 - Mezzanine The inspection of the main electrical room, it was observed that Main LT room circuit breaker was found with Burn Spot | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). | 1 month | Factory will engaged a qualified electrical engineer to evaluate circuit breaker ratings and replace all old breakers or cables whose size is less than needed for actual running load |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Main Building on level(s) L00 - Ground Floor It was observed that the distribution board near the pump room on the ground floor was found to lack coordination between the circuit breaker and the cable. A 16 sq. mm cable was terminated on a 100A circuit breaker | Properly sized circuit breakers must be installed. Additionally, investigate the burnout signs and establish an SOP to prevent temporary connections to the live parts of circuit breakers. | E3 + 1 month | Factory will evaluate and do the needful and develop SOP for temporary connections |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Circuit breakers | During the inspection of the main electrical room, it was observed that burn marks were found on several breakers throughout the facility. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). | 1 month | Factory will evaluate and do the needful. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Main Building on level(s) L00 - Ground Floor During the inspection in the mosque area on the ground floor, a hanging switch was observed connected to a circuit breaker. | Schedule a proper maintenance records to monitor, control and rectify weak electrification works. | 3 months | Factory will remove all the temporary and improper connections. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Hot Spots | This relates to the Main Building on level(s) L03 - Third Floor During the inspection of production Area 3rd Floor: Abnormal temperature recorded at almost 124°C indicating loose bolt on copper bus terminals | Rectify hot spots by addressing and repairing the cause of abnormal temperature in cable joint, which may involve overloading, connection tightening, or replacement of faulty cable joint. | 1 month | Factory will rectify the highlighted issue |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | This relates to the Main Building on level(s) L00 - Second Floor During the inspection AC circuit breaker in Office area 2nd Floor: Operating at an elevated temperature of 88°C due to undersize cable being overloaded. | Inspect all electrical panel to identify the source of abnormal temperatures, which may be caused by phase imbalance, loose connections, overloaded circuits, or other issues. Create a schedule to have a thermograph survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. | 1 month | Factory will inspect all the panels and resolve all the relevant issues. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Hot Spots | This relates to the Main Building on level(s) L00 - Mezzanine During the inspection Solar Fuse in LT Room Mezzanine: Operating at an elevated temperature of 87.7°C due to less ventilation and air conditioning in room | All electrical panel to identify the source of abnormal temperatures, which may be caused by phase imbalance, loose connections, overloaded circuits, or other issues. Create a schedule to have a thermograph survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. | 1 month | Factory will inspect all the panels and resolve all the relevant issues. Factory has already installed 2 split Air Conditions of 2 ton to maintain a proper temperature to prevent elevated temperature of components. |  |  |  | Pending Verification
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Hot Spots | This relates to the Main Building on level(s) B00 - Basement During the inspection of Basement Motor Panel TP MCB: Cables termination showed a temperature of 76°C due to lose connection of a single phase | Carry out independent thermographic survey. | 6 months | Factory will arrange thermographic survey independently after internal inspection of all panels, and share test result with Pakistan Accord for review.. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | This relates to the Main Building on level(s) B00 - Basement There was an incomplete earthing system found throughout the facility, the earth pits were present but the earth was just connected to the main LTs. No Earth connection was found in production area distribution boards. | Consult to an engineering firm, develop and install full earthing system according to proper schematics and designs approved by Pakistan Accord. | 2 months | Factory will appoint a qualified person to develop and install a full earthing system according to proper schematics and designs reviewed by Pakistan Accord. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Earthing system | There was an incomplete earthing system found throughout the facility, the earth pits were present but the earth was just connected to the main LTs. No Earth connection was found in stitching area power receptacles. | All earth connections must be connected to earth pits via their respective distribution boards, extending the connection till the end-user machine to ensure proper grounding. | 6 months | Factory will install a full earthing system and share all the designs with Accord. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Earthing system | This relates to the Main Building on level(s) L03 - Third Floor In most of the areas, earth bonding of cable tray, metal structures, metal tables and motor frames found missing especially No Earth found connected to Washing machines placed at washing area 3rd floor. | Consult to an engineering firm, develop and install full earthing system according to proper schematics and designs approved by Pakistan Accord. | 2 months | Factory will appoint a qualified person to develop and install a full earthing system according to proper schematics and designs reviewed by Pakistan Accord. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Earthing system | In most of the areas, earth bonding of cable tray, metal structures, metal tables and motor frames found missing especially No equipotential bonding with earth was evident on distribution boards doors. | Connect all metal bodies of Electric panels to the earth terminal within electric panels. Metal that is likely to be live near electrical installation shall be bonded with earth to avoid any hazard. | 6 months | Factory will install a full earthing system and share all the designs with Accord. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, The internal wiring of the control was found unsupported inside the LT panel, in close proximity to a live busbars, which can lead to insulation failure and short circuits. | Schedule a proper maintenance records to monitor, control and rectify weak electrification works. | 2 months | Factory will schedule a maintenance activity, and resolve he highlighted issue. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, A bundle of uncovered wires, either live or dead, was found inside a distribution board in the production area. These wires are very close to the internal doors of the distribution board, posing a significant risk of short circuits. | Removal/Dismantling of Idle cables and cable dressing need to be done for each distribution board. Ensure no cable bunching and splicing at all. | 3 months | Factory will schedule a maintenance activity, and resolve he highlighted issue. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, Live busbars in the LT panel were found covered with polythene sheets, which is extremely hazardous due to the lack of insulation and proper tagging. Additionally, there was no safety cover present. | All electrical components must be protection against fire risk factors. Replace it with properly designed switchboard mounted on wall surface with no exposed wiring. | 3 months | Factory will replace LT panels with properly designed switchboard mounted on wall surface with no exposed wiring. The highlighted busbar was already disconnected. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, The PVC distribution board was found with uneven internal wiring and bunching of all neutral wires on a connection strip. This strip is nearly damaged due to rust on the screws and its mounting position | Schedule a proper maintenance records to monitor, control and rectify weak electrification works. | 3 months | Factory will install additional metal body panels and ensure proper separate change panel. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Loop Connection | During our inspection, we observed the loop connections within the overall panel. In these loop connections, we energize one circuit breaker from the live part of another circuit breaker. This results in loops within the panel instead of a busbar system. | Modify the installation to prevent circuit breakers from having any loop connections. This may involve adding copper bus strips to existing panels and connecting breakers to their respective phase bus strips. | 3 months | Factory will will appoint a qualified person to assess the loop connections and modify as necessary. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Multiple Connections | While conducting our survey we have noticed that Multiple connections were found terminated on the power plug of the stitching machine, which is inappropriate. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. | 3 months | Factory will will appoint a qualified person to assess the circuits and modify as necessary. |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Multiple Connections | While conducting our survey we have noticed that Multiple connections were found linked on a PVC connector at the cutting table. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. | 3 months | Factory will will appoint a qualified person to assess the circuits and modify as necessary. |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Multiple Connections | While conducting our survey we have noticed that overall, distribution boards have multiple connections, as one MCB/MCCB is running many circuits in sharing | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. | 3 months | Work in progress. |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | DBs & Elec Protection Systems | Openings | During inspection it was observed at various location that the distribution board have unsealed openings having sharp edges which can damage insulation of the cables in LT Panel in LT Room at Mezzanine | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 3 months | Factory will seal all the openings and resolve issues related to this point. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | DBs & Elec Protection Systems | Openings | During inspection it was observed at various location that the distribution board have unsealed openings having sharp edges which can damage insulation of the cables in Production area & Stitching floors. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 3 months | Factory will seal all the openings and resolve issues related to this point. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Openings | During inspection it was observed at various location that the distribution board have unsealed openings having sharp edges which can damage insulation of the cables in Basement and Roof | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt | 3 months | Factory will seal all the openings and resolve issues related to this point. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | DBs & Elec Protection Systems | Adequate accessibility | During the survey, it was noted that various locations exhibited inadequate work clearance in Distribution board placed in basement stuck with material stacking | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 1 month | Factory will provide adequate accessibility for sufficient space. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | DBs & Elec Protection Systems | Adequate accessibility | During the survey, it was noted that various locations exhibited inadequate work clearance at Compressor panel at roof which is stuck with storage material. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 1 month | Factory will provide adequate accessibility for sufficient space. |  |  |  | Pending Verification
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | Lightning protection system is not installed in the facility. No document related to LPS assessment was found. | Factory to undertake a risk assessment to see whether a Lightning Protection System is required a qualified engineer. Design system accordingly if required and present to Pakistan Accord for review. | 2 months | Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review. Factory will install new LPS system as per design previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | Lightning protection system is not installed in the facility. No document related to LPS assessment was found. | Provide LPS if required as per design submitted previously to Pakistan Accord for review | E28 + 1 month | Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. Some of the deficiencies observed are as follows: - not a listed system - cabling not listed as fire rated - does not provide alarm and notification features consistent with standards. - repeatedly showing faults, e.g. Zone 4: First Floor and Zone 6: Third Floor - fire alarm panel Lead-Acid battery was unable to provide battery backup - detectors incorrectly installed or obstructed mostly in production area - no coverage in areas e.g. offices of 1st , 2nd and 3rd floor in production area. | Panel must be operational throughout the facility. Ensure the efficient functioning of the existing alarm and detection system throughout the building, extending its coverage to include the roof area. | 1 month | Factory to ensure the efficient functioning of the existing alarm and detection system throughout the building. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. Some of the deficiencies observed are as follows: - not a listed system - cabling not listed as fire rated - does not provide alarm and notification features consistent with standards. - repeatedly showing faults, e.g. Zone 4: First Floor and Zone 6: Third Floor - fire alarm panel Lead-Acid battery was unable to provide battery backup - detectors incorrectly installed or obstructed mostly in production area - no coverage in areas e.g. offices of 1st , 2nd and 3rd floor in production area. | (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) and submit to Pakistan Accord for review before purchasing any new equipment. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E31 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E32 + 4 month | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E33 + 5 month | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E34 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E35 + 3 month | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Detectors | During the inspection, it was observed that many areas were missing detectors. Although a stand-alone detector scheme was installed in the production areas, numerous locations still lacked proper coverage. The specific areas without detectors are listed below: • LT room • Compressor room • ETP entrance basement • HR office • Storage areas basement and ground floor • 2nd Carton storage area • 3rd Floor quality office • 4th Floor kitchen area • Many offices area occupied from 1st to 4th floor. | Consult a qualified engineer to design and implement FADS system as per NFPA standard as recommended in Section 8.1 | 3 months | Factory will ensure full coverage of detectors as per NFPA requirements as part of the FADS system |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Fire Alarm & Detection System (FADS) | Manual Call Points | The fire alarm system was tested using the push button approach from the 2nd to 5th floors. During the test, the following issues were observed: • The facility uses a push button hooter alarm system instead of a manual call point (MCP). • The number of push buttons was insufficient on each floor. • Several push buttons were found to be non-functional, and the alarm did not actuate. • There was an isolating circuit breaker in the LT room for the push button circuit that was off during the testing. • The alarm sounders produced inadequate sound in the production areas. • The system operated on a 220V AC supply, which will fail during a power outage. | Consult a qualified engineer to design and implement FADS system as per NFPA standard as recommended in Section 8.1 | 3 months | Factory will ensure full coverage of detectors as per NFPA requirements as part of the FADS system |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Emergency Lighting | No emergency lighting | During the inspection of the emergency lighting system, it was noted that several emergency lights did not comply with building standards Internal Stair case initiating from basement near ETP | A qualified engineer to be consulted to design an emergency lighting system. All emergency lights of an area must be supplied by dedicated circuits, having separate circuit breaker in the main panel, also need to regularly check the battery backup of lights for necessary replacement. Submit proposed design to Pakistan Accord for review | 3 months | Factory will installed emergency lighting system. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Emergency Lighting | No emergency lighting | During the inspection of the emergency lighting system, it was noted that several emergency lights did not comply with building standards Backyard Area at Ground Floor. | All walkways, stairs and emergency exits need to be equipped with emergency lights. Ensure, emergency lights of an area must be supplied by dedicated circuit, having separate circuit breaker in the main panel. | 3 months | Factory will installed emergency lighting system. |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Emergency Lighting | No emergency lighting | During the inspection of the emergency lighting system, it was noted that several emergency lights did not comply with building standards on Emergency Stairs and production area stitching floor. | A qualified engineer needs to be consulted to design and install an emergency lighting system. | 3 months | Factory will installed emergency lighting system. |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Emergency Lighting | Provided but non-functional | During the inspection of the emergency lighting system, we found that only a few areas were equipped with emergency lights are Non-Operational emergency light on staircase | All non-functional emergency lighting fixtures needs to be immediately fixed. A regularly check the battery backup of lights for necessary replacement. | 2 months | Factory will replace all the non functional light with the new lights |  |  |  | Pending Verification
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Emergency Lighting | General Lighting | During the inspection, it was observed that following Ares have a significant deficiency in general lighting: • Mezzanine storage area behind LT room • Area near Washing Machines • Ramp area from basement to ground floor • Storage area in basement near ETP entrance | All floors, offices and production areas need to be equipped with general lighting. | 3 months | Factory will installed the lights after the proper finalization of layouts |  |  |  | Pending Verification
3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Generator, Transformer & Sub-Station Room | Working clearance | During the survey, it was noted that various locations exhibited inadequate work clearance within facility such as • Generator placement externally • Generator fuel/oil storage placement near main gate at ground floor | Reorganise the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways.Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance check. | 6 months | Factory will reorganise/ remove the equipment layout to ensure adequate clearance |  |  |  | Pending Verification
3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E45 | Generator, Transformer & Sub-Station Room | Battery | During inspection, it was observed that the batteries of generator had some fluid spills as we had seen fluid spread off the batteries. Furthermore, the battery placement for generator was inadequate and their terminal are bare. This is not safe and have a risk of electrocution as well as causing fire if exposed to combustible materials. | Hazardous substance placed inside the Generator room need to be placed in their designated area. Bare terminals of battery need to be covered. | 1 month | Factory will remove hazardous substance from the generator room and place it to designated area |  |  |  | In Progress
3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E46 | Generator, Transformer & Sub-Station Room | Battery | During inspection, it was observed that the batteries of generator had some fluid spills as we had seen fluid spread off the batteries. Furthermore, the battery placement for generator was inadequate and their terminal are bare. This is not safe and have a risk of electrocution as well as causing fire if exposed to combustible materials. | Battery placement and cabling will be adjusted to comply with BS-7671 and NFPA standards, alongside performing a thorough periodic maintenance of the generator. | 1 month | Factory will provide covers on terminals and make sure to place the battery properly. |  |  |  | In Progress
3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E47 | Generator, Transformer & Sub-Station Room | Back-up power supply | During the inspection, we observed that a backup power supply (UPS) is being used in the plotter room. However, the UPS is not properly ventilated and its placement needs adjustment to maintain sufficient height from the floor. Additionally, the power plugs have a limiting rating and a risk of becoming loose. | Adjust the circuit breaker to the proper height and replace the PVC plugs with a distribution board equipped with circuit breakers for enhanced safety and reliability. Additionally, ensure the UPS is not overloaded beyond its capacity. | 1 month | Factory will relocate the UPS at suitable height and make sure to implement safety. |  |  |  | In Progress
3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E48 | Cabling & Wiring | Cables support and protection | During the inspection it was observed that the cables are not protected and supported properly in below areas: • Loose power receptacles found in production area • Loose cable feeding a water pump in basement | Fix the damaged equipment or remove if they are idle (not in use). Install appropriate cable containment arrangement for the electrical system. All exposed wiring shall be avoided in future installation. | 3 months | Factory will fix or replace damaged equipment as required |  |  |  | In Progress
3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E49 | Cabling & Wiring | Cables support and protection | During the inspection it was observed that the cables are not protected and supported properly in below areas: • Loose cable with no containment found in compressor distribution board. • Loose connection for battery | All kind of exposed wiring must be laid with proper dressing and their relevant conduits. Install appropriate cable containment arrangement for the electrical system. | 3 months | Factory will fix or replace damaged equipment as required |  |  |  | In Progress
3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E50 | Cabling & Wiring | Splicing of cables | During inspection it was noted that LT Room was found to have loose cables with tape joints. | Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. All stranded cables terminations shall be installed with proper cable lugs. | 4 months | Factory will replace affected cables as required |  |  |  | Pending Verification
3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E51 | Cabling & Wiring | Splicing of cables | This relates to the Main Building on level(s) L02 - Second Floor During inspection it was noted that Cutting machines on the production floor have spliced cables. | Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. All stranded cables terminations shall be installed with proper cable lugs. | 4 months | Factory will replace affected cables as required |  |  |  | Pending Verification
3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E52 | Cabling & Wiring | Splicing of cables | This relates to the Main Building on level(s) L00 - Ground Floor During inspection it was noted that the mosque's distribution board contains multiple tape joints. | Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. All stranded cables terminations shall be installed with proper cable lugs. | 4 months | Factory will replace affected cables as required |  |  |  | Pending Verification
3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E53 | Cabling & Wiring | Splicing of cables | During inspection it was noted that Stitching machines on the production floor have multiple spliced cable joints wrapped with PVC tape. | Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. All stranded cables terminations shall be installed with proper cable lugs. | 4 months | Factory will replace affected cables as required |  |  |  | In Progress
3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E54 | Cabling & Wiring | Cable trench and channel cleanliness | It was noted in several locations that cleanliness was not being maintained within the electrical panels and trunking system KE meter panel metallic enclosure at the main gate of the factory. | Electrical trunking to be cleaned, inspected, and free from dust and dirt. | 2 months | Factory will clean electrical trunking and ensure free from dust and dirt |  |  |  | Pending Verification
3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E55 | Cabling & Wiring | Cable trench and channel cleanliness | This relates to the Main Building on level(s) L00 - Ground Floor It was noted in several locations that cleanliness was not being maintained within the electrical panels and trunking system. Cable trays behind pumps on the ground floor | Electrical trunking to be cleaned, inspected, and free from dust and dirt. | 2 months | Factory will clean electrical trunking and ensure free from dust and dirt |  |  |  | Pending Verification
3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E56 | Cabling & Wiring | Cable trench and channel cleanliness | It was noted in several locations that cleanliness was not being maintained within the electrical panels and trunking system. The cable trunking system was found filled with a high quantity of fluff, dust, and combustible material, posing a high fire risk Cable trays/containments in the production area | Electrical trunking to be cleaned, inspected, and free from dust and dirt. | 2 months | Factory will clean electrical trunking and ensure free from dust and dirt |  |  |  | Pending Verification
3 | 8 |  | 166 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E57 | Cabling & Wiring | Fixtures | It was observed that several three-phase receptacles were installed on the ground beside a cable tray, and some were left inside the electrical panel, lying freely on metal sheets at Plotter room with loose wires and unmounted power receptacles | Damage power receptacles need to be replaced. Every two-pin plug should be replaced with a three-pin plug which has a proper earth wire connected to it. | 3 months | Factory will replace damaged receptacles as required |  |  |  | In Progress
3 | 8 |  | 167 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E58 | Cabling & Wiring | Fixtures | It was observed that several three-phase receptacles were installed on the ground beside a cable tray, and some were left inside the electrical panel, lying freely on metal sheets Damaged power sockets throughout the facility. | Ensure that all power receptacles are fixed properly in place and their cables are protected as well. | 3 months | Factory will properly fix damaged receptacles as required |  |  |  | In Progress
3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E59 | Cabling & Wiring | Fixtures | It was observed that several three-phase receptacles were installed on the ground beside a cable tray, and some were left inside the electrical panel, lying freely on metal sheets Melted power sockets in the production area where dryers are used. | Ensure that all power receptacles are fixed properly in place and their cables are protected as well. | 3 months | Resolved |  |  |  | In Progress
3 | 8 |  | 169 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E60 | Cabling & Wiring | Fixtures | It was observed that several three-phase receptacles were installed on the ground beside a cable tray, and some were left inside the electrical panel, lying freely on metal sheets Power board mounted with fiber threads on the inspection table in the production area. | Ensure that all power receptacles are fixed properly in place and their cables are protected as well. | 3 months | Factory will properly fix damaged receptacles as required |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
10-May-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Denim-E (Pvt) Ltd. (Unit-2), Plot# 19, Sector 27, Korangi Industrial Area Karachi, Sindh, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-05-10
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in the building including the staircase doors and factory main exit gates. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | Factory will remove all the non-compliant locking features from doors. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in the building including the staircase doors and factory main exit gates. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 &1.5 | 3 months | Need Clarification |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Sliding door found in escape at level 4 production. | Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit as per Pakistan Accord Building Standard cl.1.5 | 3 months | Factory will provide pocket door into existing door. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Number of exits | Number of exits provided are less than the required in level 4 marketing office. | Limit the number of people to less than 50 until second exit is provided. | 1 month | Factory will limit the number of peoples to 50. |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Number of exits | Number of exits provided are less than the required in level 4 marketing office. | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory will plan for the possible solution and provides detail to pakistan Accord. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Number of exits | Number of exits provided are less than the required in level 4 marketing office. | Provide safe/alternative means of egress from the areas identified to ensure there are sufficient number of exits to accommodate the occupant load and travel distance requirements, in accordance with the Pakistan Accord Building Standard. | F5 + 4 months | Factory will plan for the possible solution and provides detail to pakistan Accord. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | All 3 Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. | Remove Fire load from the stairs. | 1 month | Done, factory will provide pictorial evidence |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | All 3 Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover: 1) Layout showing the location of fire rated walls/doors to protect the stairs; 2) Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | Factory will appoint an architect to propose how the stair will be protected and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | All 3 Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. All doors into stairs need to be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. | F8 + 4 months | Factory will implement proposal after review by Accord. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Escape stair condition | Staircase S1, S2, S3 and inside main gate has missing handrails. | Provide handrails on both sides of the exit stair in accordance with Pakistan Accord Building Standard | 1 month | Factory will install all the secondary handrails on stairs |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Obstruction and trip hazard found along the means of egress in S1 entrance from roof, level 2 hallway and basement access to S1. | Remove obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit capacity. | 1 month | Factory will remove all the mentioned obstruction. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit access | Obstruction and trip hazard found along the means of egress in S1 entrance from roof, level 2 hallway and basement access to S1. | Submit the proposal to the Accord for review the planned changes encompassing the uneven steps in staircase per Pakistan Accord Building Standard. | 4 months | Factory will remove all the mentioned obstruction. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit access | Obstruction and trip hazard found along the means of egress in S1 entrance from roof, level 2 hallway and basement access to S1. | Escape routes shall be monitored for obstructions and implement all agreed actions on site. | F12 + 4 months | Factory will remove all the mentioned obstruction. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Staircase S2 discharge inside the building; Staircase S3 discharge is obstructed and facility exit is through high risk area. | Remove obstruction from the blocked route. | 1 month | Factory will remove all the mentioned obstruction. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit discharge | Staircase S2 discharge inside the building; Staircase S3 discharge is obstructed and facility exit is through high risk area. | Prepare drawings showings proposed fire separation details of the exit discharge routes. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors; - Details of fire rated walls and doors (e.g. listing, fire rating period, door self-closers, door opening direction) | 4 months | Factory will appoint an architect to propose how the route will be protected and submit to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit discharge | Staircase S2 discharge inside the building; Staircase S3 discharge is obstructed and facility exit is through high risk area. | Ensure exit discharge routes are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow Pakistan Accord Building Standard. - All doors into stair discharge routes need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into exit discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge routes need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. Where stairs discharge within the building, a fire separated corridor shall be provided that leads outside building. | F15 + 4 months | Factory will implement plan reviewed by Accord previously |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Travel distance | Common path travel distance on mezzanine floor exceeds 23m. | Design modifications to ensure travel distance code compliance for escape routes or propose alternative paths that comply with Pakistan Accord Standard and BCP and present to Pakistan Accord for review. | 4 months | Factory will appoint an architect to propose how the an additional exit will be provided and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Travel distance | Common path travel distance on mezzanine floor exceeds 23m. | Provide alternative exiting arrangements to reduce the travel distances to be in accordance with the Pakistan Accord Building Standard. | F17 + 4 months | Factory will provide Emergency exit |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit signage | Missing exit signage on exit doors, throughout floors and final exit to building and premises, also misleading exit directions. | Remove misleading direction arrows from the means of egress. | 1 month | Factory will provide additional signage and remove the misleading directions. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Exit signage | Missing exit signage on exit doors, throughout floors and final exit to building and premises, also misleading exit directions. | Provide exit signage complying with Building Code of Pakistan Standard where signage is missing. | 3 months | Factory will provide additional signage and remove the misleading directions. |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Means of Escape | Exit signage | Missing exit signage on exit doors, throughout floors and final exit to building and premises, also misleading exit directions. | Ensure that all exit signage is checked periodically and in good working condition. | F20 + 1 month | Factory will provide additional signage and remove the misleading directions. |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 15 m in height to highest occupiable floor. | (1) Submit design documentation for a sprinkler system along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24 | 4 month | Factory will appoint consultant and submit design documentation for suppression system (SUPS), including standpipe system and supporting infrastructure, to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 15 m in height to highest occupiable floor. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F22 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 15 m in height to highest occupiable floor. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F23 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and proceed with installation |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 15 m in height to highest occupiable floor. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F24 + 3 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 15 m in height to highest occupiable floor. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F25 + 3 months | Factory will advise Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Sprinkler system | No automatic sprinkler system provided for building more than 15 m in height to highest occupiable floor. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F26 + 3 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Fire pumps | There is no fire pump at the facility. | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and following steps (1) to (6) above. | 18 months | Factory has already procured ULFM approved naffco fire pump, pump has already in house since last 3 months we will submit full documentation on pumps for Accord review. |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Suppression | Fire pumps | There is no fire pump at the facility. | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and following steps (1) to (6) above. | 18 months | Factory will provide pumps as part of the supporting infrastructure for the SUPS system as above |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Suppression | Standpipe system | Insufficient number of class 1 standpipe connections provided throughout facility and damaged hose found at some places. | Provide Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system and following steps (1) to (6) above. | 18 months | Factory will provide pumps as part of the supporting infrastructure for the SUPS system as above |  |  |  | Pending Verification
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Separation of shafts | The lift shafts have unprotected opening in production floors. | Submit proposal for fire protection of lift shaft openings to Pakistan Accord for review, the design should comply with the Pakistan Accord Building Standard. | 4 months | Factory will prepare drawings showing proposed fire separating construction for lift shafts and submit to Accord for review prior to the rectification works |  |  |  | Pending Verification
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Separation of shafts | The lift shafts have unprotected opening in production floors. | Separate lift shaft by fire-rated construction, implementing the previously reviewed design proposal. | F31 + 4 months | Fire rated separation of shafts will be completed,according to proposal previously reviewed by Accord |  |  |  | Pending Verification
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Floor openings | Penetrations and opening in between floors in ground, mezzanine and basement. | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory will prepare drawings showing proposals for fire separation at floor openings and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Floor openings | Penetrations and opening in between floors in ground, mezzanine and basement. | Maintain fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure. | F33 + 4 months | Fire rated separation at openings between floors will be completed,according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Separation of occupancies | Level 4 office is not fire separated from production through fire rated construction. | Prepare drawings showing proposed fire separation details of separation of occupancies. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors. - Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will prepare drawings showing proposals for fire rated construction to separate different occupancies and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Separation of occupancies | Level 4 office is not fire separated from production through fire rated construction. | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | F35 + 4 months | Fire rated construction will provide separation between occupancies, including brickwork and opening assemblies,according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Storage | Dedicated storage area not separated by fire rated construction at level 5, level 1 and basement. | Identify all designated storage areas.For all storage areas where storage cannot be managed within in-process storage limitations described above, prepare drawings showings proposed fire separation details of storage areas. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors. - Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will prepare drawings indicating how in-process storage will be controlled within allowable limitations, and showing proposals for fire rated separation of large areas of storage and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Rated Construction | Storage | Dedicated storage area not separated by fire rated construction at level 5, level 1 and basement. | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | F37+ 4 months | For large areas of storage fire rated separation will be provided, in accordance with proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Hazardous Materials | Chemicals storage | Bulk storage of flammable and combustible liquids at basement and along S2 staircase is not fire compartmented and ventilated for the occupants working inside. | All chemicals flammable or dangerous not immediately needed for production should be stored in designated rooms. | 1 month | Factory will manage to store all the chemical on designated place |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Hazardous Materials | Chemicals storage | Bulk storage of flammable and combustible liquids at basement and along S2 staircase is not fire compartmented and ventilated for the occupants working inside. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities, ventilation, following the electrical specifications and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. All chemical storage area needs to be fire separated from rest of the building by a 2 hour rated fire construction and the room must be properly ventilated. | 4 months | MSDS sheets will be provided that identify storage requirements for all chemicals used on site and submitted to Accord for review. Factory will follow recommendations and provide storage for chemicals in accordance with NFPA 30. |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Fire Safety Management | Emergency Action Plan | Evacuation maps are missing at some places and Action Plan document is not available and ERT roles and responsibilities not defined. | Prepare a draft of an evacuation plan for review and comments by Accord. Prepare a drawing showing where evacuation plans will be located. Prepare an Emergency Action Plan report. | 3 months | Factory will prepare a draft of an evacuation plan for review and comments by Accord. EAP will be implemented and records kept as required |  |  |  | Pending Verification
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Fire Safety Management | Emergency Action Plan | Evacuation maps are missing at some places and Action Plan document is not available and ERT roles and responsibilities not defined. | Ensure Evacuation Action Plans are posted in the building per NFPA 2800. | F41 + 1 months | Evacuation maps will be posted on each floor as required by EAP |  |  |  | Pending Verification

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2024-05-10
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Denim-E (Pvt) Ltd. (Unit-2), Plot# 19, Sector 27, Korangi Industrial Area Karachi, Sindh, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-05-10
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal columns at the Ground floor level appear to be overstressed against the observed load. | Building engineer to scan all columns along the gridlines marked using ferro scanner to confirm number and diameter of the reinforcing bars in the columns in the basement and submit to Pakistan Accord for review. | 2 months | Factory will provide Ferroscan reports for all columns required along with design to Accord for review. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal columns at the Ground floor level appear to be overstressed against the applied load. | Factory Engineer to review design, loads and columns stresses in area identified above. | S1 + 1 month | Factory management will concern with building engineer for review the design and provide the stability reports. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal columns at the Ground floor level appear to be overstressed against the applied load. | Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the columns identified in the report. | S2+ 3 months | Factory will provide concrete cylinder strength reports from tests taken during construction or contract an approved laboratory to determine the concrete strength by taken at least 4 No. 100 diam cores, and submit reports on concrete strength to Accord for review. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal columns at the Ground floor level appear to be overstressed against the applied load. | Produce and actively manage a loading plan for all floor plates within the factory considering floor capacity and column capacity. | 6 months | Based on actual concrete strength and reinforcement details Factory develop safe loading plans for all floors, and submit to Accord for review. Factory will display load capacity plan on every floor and moreover each floor load plan will provide to floor manager . |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Structural System | Lateral stability system | On the 4th and the 5th floor of the building as there is no apparent lateral stability system, the slab consists of combination of flat slab and the beam slab combination. The floors below i.e. from Ground floor to 3rd floor are all moment resisting frame. | Building Engineer to review the design and check for the lateral stability for the 4th and 5th floor. | 6 months | Factory management will concern with building engineer for review the design and provide the stability reports. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Moisture ingress | This refers to the roof of the building where there are signs of water ingress from the roof. | Building Engineer to inspect the areas which is experiencing water leakage and propose measures to prevent further damage and carry out repair works. | 6 months | Building engineer will inspect the highlighted are and carry out repair work. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Other Damage/Defects | Moisture ingress | the water seems to be seeping out from the construction joint of OHWT on the roof causing lime leaching on the OHWT. | Building Engineer to inspect the areas which is experiencing water leakage and propose measures to prevent further damage and carry out repair works | 6 months | Building engineer will inspect the highlighted are and carry out repair work. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural Documentation | Documentation unavailable | The structural drawings from 1st floor to roof floor and the foundation drawings are not available | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | Factory will provide all the structural drawings. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Structural Documentation | Lack of safe load plans | No safe load plans posted in the factory. | Building Structural Engineer to produce loading plans for all floors within the factory considering floor capacity and column capacity. Loading to be actively managed by Factory Management. | 6 months | Factory will display load capacity plan on every floor and moreover each floor load plan will provide to floor manager . |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Other Damage/Defects | Health and Safety | The upper roof level of the building where there is no edge protection, the area is being used as accommodation/ sleeping area for the workers. | Provide appropriate edge protection to concerned areas. | 3 months | Factory has already installed edge protection and furthermore, no sleeping is allowed over there anymore as that was a temporary resting area for security guard. Factory will provide pictorial evidence to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Other Damage/Defects | Health and Safety | There is no safe access provided to access the upper roof level from the roof level. | Provide appropriate access to the upper roof by constructing a proper staircase or ladder with appropriate fall protection system. | 3 months | Factory will construct a proper MS staircase with fall protection system. |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1