## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
25-Jul-24
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | FASHION KNIT INDUSTRIES UNIT 1 & 2, Plot # C 30 Mangopir Road, S.I.T.E Karachi. Pakistan.
[9 empty] | Date of Initial Inspection | [12 empty] | 25-Jul-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. Install an A1-size laminated single line diagram of the electrical distribution system within the substation. Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. Keep an attendance record of each person and the date when they undertook the training, affix training record in A4 size inside the substation on a wall adjacent to the entry/exit door. | 3 months | Factory will ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. Moreover, facility will install an A1-size laminated single line diagram of the electrical distribution system within the substation. Facility will regularly update and review the substation layout drawings. Moreover factory will also provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. Furthermore, factory will also maintained the training record of the concern personnel in inside the substation. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | - It was found that the electrical single-line diagrams (SLDs) for the factory were missing. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. - The factory lacks documented diagrams illustrating the electrical distribution system, including the connection and configuration of all electrical components. | Develop comprehensive electrical single-line diagrams for the entire facility following the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. Install an A1-size laminated single line diagram of each main LT distribution board within the respective LT room. | E1 + 1 month | Factory will prepare electrical single-line diagrams for the overall site including the all requirements of Accord Pakistan. Facility will Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. Furthermore, factory will install an A1-size laminated single line diagram of each main LT distribution board within the respective LT room. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E3 | Diagrams & Drawings | Electrical layout drawing | - During the survey, it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. This absence was consistent across all areas where such documentation should be available. | Develop comprehensive electrical layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. Systems shall include but not be limited to the following for each floor to 1:100 scale on A1 sheet. | 8 months | Facility will develop electrical layout drawings separately for each electrical system. Moreover, facility will also retain the drawings along with all O&M information for the facility. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | - It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. At Lift DB-on Rooftop Building 1 circuit breaker, amend the cable/CB size for the load as per BS7671. At Knitting DB in Building 1, 2nd Floor, circuit breaker, amend the cable/CB size for the load as per BS7671. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current carrying capacity, submit a table/schedule for Accord review. If the breaker has adjustable settings, it must be configured to allow current within the cable ampacity after applying derating factors. | 3 months | Facility will evaluate the breaker ratings and cable sizes for all circuits in the site according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Moreover, facility ensure that the breaker rating does not exceed the cable current carrying capacity, submit a table/schedule for Accord review. If the breaker has adjustable settings, facility will configure to allow current within the cable ampacity after applying derating factors. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E5 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. 1. Building 1, 2nd Floor, New Knitting Department 70.3°C 2. Building 2, 1st Floor, Finishing 73.1°C 3. Building 2, 2nd Floor, Dyeing Lab 84.5°C 4. Building 2, Finished Fabric Storage 93.0°C 5. Building 2, 1st Floor, Reception 76.3°C 6. Building 2, 1st Floor, Office Lighting 73.6°C 7. Building 2, Ground Floor, Chemical Storage 69.6°C | Any circuits identified as category high must be immediately rectified. Where the cause or ratification requires investigation, the circuit shall be isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. Do not operate the circuit until the hotspot has been resolved. Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks. A thermographic report of the full installation should be kept on site, minimum frequency of reporting should be twice a year and any medium or high category items should be resolved accordingly. In the future, reports for the previous 3-years should always be available, in PDF or hardcopy. | 1 month | Factory will take immediate corrective action and rectify all high risk circuits on priority. Furthermore, facility will also conduct regular thermographic inspections according to the maintenance schedule to proactively manage and mitigate the risks. Facility will kept thermographic report of the full installation on site, setting minimum frequency of reporting by twice a year. |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E6 | DBs & Elec Protection Systems | Earthing system | - The reliable connectivity of earthing system from earth pits to LT panels, DBs, cable trays and end user machines was missing . - The bonding mechanism was not as per standard. Cable trays, distribution boards, inner sheets, metallic pipes, and metallic gates or cages were not provided with proper equipotential bonding. - Earthing and Neutral cables were observed to be interconnected in several distribution boards. - Multi-looping of earth cables was observed in multiple locations. | - Evaluate the earthing system installation throughout the facility. Confirm the earthing topology being employed by the Factory throughout the facility (TN-C, TN-S, TT, TN-C-S) - Propose a design for the earthing system and earth pits to make them easily accessible for testing, maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. - Prepare a dedicated SLD for Earth and Neutral for the full system including identification of earth pits, main earth bar, earth neutral connection, earth cable sizes, grounding/bonding of conductive parts (pipework, metallic frame, tapware) and the topology of the system shall be indicated on the SLD (TN-C, TN-S, TT, TN-C-S) - Prepare a comparison table of existing earth cable sizes and proposed earthing cables with appropriately sized cables as per the requirements of BS 7671 18th Edition + A2 (2022) Appendix 4, Section 5. - Present a program to replace all non-compliant earthing conductors to meet the minimum cross-sectional area specified by the Standard and rewire all earthing and neutral cabling to comply with the topology including wiring for equipotential bonding/grounding of all metallic/conductive materials. | 6 months | - Evaluate the earthing system installation throughout the facility. Confirm the earthing topology being employed by the Factory throughout the facility (TN-C, TN-S, TT, TN-C-S) - Propose a design for the earthing system and earth pits to make them easily accessible for testing, maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. - Prepare a dedicated SLD for Earth and Neutral for the full system including identification of earth pits, main earth bar, earth neutral connection, earth cable sizes, grounding/bonding of conductive parts (pipework, metallic frame, tapware) and the topology of the system shall be indicated on the SLD (TN-C, TN-S, TT, TN-C-S) - Prepare a comparison table of existing earth cable sizes and proposed earthing cables with appropriately sized cables as per the requirements of BS 7671 18th Edition + A2 (2022) Appendix 4, Section 5. - Present a program to replace all non-compliant earthing conductors to meet the minimum cross-sectional area specified by the Standard and rewire all earthing and neutral cabling to comply with the topology including wiring for equipotential bonding/grounding of all metallic/conductive materials. |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | - The reliable connectivity of earthing system from earth pits to LT panels, DBs, cable trays and end user machines was missing . - The bonding mechanism was not as per standard. Cable trays, distribution boards, inner sheets, metallic pipes, and metallic gates or cages were not provided with proper equipotential bonding. - Earthing and Neutral cables were observed to be interconnected in several distribution boards. - Multi-looping of earth cables was observed in multiple locations. | i. Disconnect unnecessary earth-neutral connections that are not aligned with the proposed earthing topology. ii. Install earthing systems as per the agreed topology and program, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. iii. Install equipotential bonding for all conductive metallic objects using appropriately sized cables to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. iv. Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. v. Document all inspections and maintenance activities to ensure ongoing compliance. vi. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. vii. Keep an attendance record of each person and the date when they undertook the training, affix training record in A4 size inside the LT room on a wall adjacent to the main earth bar position. | 6 months | Facility will take corrective action as per the below requirements of the Accord Pakistan. i. Disconnect unnecessary earth-neutral connections that are not aligned with the proposed earthing topology. ii. Install earthing systems as per the agreed topology and program, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. iii. Install equipotential bonding for all conductive metallic objects using appropriately sized cables to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. iv. Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. v. Document all inspections and maintenance activities to ensure ongoing compliance. vi. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. vii. Keep an attendance record of each person and the date when they undertook the training, affix training record in A4 size inside the LT room on a wall adjacent to the main earth bar position. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E8 | DBs & Elec Protection Systems | Panel/cabling/busbar | - In several external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. - Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. Location: Building 2 Spinning + Knitting - There were visible signs of damage to panels, cables, and busbars e.g., broken locks, non-operational ampere and volt meters. Location: All Buildings | Any panel that is in a public area should be key locked to prevent access to general public. Only facilities maintenance staff and authorized electricians should have the ability to open and operate circuit protection devices. | 1 month | Facility will take immediate corrective action and close all the opened electrical panel. Furthermore, facility will also provide training to staff and workers that only authorized personnel are allowed to open this panel. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Panel/cabling/busbar | - In several external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. | i. Identify electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed following Section 512.2 of BS 7671 18th Edition + A2 (2022). The typical requirements are as follows: a. All panels located in high moisture/humid environment should be minimum IPx4. b. All panels located in dusty environment should be minimum IP4x. c. All panels located in high moisture and dusty environment should be minimum IP44. d. All panels located in an egress path must have smoke seals around the panel doors. e. Panels may not be installed in unsafe locations such as above/under a sink, above/behind a door, on a stair, in an egress path (unless smoke seals are installed), in proximity to rotating machinery, in proximity to a worker station, in proximity to hazardous chemicals/gas. ii. Submit a program of the panels and equipment that need to be upgraded or replaced to the Accord for review. | 2 months | Facility will take corrective action and will install electrical components in the suitable environmental conditions as per the requirement of Accord Pakistan. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E10 | DBs & Elec Protection Systems | Panel/cabling/busbar | Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. There were visible signs of damage to panels, cables, and busbars e.g., broken locks, non-operational ampere and volt meters. | Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. Inspect and repair or replace all damaged panels, cables, and busbars to ensure the integrity of the electrical system following Section 522 of BS7671 18th Edition + A2 (2022) Establish a schedule for regular maintenance and inspection of the panel, cabling, and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | E9 + 3 months | Facility will take corrective action and repair all the broken locks, install ampere where required and volt meters. |  |  |  | In Progress
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Multiple Connections | - During the inspection, multi-looping was observed in several electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. Location: All Buildings | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each circuit following Section 430 of BS 7671 18th Edition + A2 (2022) | 3 months | Facility will inspect and clear all the multi-looping that was observed in electrical panels. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E12 | DBs & Elec Protection Systems | Openings | - Unsealed openings were discovered in the panels and distribution boards - The base plate in several electrical panels was missing. Location: All buildings | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). If using expansion foam product, only use non-flammable expansion foam. Submit the foam product manufacturer name, product model, serial number and product images to the Accord. | 3 months | Factory will take corrective actions and will sealed all openings and replace missing panels to restore the integrity and safety of the electrical systems. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Openings | - Unsealed openings were discovered in the panels and distribution boards - The base plate in several electrical panels was missing. Location: All buildings | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | 6 months | Factory will conduct regular maintenance of the panels and kept its record up to date. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Adequate accessibility | - At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. - In several instances, the placement of electrical panels adjacent to machines that continuously reject heat has caused the surrounding temperature to exceed ambient by several degrees. - In some instances, goods were stored directly adjacent to or in front of the distribution boards blocking clear access and creating an unsafe working environment. Location: Washing area | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). Guidance on the panel clearances is as following: • Clearance in front of panel beyond door swing zone: 600mm (2 feet) with the panel door in open position • Clearance in front of panels with dead front switchgear: 1000mm (3.3 feet/40 inch) • Clearance on side between two side-by-side panels: 50mm (2 inch) gap between two panels • Clearance behind panel with lift-off doors: 600mm (2 feet) • Clearance between a panel and any worker station: 1200mm (4 feet) • Clearance from any portable gas cylinder or gas vent: 1500mm (5 feet) • Clearance from fixed gas/fuel storage cylinder 3600mm (12 feet) | 1 month | Facility will take corrective action and will relocate all the electrical panel at the sufficient space. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Adequate accessibility | - At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. - In several instances, the placement of electrical panels adjacent to machines that continuously reject heat has caused the surrounding temperature to exceed ambient by several degrees. - In some instances, goods were stored directly adjacent to or in front of the distribution boards blocking clear access and creating an unsafe working environment. | Develop a periodic maintenance program to ensure that each distribution panel has adequate space. Remove all storage material from the panel clearance zones at all times. | 3 months | Facility will take corrective action and will maintain regular basis checklist to cross verify the availability of sufficient space at electrical panel and storage material should be kept away from the panels. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Lint & dust inside panel board | - The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022) A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 1 month | Facility will instruct cleaning staff to clean all the electrical panel immediately and make sure that it will be cleaned on regular basis. Furthermore, factory will also obtain a procedure for maintenance and ensure the implementation of it. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | - No lightning protection system was installed, and there was no risk assessment provided to confirm if it was not required. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. In addition, consider installation of surge protection devices (SPD) at all main LT panels and sensitive distribution boards supply power such as UPS units, telecommunications. Submit assessment and a program for the implementation (if applicable) to the Pakistan Accord. | 2 months | Facility will conduct comprehensive risk assessment to check the lightning protection system and submit the assessment report to Accord Pakistan for review and approval. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E18 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | - No lightning protection system was installed, and there was no risk assessment provided to confirm if it was not required. | If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). A dedicated SLD shall be included for the Lightning Protection System including maximum building height, maximum height of objects (antenna tower, water tanks, solar PV, lift motor room, cooling towers etc.) above the roof level, height of the lightning arrestor rod, size of cable from arrestor to the pit or details of connection to building structure, proof of continuity/resistance test between roof structure connection and earth pit. | 6 months | Facility will re-conduct risk assessment and will check the needs of LPS and will proceed with requirement of an appropriate system in compliance with relevant standard. |  |  |  | In Progress
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - Fire Alarm and Detection System was non listed, non-functional, inappropriate detection and MCP coverage, faulty detectors low audibility in different areas, non-functional detectors etc. and does not comply with NFPA72. | Ensure the functionality and performance of the existing alarm and detection system within the building. | 1 month | Facility will take corrective action and will ensure the functionality and performance of the existing alarm and detection system within the building. |  |  |  | In Progress
No | 3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - Fire Alarm and Detection System was non listed, non-functional, inappropriate detection and MCP coverage, faulty detectors low audibility in different areas, non-functional detectors etc. and does not comply with NFPA72. | i. Submit design documentation for new FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | Facility will submit the documentation for new design of FADS system to Accord Pakistan before going to purchase. |  |  |  | In Progress
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - Fire Alarm and Detection System was non listed, non-functional, inappropriate detection and MCP coverage, faulty detectors low audibility in different areas, non-functional detectors etc. and does not comply with NFPA72. | i. Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E20 + 1 month | Documentation of L/C opening showing import of components are opened will submit to Accord Pakistan for review. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - Fire Alarm and Detection System was non listed, non-functional, inappropriate detection and MCP coverage, faulty detectors low audibility in different areas, non-functional detectors etc. and does not comply with NFPA72. | ii. Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E21 + 4 months | Facility will submit documentation of listed FADS system to Accord Pakistan for review. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - Fire Alarm and Detection System was non listed, non-functional, inappropriate detection and MCP coverage, faulty detectors low audibility in different areas, non-functional detectors etc. and does not comply with NFPA72. | iii. Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E22 + 5 months | After installation of FADS system, facility will submit the 'as-built' documentation of the system to Accord for review. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - Fire Alarm and Detection System was non listed, non-functional, inappropriate detection and MCP coverage, faulty detectors low audibility in different areas, non-functional detectors etc. and does not comply with NFPA72. | iv. Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E23 + 3 months | Facility will install FADS listed and after completion will report to Accord Pakistan for review. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - Fire Alarm and Detection System was non listed, non-functional, inappropriate detection and MCP coverage, faulty detectors low audibility in different areas, non-functional detectors etc. and does not comply with NFPA72. | v. Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | E24 + 3 months | Facility will take corrective action and will do testing and commissioning (T&C) certification. Moreover, after completion of the certification facility will inform Accord Pakistan for review. Facility will also maintain the FADS system and maintain its records on site. |  |  |  | In Progress
No | 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Emergency Lighting | No emergency lighting | - During the inspection, it was observed that emergency lighting and illuminated exit signage was not installed at many locations within the facility. | To address the lack of emergency lighting in the facility, emergency lighting systems should be designed and installed following the Building Code of Pakistan Fire Safety Provisions 2016. This includes ensuring proper placement in all egress routes and compliance with specified standards for illumination and battery backup. General guidance on emergency and exit lights: Emergency and exit illuminate signage should be installed to provide coverage in all areas, in all egress pathways, at all doors on an egress pathway, at all perimeters doors leading to an outdoor egress area, at all change in level (stairs, ramps), at all intersections in an egress pathway, in each aisle in a storage or racking area. Emergency lighting should not cause blinding glare into the eyes of people using the egress pathway or doors. Illuminated exit signage and non-illuminated exit signage are not equal. All non-illuminated exit signs must have an emergency light mounted nearby to shine light onto the exit sign. | 3 months | Facility will take immediate corrective action and install emergency lighting and illuminated exit signage where required. Furthermore, facility will also made checklist on regular basis to cross verify the availability of the lights. |  |  |  | In Progress
No | 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Cabling & Wiring | No emergency lighting | - During the inspection, it was observed that emergency lighting and illuminated exit signage was not installed at many locations within the facility. | Maintain comprehensive records of all installations, tests, and maintenance activities. Train facility personnel on the operation and maintenance of emergency lighting systems to ensure prompt identification and resolution of any issues. | 3 months | Factory will start maintaining comprehensive records of all installations, tests, and maintenance activities. Train facility personnel on the operation and maintenance of emergency lighting systems to ensure prompt identification and resolution of any issues. |  |  |  | In Progress
No | 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Generator, Transformer & Sub-Station Room | Battery | - Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. Develop a periodic maintenance program to ensure every battery in the facility is installed properly with clean terminals and proper cable termination. Record battery voltage level and discharge test every 6 months. Replace batteries as necessary. | 2 months | Facility will take corrective action and will insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. moreover facility will develop a periodic maintenance program to ensure every battery in the facility is installed properly with clean terminals and proper cable termination. Record battery voltage level and discharge test every 6 months. Replace batteries as necessary. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E29 | Cabling & Wiring | Cables support and protection | - Proper supports were not provided for cables; they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. Inadequate cable support results in sagging or stress on cables, which can lead to damage or failure. - Numerous loose connections were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections and the practice of inserting exposed wires directly into sockets to prevent electrical hazards. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices | 3 months | Facility will take corrective action and will secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). Moreover, Facility will implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices. |  |  |  | In Progress
No | 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Cable trench and channel cleanliness | - Numerous trunking systems were found to be filled with a significant amount of lint and dust, which poses a serious fire risk. - It was also found that trench covers were missing or did not adequately withstand the weight of personal. | Clean all cable trunking and trench systems to remove accumulated rubbish, water, dust and lint, ensuring that any potential fire hazards are mitigated. Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 3 months | Facility will take corrective action and clean all cable trunking and trench systems to remove accumulated rubbish, water, dust and lint, ensuring that any potential fire hazards are mitigated. Moreover, facility will Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. |  |  |  | In Progress
No | 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Cabling & Wiring | Splicing of cables | - Cables terminations within panels and switchgear were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. | Install cable lugs on all improperly terminated cables within panels and switchgear to secure connections and prevent breaking strands and loose connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | Facility will Install cable lugs on all improperly terminated cables within panels and switchgear to secure connections and prevent breaking strands and loose connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Cabling & Wiring | Splicing of cables | - PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. Use appropriate cable lugs when terminating cabling into MCCB, bus bar, earth bar or neutral bar). | 6 months | Facility will replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). Furthermore, facility will also replace all damaged cabling with new wiring & use appropriate cable lugs when terminating cabling into MCCB, bus bar, earth bar or neutral bar). |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E33 | Cabling & Wiring | Splicing of cables | - Cables terminations within panels and switchgear were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 4 months | Facility will Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. |  |  |  | In Progress
No | 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Cabling & Wiring | Splicing of cables | - PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance and provide continuous training for staff on proper jointing techniques. Provide cable soldering training and equipment to staff along with heat shrink sleeves in lieu of PVC tape joints. | 6 months | Facility will establish a policy prohibiting the use of PVC tape for electrical jointing. Moreover facility will also regularly inspect and maintain electrical installations to ensure compliance and provide continuous training for staff on proper jointing techniques. Factory will also provide cable soldering training and equipment to staff along with heat shrink sleeves in lieu of PVC tape joints. |  |  |  | In Progress
No | 3 | 8 |  | 168 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable color coding practices were identified, posing significant risks of misinterpretation and misidentification of cables. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. Colour coding should be consistent throughout the facility. Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | 2 months | Facility will conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This will involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. Colour coding should be consistent throughout the facility. Furthermore, factory will develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. Moreover, facility will also provide training sessions to the concern personnel on regular basis. |  |  |  | In Progress
No | 3 | 8 |  | 172 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Cabling & Wiring | Fixtures | During the inspection, the electrical fixtures throughout the facility were visually surveyed, revealing several damaged power sockets, LED lights, and switchboards, with many LED lights found hanging by their power cables, posing a risk of cable damage. | Install appropriate mounting hardware to securely hang LED lights/power outlets and prevent cable damage. Replace or repair broken and exposed power sockets immediately to restore safe and secure connections. Install caps on junction boxes. Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed. Develop installation guidelines and training for personnel to ensure future power receptacles are installed in compliant and safe locations. | 3 months | Facility will Install appropriate mounting hardware to securely hang LED lights/power outlets and prevent cable damage. Factory will replace or repair broken and exposed power sockets immediately to restore safe and secure connections. Install caps on junction boxes. Furthermore, factory will also Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed and develop installation guidelines and training for personnel to ensure future power receptacles are installed in compliant and safe locations. |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
25-Jul-2024
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [12 empty] | Fashion Knit Industries Unit 1 & 2, C-30, S.I.T.E., Manghopir Road, Moin Akhtar Road, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 25-Jul-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Protection of stairs | Fire load in stairs such as building 1+3 level 1 | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | Facility have immediately cleared the obstructions from stairs. | Done |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Protection of stairs | Unprotected openings into stairs such as unprotected & open Stair at Building 1+3 level 6, Unprotected openings exposing exterior exit stairway at Building 1+3 level 4 & 5. Unprotected penetrations into stairs such as emergency exit stair Building 1+3 level 4 & 5, Services are passing through cotton pipes at Building 2 level 1 stair, some pipes at stair Building 1+3 level 2 yarn area, Building 1+3 ground floor exit blocked due to gas lines Doors do not fire doors such as building 1+3 ground floor to level 5 | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect the stairs. Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | Factory will made drawing through third party consultant as per the requirement of accord and will submit it to accord for approval. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Protection of stairs | Unprotected openings into stairs such as unprotected & open Stair at Building 1+3 level 6, Unprotected openings exposing exterior exit stairway at Building 1+3 level 4 & 5. Unprotected penetrations into stairs such as emergency exit stair Building 1+3 level 4 & 5, Services are passing through cotton pipes at Building 2 level 1 stair, some pipes at stair Building 1+3 level 2 yarn area, Building 1+3 ground floor exit blocked due to gas lines Doors do not fire doors such as building 1+3 ground floor to level 5 | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: All doors into stairs should be fire resisting doors with self-closing mechanisms. Doors into stairs should be kept closed (but not locked) at all times. Increase clear height under doorway to 6 ft 8 in (2050 mm) or provide alternative escape route. Stair railing height should be adequate enough to protect fall during emergency evacuations. Spiral stair shall replace or provide alternate exit route. | F2 + 4 months | Factory will make separate fire rate construction at stairs with fire doors. Moreover, factory will also make sure about the below points; Installation of self-closing mechanism on fire resisting door at stairs. No looking mechanism will be there at doors and the doors should kept closed all time at stairs. Height of doors will be increased according to the standard. Stairs railing height should also be increased according to the requirement Spiral stairs will be dismantle and alternative route will be provided |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Number of exits | There is only a single exit from site and there is a risk it may not be available in the event of fire in the building. Single exit from factory premises and the width is insufficient and more diverse exits are needed. Single exit from some of the occupied floors such as 1 exit at mezzanine Building 1+3, 1 exit at Building 1+3 basement. There are areas with over 50 occupants that are served by only 1 exit such as 1 exit at Canteen Building 1+3 level 2, 01 exit for Building 1+3 & 2 passageway. | Review each floor and area to ensure that the number of exits complies with Pakistan Accord Building Standard, including the exit from the premises as there is no emergency muster area on site. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | Factory will provide one or more emergency exits were required as per the requirement of the accord standard. Furthermore, factory will also make plan for additional exits where necessary and submit it to the accord for approval and rectification. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Number of exits | There is only a single exit from site and there is a risk it may not be available in the event of fire in the building. Single exit from factory premises and the width is insufficient and more diverse exits are needed. Single exit from some of the occupied floors such as 1 exit at mezzanine Building 1+3, 1 exit at Building 1+3 basement. There are areas with over 50 occupants that are served by only 1 exit such as 1 exit at Canteen Building 1+3 level 2, 01 exit for Building 1+3 & 2 passageway. | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Building Standard. | F4 + 4 months | After approval of the above plan for exits, factory will implement it accordingly. Moreover, factory will also make sure for the availability of adequate number of exits as per the accord standard. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits Common path has been measured as 85m approx. at building 1+3 Knitting 1 Common path has been measured as 81m approx. at building 1+3 Knitting 2 Common path has been measured as 60m approx. at building 1+3 Roof Common path has been measured as 46m approx. at building 1+3 level 5 | Areas with a single direction travel distance > 45m should be vacated until another exit route can be provided. Train fire wardens. Have more regular evacuation drills. | 2 weeks | Factory will manage the travel distance of escape route as per the requirement of accord standard. Moreover, facility already training the fireman's and conducting fire evacuation drill by the third party. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits Common path has been measured as 25m approx. at building 1+3 Canteen level 2 Common path has been measured as 34m approx. at building 1+3 level 2 Common path has been measured as 32m approx. at building 1+3 level 6 Common path has been measured as 27m approx. at building 2 level 2 Common path has been measured as 29m approx. at building 2 Ground floor Common path has been measured as 37m approx. at building 1+3 Basement Common path has been measured as 44m approx. at building 2 level 2 Common path has been measured as 85m approx. at building 1+3 Knitting 1 Common path has been measured as 81m approx. at building 1+3 Knitting 2 Common path has been measured as 60m approx. at building 1+3 Roof Common path has been measured as 46m approx. at building 1+3 level 5 | Propose a plan for addressing the excessive common path & travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review common paths & travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | Factory will propose a plan for addressing the excessive common path & travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review. Moreover, factory will also review common paths and travel distances from all areas in the building to ensure that they meet the accord standard. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Travel distance | Common path of travel distances exceed permitted limits Common path has been measured as 25m approx. at building 1+3 Canteen level 2 Common path has been measured as 34m approx. at building 1+3 level 2 Common path has been measured as 32m approx. at building 1+3 level 6 Common path has been measured as 27m approx. at building 2 level 2 Common path has been measured as 29m approx. at building 2 Ground floor Common path has been measured as 37m approx. at building 1+3 Basement Common path has been measured as 44m approx. at building 2 level 2 Common path has been measured as 85m approx. at building 1+3 Knitting 1 Common path has been measured as 81m approx. at building 1+3 Knitting 2 Common path has been measured as 60m approx. at building 1+3 Roof Common path has been measured as 46m approx. at building 1+3 level 5 | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F7 + 4 months | Facility will submit the plan to accord for prior approval and will implement the plan once get approved. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit access | Insufficient headroom along escape route (i.e. headroom height is less than 2.05m) (Head room clearance is 1.7 meters at Building 1+3 level 1) | Provide warning signs where headroom height is less than 2.05 m on escape routes. | 2 weeks | Facility have taken immediate corrective action and have pasted warning signs of lower height where required. | Done |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | The interior exit only stairway S-6 from Building 1+3 level 5 discharges internally, into level 4 Both stairs from Office & workshop Building 1+3 mezzanine discharges internally, into ground floor The interior exit only stairway S-5 from Building 1+3 level 2 discharges internally, into level 1 Offices at mezzanine Building 1+3 spiral stair discharge within building Stair S-2 Building 2 discharges internally at Ground Floor level Insufficient headroom along escape route (i.e. headroom height is less than 2.05m). Head room clearance was observed 1.7 meters at Building 1+3 level 1 Electrical DB in the escape route from the canteen of Building 1+3 level 2 Escape passing through increased risk area on way to exit. Canteen “250 occupancy” one exit passes through storage area Building 2 level 2 | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect stair discharge corridors Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply. Submit the proposal to Pakistan Accord for review. | 4 months | Facility will submit the drawing as per the requirement of accord standard consisting of the below things; Layout showing the location of fire rated walls and doors to protect stairs. Details of proposed fire rated walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) Propose modifications to ensure 2.05m headroom height is achieved along the escape routes or propose alternative egress routes that comply and will submit the proposal to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | The interior exit only stairway S-6 from Building 1+3 level 5 discharges internally, into level 4 Both stairs from Office & workshop Building 1+3 mezzanine discharges internally, into ground floor The interior exit only stairway S-5 from Building 1+3 level 2 discharges internally, into level 1 Offices at mezzanine Building 1+3 spiral stair discharge within building Stair S-2 Building 2 discharges internally at Ground Floor level Insufficient headroom along escape route (i.e. headroom height is less than 2.05m). Head room clearance was observed 1.7 meters at Building 1+3 level 1 Electrical DB in the escape route from the canteen of Building 1+3 level 2 Escape passing through increased risk area on way to exit. Canteen “250 occupancy” one exit passes through storage area Building 2 level 2 | Ensure discharge routes / corridors are adequately fire separated from the rest of the Building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. Implement measures to ensure adequate clear head height is achieved along all escape routes. | F10 + 4 months | Factory will ensure discharge routes are fire separated from the rest of the building and will prepare the design according to the accord standard. The submitted plan will include following requirements: All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. Implement measures to ensure adequate clear head height is achieved along all escape routes. |  |  |  | In Progress
No | 3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Escape doors | Escape doors are lockable. It was observed throughout examples Building 1+3 level 2, In-between Building 1 and 2, workers found inside the locked door Thread Storage area Building 2 ground floor, Building 4 ground floor. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 2 weeks | Factory has removed all non-compliant locking features from doors on all egress paths as per the Accord standard. | Done |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Escape doors | Escape doors are lockable. It was observed throughout examples Building 1+3 level 2, In-between Building 1 and 2, workers found inside the locked door Thread Storage area Building 2 ground floor, Building 4 ground floor. Doors into stairs swing against the direction of escape such as door swings inward Building 4 ground floor Sliding doors serve for escape from areas with more than 10 occupants such as building 1+3 level 1, Roof & Basement, Blower room Building 1+3 level 1, Mezzanine Building 1 | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, which are side swinging and open in the direction of travel to an exit. | 3 months | Facility will provide easy opening mechanism according to the standard and escape door will be open toward direction of escape route. Furthermore, facility will replace sliding door with the swing door which will be open towards direction of travel. |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Escape doors | Escape doors are lockable. It was observed throughout examples Building 1+3 level 2, In-between Building 1 and 2, workers found inside the locked door Thread Storage area Building 2 ground floor, Building 4 ground floor | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F13 + 3 months | Factory has removed all locking devices from the door. | Done |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Escape stair condition | Handrails are too low such as stair railing height is low at Building 1+3 level 5 stairs S-6 | Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. | 3 months | Facility will install handrails on both sides of each stairs with appropriate height. |  |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit discharge | External escape routes are obstructed from external routes from stairs S-1 and S-9 | Remove obstructions on external escape routes and keep them clear for escape. | 2 weeks | Facility has removed obstructions on external escape routes and keep them clear for escape. | Done |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit discharge | External escape routes are obstructed from external routes from stairs S-1 and S-9 | Prepare drawings showing proposed fire separating construction to exit discharge routes if needed. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: Layout showing the location of fire rated walls/doors to protect stair discharge routes Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes | 4 months | Factory will prepare drawings showing proposed fire separating construction to exit discharge routes if needed. These will be submitted to Accord for review and approval prior to commencing rectification works. The drawings will cover: Layout showing the location of fire rated walls/doors to protect stair discharge routes Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes |  |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit discharge | External escape routes are obstructed from external routes from stairs S-1 and S-9 | Ensure external exit discharge routes are adequately fire separated from the rest of the Building. Ensure external escape routes do not pass close to unprotected high-risk areas | F17 + 4 months | Factory will ensure external escape routes do not pass close to unprotected high-risk areas |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit signage | Missing exit signs at entry into stairs. All Buildings e.g.: Building 1+3 exit stairs level 2 & 3. Missing exit signs at stair discharge routes. All Buildings e.g.: Building 2 basement. Missing exit signs in production areas. All Buildings e.g.: Building 1+3 level 2, Building 1+3 ground floor to level 6, Building 1+3 level 1. Electrically powered exit signs are not a tested and listed system Electrically powered exit signs indicate battery problems | Provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 4 months | Factory has Installed exit signages at all required areas as per the requirement of Accord. | Done |  |  | In Progress
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Exit signage | Missing exit signs at entry into stairs. All Buildings e.g.: Building 1+3 exit stairs level 2 & 3. Missing exit signs at stair discharge routes. All Buildings e.g.: Building 2 basement. Missing exit signs in production areas. All Buildings e.g.: Building 1+3 level 2, Building 1+3 ground floor to level 6, Building 1+3 level 1. Electrically powered exit signs are not a tested and listed system Electrically powered exit signs indicate battery problems | Ensure that all exit signage is checked periodically and in good working condition. | F19 + 4 months | Factory has Installed exit signages at all required areas as per the requirement of Accord. | Done |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building such as Grey fabric storage area Building level 2, Finishing Building 2 level 1, Dyeing area Building 2 ground floor, Excessive fabric stored at Building 2 level 1 production, Building 2 basement, Knitting area Building 2, storage area to finishing at Building 2 level 1. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will identify all designated storage areas for fire separation and limited storage. Facility will also made drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. Drawings will cover details e.g. listing, fire, rating period, self-closers, door opening direction. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building such as Grey fabric storage area Building level 2, Finishing Building 2 level 1, Dyeing area Building 2 ground floor, Excessive fabric stored at Building 2 level 1 production, Building 2 basement, Knitting area Building 2, storage area to finishing at Building 2 level 1. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F21 + 4 months | Factory will ensure that the above plan is implemented and following the requirements of accord standard. |  |  |  | In Progress
No | 3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction. All Lift shafts e.g.: Building 1+3 ground floor to level 6, Building 4, Lift shaft openings at Building 2 level 1. Openings in walls enclosing the shaft such as opening around fire hydrant Building 1+3 level 1 S-5. Duct shafts are not fire separated such as service duct at Building 1+3 level 1. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors enclosing vertical shafts. Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of fire rated walls and doors enclosing vertical shafts. Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) |  |  |  | In Progress
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Separation of shafts | Lift shafts are not separated with fire rated construction. All Lift shafts e.g.: Building 1+3 ground floor to level 6, Building 4, Lift shaft openings at Building 2 level 1. Openings in walls enclosing the shaft such as opening around fire hydrant Building 1+3 level 1 S-5. Duct shafts are not fire separated such as service duct at Building 1+3 level 1. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F23 + 4 months | Factory will Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Separation of occupancies | Basement is not fire separated from the rest of the building such as building 1+3 basement. Storage area and workshop mezzanine Building 1+3 is not fire separated. Canteen & food processing/ cooking area at Building 2 level 2 is not fire separated | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building Proposed fire separation details (including fire rating of walls and doors) | 4 months | Factory will prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building, Proposed fire separation details (including fire rating of walls and doors) |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Rated Construction | Separation of occupancies | Basement is not fire separated from the rest of the building such as building 1+3 basement. Storage area and workshop mezzanine Building 1+3 is not fire separated. Canteen & food processing/ cooking area at Building 2 level 2 is not fire separated. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F25 + 4 months | Facility will provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building. Fire Pumps are not separated from LPG Vessels & unprotected openings. Electrical rooms are not fire separated such as building 1+3 ground floor, Building 4, Power generation room Building 2. Boiler area is not fire separated such as building 1+3 level 1. Mechanical plant areas are not fire separated such as cooling room Building 1+3 level 1 & 2, Cooling room Building 2 level 1. Workshop is not fire separated such as building 1+3 level 2, Storage & Workshop at Building 1+3 Mezzanine. Compressed air vessel is not separated in building 1+3 level 2. Generator room is not separated in building 2 ground floor. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | Factory will prepare drawings showing the proposed fire separation details of increased fire hazard areas. Although facility will also submit this proposed design which including the following; Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building. Fire Pumps are not separated from LPG Vessels & unprotected openings. Electrical rooms are not fire separated such as building 1+3 ground floor, Building 4, Power generation room Building 2. Boiler area is not fire separated such as building 1+3 level 1. Mechanical plant areas are not fire separated such as cooling room Building 1+3 level 1 & 2, Cooling room Building 2 level 1. Workshop is not fire separated such as building 1+3 level 2, Storage & Workshop at Building 1+3 Mezzanine. Compressed air vessel is not separated in building 1+3 level 2. Generator room is not separated in building 2 ground floor. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F27 + 4 months | Facility will do 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Floor openings | Openings linking different levels are not fire separated such as building 2 level 2 to level 3 Finishing Production. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of floor openings Proposed fire separation details (including fire rating of walls and doors) | 4 months | Facility will prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of floor openings Proposed fire separation details (including fire rating of walls and doors) |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Floor openings | Openings linking different levels are not fire separated such as building 2 level 2 to level 3 Finishing Production. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F29 + 4 months | Facility will provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Hazardous Materials | Chemicals storage | Chemicals stored at Building 1+3 roof. Chemical store at Building 2 ground floor & Building 4 is not fire separated. Chemical store at Building 2 require fire separation from both sides as fabric storage area is located at one side and packing material stored other side. Gas storage areas are not fire separated from the rest of the building. LPG vessels are stored in fire pump room. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Locations of all chemical & gas storage areas Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) Ventilation provisions to each of these rooms | 3 months | Factory will collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Moreover, facility will also prepare drawings showing the proposed chemical storage areas that including the following; Locations of all chemical & gas storage areas Locations of fire rated walls and doors to protect these rooms Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) Ventilation provisions to each of these rooms Factory will also submit the proposed designed with the accord for prior approval. |  |  |  | In Progress
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Hazardous Materials | Chemicals storage | Chemicals stored at Building 1+3 roof. Chemical store at Building 2 ground floor & Building 4 is not fire separated. Chemical store at Building 2 require fire separation from both sides as fabric storage area is located at one side and packing material stored other side. Gas storage areas are not fire separated from the rest of the building. LPG vessels are stored in fire pump room. | Implement the above plan on site. All chemical & gas storage areas to be compliant with Accord Standard. | F31 + 3 months | Facility will implement the above plan accordingly and will also monitor it to ensure the 100% implementation. |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Suppression | Sprinkler system | Sprinkler system is not provided at Building 1+3- height 30.5 meters and Building 4- height 24.3 meters | (1) Submit design documentation for a sprinkler system [along with required standpipe system] and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | Facility will Submit design documentation for a sprinkler system [along with required standpipe system] and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Facility will also design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. |  |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Suppression | Sprinkler system | Sprinkler system is not provided at Building 1+3- height 30.5 meters and Building 4- height 24.3 meters | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F33 + 1 month | Facility will submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. |  |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Suppression | Sprinkler system | Sprinkler system is not provided at Building 1+3- height 30.5 meters and Building 4- height 24.3 meters | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F34 + 3 months | Facility Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. |  |  |  | In Progress
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Suppression | Sprinkler system | Sprinkler system is not provided at Building 1+3- height 30.5 meters and Building 4- height 24.3 meters | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F35 + 3 months | After the installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Suppression | Sprinkler system | Sprinkler system is not provided at Building 1+3- height 30.5 meters and Building 4- height 24.3 meters | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F36 + 3 months | Factory will inform Pakistan Accord when SUPS installation fully completed and fully functional so than Accord may come for verification. |  |  |  | In Progress
No | 3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Suppression | Sprinkler system | Sprinkler system is not provided at Building 1+3- height 30.5 meters and Building 4- height 24.3 meters | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F37 + 4 months = 18 months | Facility will provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete |  |  |  | In Progress
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Suppression | Fire pumps | Fire pump set is not listed There is no jockey pump Fire pumps do not start automatically & can be operated only on manual mode. Electric-driven fire pump shaft guard is not intact, posing a risk of entanglement | Provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following steps (1) to (6) above. | 18 months | Facility will Provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system by following steps (1) to (6) above. |  |  |  | In Progress
No | 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Fire Suppression | Water supply | No separate fire water tank. 03 underground common tanks for domestic & for fire water with capacities as 105, 55 & 35 Imperial gallons, 02 overhead water tanks at Building 1 85590 US gallons & Building 4. | Review arrangement of water supply and storage requirements to cover fire water supply as part of supporting infrastructure for the SUPS system, in accordance with NFPA 22 & 24, and submit to Accord for review. | 4 months | Facility will review arrangement of water supply and storage requirements to cover fire water supply as part of supporting infrastructure for the SUPS system, in accordance with NFPA 22 & 24, and submit to Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Fire Suppression | Water supply | No separate fire water tank. 03 underground common tanks for domestic & for fire water with capacities as 105, 55 & 35 Imperial gallons, 02 overhead water tanks at Building 1 85590 US gallons & Building 4. | Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system. | 18 months | Facility will provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system. |  |  |  | In Progress
No | 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs such as in buildings 1+3 & 2. Standpipe system infrastructure is not installed at Building 4. | Replace any damaged equipment and ensure current system is fully operational. | 1 month | Facility will replace any damaged equipment and ensure current system is fully operational. |  |  |  | In Progress
No | 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F43 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs such as in buildings 1+3 & 2. Standpipe system infrastructure is not installed at Building 4. | Provide the design for a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system by following steps (1) to (6) above. | 18 months | Facility will provide the design for a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14. |  |  |  | In Progress
No | 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F44 | Fire Suppression | Fire extinguishers | Incorrect type of extinguishers in kitchen areas. K-type fire extinguishers are not available at cooking area Building 2 level 2. | Ensure that all Building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 4 months | Facility will ensure that all Building areas are protected using fire extinguishers. The coverage and type of extinguishers used should follow NFPA 10. | 2025-06-01 |  |  | In Progress
No | 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F45 | Fire Suppression | Fire extinguishers | Incorrect type of extinguishers in kitchen areas. K-type fire extinguishers are not available at cooking area Building 2 level 2. | Monitor fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | F44 + 4 months | Facility will monitor placement fire extinguishers for coverage and extinguisher type to comply with NFPA 10. | 2025-06-01 |  |  | In Progress
No | 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F46 | Fire Safety Management | Fire drills | Not all staff are involved in fire drills such as 9th March, 2024 11:00 PM evacuation drill was conducted by all department with head count: 278, 9th March, 2024 11:00 AM evacuation drill was conducted by spinning department with head count: 110. | Conduct a fire drill and make records, including findings and recommended future improvements. Ensure involvement of all staff in evacuation drills. | 2 months | Facility will Conduct a fire drill and make records, including findings and recommended future improvements. Moreover factory will also ensure involvement of all staff in evacuation drills. |  |  |  | In Progress
No | 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F47 | Fire Safety Management | Fire drills | Not all staff are involved in fire drills such as 9th March, 2024 11:00 PM evacuation drill was conducted by all department with head count: 278, 9th March, 2024 11:00 AM evacuation drill was conducted by spinning department with head count: 110. | Ensure fire drills are performed a minimum 2 times per year. | F46 + 2 months | Facility will Ensure fire drills are performed a minimum 2 times per year. |  |  |  | In Progress
No | 3 | 8 |  | 157 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F48 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Standpipes Inadequate records of maintenance of Emergency lighting Inadequate records of maintenance of Fire Extinguishers Inadequate records of maintenance of Fire Doors | Prepare maintenance schedule for all life safety systems. | 3 months | facility will Prepare maintenance schedule for all life safety systems. |  |  |  | In Progress
No | 3 | 8 |  | 158 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F49 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Standpipes Inadequate records of maintenance of Emergency lighting Inadequate records of maintenance of Fire Extinguishers Inadequate records of maintenance of Fire Doors | Prepare a schedule of proposed system maintenance. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | Factory will prepare a schedule of proposed system maintenance Identify how systems will be maintained and designate the responsible personnel. Facility will also submit the proposed schedule to accord for review and approval. |  |  |  | In Progress
No | 3 | 8 |  | 159 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F50 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System Inadequate records of maintenance of Fire Pumps Inadequate records of maintenance of Standpipes Inadequate records of maintenance of Emergency lighting Inadequate records of maintenance of Fire Extinguishers Inadequate records of maintenance of Fire Doors | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep maintenance records. | F49 + 3 months | Facility will ensure all systems are being maintained as per the schedule agreed with Accord. Facility will also keep maintenance records. |  |  |  | In Progress
No | 3 | 8 |  | 160 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F51 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Detection and Alarm System Inadequate records of testing of Fire Pumps Inadequate records of testing of Standpipes Inadequate records of testing of Emergency lighting Inadequate records of testing of Fire Extinguishers Inadequate records of testing of Fire Doors | Prepare testing schedule for all life safety systems. | 3 months | Facility will Prepare testing schedule for all life safety systems and implement it accordingly. |  |  |  | In Progress
No | 3 | 8 |  | 161 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F52 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Detection and Alarm System Inadequate records of testing of Fire Pumps Inadequate records of testing of Standpipes Inadequate records of testing of Emergency lighting Inadequate records of testing of Fire Extinguishers Inadequate records of testing of Fire Doors | Prepare a schedule of proposed system testing. Identify how systems will be tested and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | Facility will Prepare a schedule of proposed system testing. Identify how systems will be tested and designate the responsible personnel The proposed schedule will be submit to accord for prior approval. |  |  |  | In Progress
No | 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F53 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Detection and Alarm System Inadequate records of testing of Fire Pumps Inadequate records of testing of Standpipes Inadequate records of testing of Emergency lighting Inadequate records of testing of Fire Extinguishers Inadequate records of testing of Fire Doors | Ensure all systems are being tested as per the schedule agreed with Accord Keep testing records. | F52 + 3 months | Facility will ensure that all systems are being tested as per the schedule agreed with Accord |  |  |  | In Progress
No | 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F54 | Fire Safety Management | Emergency Action Plan | EAP document does not describe the roles and responsibilities of key individuals in the event of fire. Evacuation Plans are observed missing at Building 3 & 4 all levels and Building 1 & 2 multiple locations. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan by incorporating roles & responsibilities of key individuals in the event of fire. | 2 months | Factory will Ensure that evacuation plans are provided on each level. Furthermore factory will also prepare an Emergency Action Plan by incorporating roles & responsibilities of key individuals in the event of fire. | 2025-06-01 |  |  | In Progress
No | 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F55 | Fire Safety Management | Emergency Action Plan | EAP document does not describe the roles and responsibilities of key individuals in the event of fire. Evacuation Plans are observed missing at Building 3 & 4 all levels and Building 1 & 2 multiple locations. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F54 + 2 month | Facility will ensure that emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | 2025-06-01 |  |  | In Progress
No | 3 | 8 |  | 165 | 421 | 6 | 5
No | 3 | 8 |  | 166 | 421 | 6 | 5
No | 3 | 8 |  | 167 | 421 | 6 | 5
No | 3 | 8 |  | 168 | 421 | 6 | 5
No | 3 | 8 |  | 169 | 421 | 6 | 5
No | 3 | 8 |  | 170 | 421 | 6 | 5
No | 3 | 8 |  | 171 | 421 | 6 | 5
No | 3 | 8 |  | 172 | 421 | 6 | 5
No | 3 | 8 |  | 173 | 421 | 6 | 5
No | 3 | 8 |  | 174 | 421 | 6 | 5
No | 3 | 8 |  | 175 | 421 | 6 | 5
No | 3 | 8 |  | 176 | 421 | 6 | 5
No | 3 | 8 |  | 177 | 421 | 6 | 5
No | 3 | 8 |  | 314 | 421 | 6 | 5
No | 3 | 8 |  | 315 | 421 | 6 | 5
No | 3 | 8 |  | 346 | 421 | 6 | 5
No | 3 | 8 |  | 349 | 421 | 6 | 5
No | 3 | 8 |  | 350 | 421 | 6 | 5
No | 3 | 8 |  | 351 | 421 | 6 | 5
No | 3 | 8 |  | 352 | 421 | 6 | 5
No | 3 | 8 |  | 353 | 421 | 6 | 5
No | 3 | 8 |  | 354 | 421 | 6 | 5
No | 3 | 8 |  | 355 | 421 | 6 | 5
No | 3 | 8 |  | 356 | 421 | 6 | 5
No | 3 | 8 |  | 357 | 421 | 6 | 5
No | 3 | 8 |  | 358 | 421 | 6 | 5
No | 3 | 8 |  | 359 | 421 | 6 | 5
No | 3 | 8 |  | 360 | 421 | 6 | 5
No | 3 | 8 |  | 361 | 421 | 6 | 5
No | 3 | 8 |  | 362 | 421 | 6 | 5
No | 3 | 8 |  | 363 | 421 | 6 | 5
No | 3 | 8 |  | 364 | 421 | 6 | 5
No | 3 | 8 |  | 365 | 421 | 6 | 5
No | 3 | 8 |  | 366 | 421 | 6 | 5
No | 3 | 8 |  | 367 | 421 | 6 | 5
No | 3 | 8 |  | 368 | 421 | 6 | 5
No | 3 | 8 |  | 369 | 421 | 6 | 5
No | 3 | 8 |  | 370 | 421 | 6 | 5
No | 3 | 8 |  | 371 | 421 | 6 | 5
No | 3 | 8 |  | 372 | 421 | 6 | 5
No | 3 | 8 |  | 373 | 421 | 6 | 5
No | 3 | 8 |  | 374 | 421 | 6 | 5
No | 3 | 8 |  | 375 | 421 | 6 | 5
No | 3 | 8 |  | 376 | 421 | 6 | 5
No | 3 | 8 |  | 377 | 421 | 6 | 5
No | 3 | 8 |  | 378 | 421 | 6 | 5
No | 3 | 8 |  | 379 | 421 | 6 | 5
No | 3 | 8 |  | 380 | 421 | 6 | 5
No | 3 | 8 |  | 381 | 421 | 6 | 5
No | 3 | 8 |  | 382 | 421 | 6 | 5
No | 3 | 8 |  | 383 | 421 | 6 | 5
No | 3 | 8 |  | 384 | 421 | 6 | 5
No | 3 | 8 |  | 385 | 421 | 6 | 5
No | 3 | 8 |  | 416 | 421 | 6 | 5
No | 3 | 8 |  | 417 | 421 | 6 | 5
No | 3 | 8 |  | 418 | 421 | 6 | 5
No | 3 | 8 |  | 419 | 421 | 6 | 5
No | 3 | 8 |  | 420 | 421 | 6 | 5
No | 3 | 8 |  | 421 | 421 | 6 | 5
No | 3 | 8 |  | 422 | 421 | 6 | 5
No | 3 | 8 |  | 423 | 421 | 6 | 5
No | 3 | 8 |  | 424 | 421 | 6 | 5
No | 3 | 8 |  | 425 | 421 | 6 | 5
No | 3 | 8 |  | 426 | 421 | 6 | 5
No | 3 | 8 |  | 427 | 421 | 6 | 5
No | 3 | 8 |  | 428 | 421 | 6 | 5
No | 3 | 8 |  | 429 | 421 | 6 | 5
No | 3 | 8 |  | 430 | 421 | 6 | 5
No | 3 | 8 |  | 431 | 421 | 6 | 5
No | 3 | 8 |  | 432 | 421 | 6 | 5
No | 3 | 8 |  | 433 | 421 | 6 | 5
No | 3 | 8 |  | 434 | 421 | 6 | 5
No | 3 | 8 |  | 435 | 421 | 6 | 5
No | 3 | 8 |  | 436 | 421 | 6 | 5
No | 3 | 8 |  | 437 | 421 | 6 | 5
No | 3 | 8 |  | 438 | 421 | 6 | 5
No | 3 | 8 |  | 439 | 421 | 6 | 5
No | 3 | 8 |  | 440 | 421 | 6 | 5
No | 3 | 8 |  | 502 | 421 | 6 | 5
No | 3 | 8 |  | 503 | 421 | 6 | 5
No | 3 | 8 |  | 504 | 421 | 6 | 5
No | 3 | 8 |  | 505 | 421 | 6 | 5
No | 3 | 8 |  | 506 | 421 | 6 | 5
No | 3 | 8 |  | 507 | 421 | 6 | 5
No | 3 | 8 |  | 508 | 421 | 6 | 5
No | 3 | 8 |  | 509 | 421 | 6 | 5
No | 3 | 8 |  | 510 | 421 | 6 | 5
No | 3 | 8 |  | 511 | 421 | 6 | 5
No | 3 | 8 |  | 512 | 421 | 6 | 5
No | 3 | 8 |  | 513 | 421 | 6 | 5
No | 3 | 8 |  | 514 | 421 | 6 | 5
No | 3 | 8 |  | 515 | 421 | 6 | 5
No | 3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[9 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
25-Jul-24
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [12 empty] | Fashion Knit Industries Unit 1 & 2, C-30, S.I.T.E., Manghopir Road, Moin Akhtar Road, Karachi, Sindh, Pakistan.
[9 empty] | Date of Initial Inspection | [12 empty] | 25-Jul-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | This issue refers to Building-01. Building-01 (South Side): The ground-floor internal column of the Building-01 part adjacent to Building-03, which supports the overhead water tank and mezzanine floor (loaded with cotton bales for storage), has been found to be potentially overstressed. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | In Building-01, remove all cotton bales from the external bay of the mezzanine floor and shift them to the ground floor. Send pictorial evidence of this to Pakistan Accord. | 1 month | Factory have immediately removed the cotton bales from the external bay of the mezzanine floor and shift them to the ground floor. Moreover, facility will share the pictorial evidences to Accord. | Done |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | This issue refers to Building-01. Building-01 (South Side): The ground-floor internal column of the Building-01 part adjacent to Building-03, which supports the overhead water tank and mezzanine floor (loaded with cotton bales for storage), has been found to be potentially overstressed. Building-01 (North Side): The ground-floor internal columns of Building-01 near the boiler side (north side elevation) have also been identified as potentially overstressed, likely due to the loading of heavy machinery related to knitting and spinning operations. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Verify in-situ concrete stresses either by 100mm dia. cores from at least four of the identified overstressed columns of each building or existing cylinder strength data for the identified columns along with details of the steel bars, including their type and diameter. When investigating the type, number, and diameter of rebar, only the concrete cover should be removed, and this must be done from the ground floor for at least four columns in a way that does not compromise the overall capacity of the column. Send pictorial evidence and reports to Pakistan Accord for their review. | 3 months | Facility have conduct core testing of the column by third party and already shared the pictures and report of the test to the accord for review. | Done |  |  | In Progress
[9 empty] | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | This issue refers to Building-01. Building-01 (South Side): The ground-floor internal column of the Building-01 part adjacent to Building-03, which supports the overhead water tank and mezzanine floor (loaded with cotton bales for storage), has been found to be potentially overstressed. Building-01 (North Side): The ground-floor internal columns of Building-01 near the boiler side (north side elevation) have also been identified as potentially overstressed, likely due to the loading of heavy machinery related to knitting and spinning operations. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Factory Engineer to review design, loads and columns stresses in areas identified and Submit the report to Pakistan Accord for review. | S2 + 3 months | Factory third party consultant engineer will review the design, loads and columns stresses in areas identified and submit the report to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | This issue refers to Building-01. Building-01 (South Side): The ground-floor internal column of the Building-01 part adjacent to Building-03, which supports the overhead water tank and mezzanine floor (loaded with cotton bales for storage), has been found to be potentially overstressed. Building-01 (North Side): The ground-floor internal columns of Building-01 near the boiler side (north side elevation) have also been identified as potentially overstressed, likely due to the loading of heavy machinery related to knitting and spinning operations. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Produce and actively manage a loading plan for all floor plates within the factory considering floor capacity and column capacity. Submit these plans to Pakistan Accord for review. | S3 + 3 months | Facility will produce and actively manage a loading plan for all floor plates within the factory considering floor capacity and column capacity. Moreover factory will also submit these plans to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | This issue refers to Building-01. Building-01 (South Side): The ground-floor internal column of the Building-01 part adjacent to Building-03, which supports the overhead water tank and mezzanine floor (loaded with cotton bales for storage), has been found to be potentially overstressed. Building-01 (North Side): The ground-floor internal columns of Building-01 near the boiler side (north side elevation) have also been identified as potentially overstressed, likely due to the loading of heavy machinery related to knitting and spinning operations. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Implement approved remedial works as required. | S3 + 3 months | Factory will ensure the implementation of the approved remedial works as per the requirement of Accord Standard. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Potential Overstress | Highly stressed columns | This issue refers to Building-01. Building-01 (South Side): The ground-floor internal column of the Building-01 part adjacent to Building-03, which supports the overhead water tank and mezzanine floor (loaded with cotton bales for storage), has been found to be potentially overstressed. Building-01 (North Side): The ground-floor internal columns of Building-01 near the boiler side (north side elevation) have also been identified as potentially overstressed, likely due to the loading of heavy machinery related to knitting and spinning operations. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Continue to implement approved load plan. | S4 + 1 months | Facility will continue to implement the approved load plan in required areas. | 2025-12-27 |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02 (North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | In Building-02, reduce the stacking of fabric rolls to a maximum of 6 rolls high on the 2nd and 3rd floors. The remaining rolls should be shifted to the ground floor. It must be ensured that the stacking height does not exceed 1.95 meter to maintain a distributed load of 4 KPa. This height restriction is based on the specification of Gray fabric rolls, each having a diameter of 325 mm and an average weight of 27 kg. Send pictorial evidence of this to Pakistan Accord. | 1 month | Factory have removed the rolls stacking above the height of 6 fts. Moreover, factory have also shifted some rolls to the ground floor. Facility have also provided trainings awareness session to the workers for the stacking and safe handling of the fabric rolls. | Done |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02(North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Verify in-situ concrete stresses either by 100mm dia. cores from at least four of the identified overstressed columns of each building or existing cylinder strength data for the identified columns along with details of the steel bars, including their type and diameter. When investigating the type, number, and diameter of rebar, only the concrete cover should be removed, and this must be done from the ground floor for at least four columns in a way that does not compromise the overall capacity of the column. Send pictorial evidence and reports to Pakistan Accord for their review. | 3 months | Facility have conducted core testing of the column by third party and already shared the pictures and report of the test to the accord for review. | Done |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02(North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Factory Engineer to review design, loads and columns stresses in areas identified and Submit the report to Pakistan Accord for review. | S8 + 3 months | Factory third party engineer will review design, loads and columns stresses in areas identified and Submit the report to Pakistan Accord for review. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02(North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | A Detail Engineering Assessment of the Building-02to be commenced and submit the recommendations to Pakistan Accord for review and approval. | 1 month | Facility will conduct a detail Engineering Assessment of the Building-02 to be commenced and submit the recommendations to Pakistan Accord for review and approval. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02(North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building , in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 1 month | Factory have already Appointed qualified and competent Structural Engineer to carry out DEA on the full building , in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02(North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | S11 + 6 months | Factory will submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | 2025-12-27 |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02 (North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | S12 + 4 months | Factory will submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | 2025-12-27 |  |  | In Progress
No | 3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02(North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | (4) Submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review | S13 + 4 months | Factory will submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review | 2025-11-01 |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02 (North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord | S14 + 6 months | Factory will carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02 (North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistani Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete | S15 + 1 months | factory will inform accord Pakistan upon completion of the retrofitting works for verification inspection. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02 (North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Produce and actively manage a loading plan for all floor plates within the factory considering floor capacity and column capacity. Submit these plans to Pakistan Accord for review and approval. | S9 + 3 months | Facility will implement the loading plan for all the floor plates considering the floor capacity and will submit the plan to accord Pakistan accordingly. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02 (North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Implement approved remedial works as required. | S9 + 3 months | Factory will ensure the implementation of the approved remedial works as per the requirement of Accord Standard. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S19 | Potential Overstress | Highly stressed columns | This issue refers to Building-02. Building-02 (North Side): The ground-floor internal columns of Building-02, near the boiler side on the north side (Grid 14 m), are highly stressed, mainly due to the high stacking of Gray fabric rolls. The problem is that these columns may not be able to safely support the loads, potentially leading to structural damage or failure. This situation poses significant safety risks to occupants and could impact the overall stability of the buildings. | Continue to implement approved load plan. | S17 + 1 months | Factory will ensure the continuation of the implementation of approved remedial works as per the requirement of Accord Standard. |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Potential Overstress | Highly stressed columns | This issue refers to Building-04. Building-04: The basement-floor external column of Building-04, on the cantilevered side, has been found to be potentially stressed due to the large number of stories above it. There is a concern that these columns may not fully support the required loads, which could potentially compromise the structural integrity. This situation may present safety considerations for occupants and affect the overall stability of the buildings. | For the newly constructed Building-04, which is currently unoccupied, the allowable loads for all floors must be confirmed by the design engineer prior to occupancy. Submit it to Pakistan Accord for review. | 1 month | Facility will confirm the allowable loads for all the floor at newly constructed building and report should be submit to accord Pakistan for review. | 2025-12-27 |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Potential Overstress | Highly stressed columns | This issue refers to Building-04. Building-04: The basement-floor external column of Building-04, on the cantilevered side, has been found to be potentially stressed due to the large number of stories above it. There is a concern that these columns may not fully support the required loads, which could potentially compromise the structural integrity. This situation may present safety considerations for occupants and affect the overall stability of the buildings. | Factory Engineer to review design, loads and columns stresses in areas identified and Submit the report to Pakistan Accord. | 3 months | Facility third party hired engineer will review design, loads and columns stresses in areas identified and Submit the report to Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S22 | Potential Overstress | Highly stressed columns | This issue refers to Building-04. Building-04: The basement-floor external column of Building-04, on the cantilevered side, has been found to be potentially stressed due to the large number of stories above it. There is a concern that these columns may not fully support the required loads, which could potentially compromise the structural integrity. This situation may present safety considerations for occupants and affect the overall stability of the buildings. | Produce and actively manage a loading plan for all floor plates within the factory considering floor capacity and column capacity. Submit these plans to Pakistan Accord for review. | S21 + 3 months | Factory will produce and actively manage a loading plan for all floor plates within the factory considering floor capacity and column capacity. Submit these plans to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S23 | Potential Overstress | Highly stressed columns | This issue refers to Building-04. Building-04: The basement-floor external column of Building-04, on the cantilevered side, has been found to be potentially stressed due to the large number of stories above it. There is a concern that these columns may not fully support the required loads, which could potentially compromise the structural integrity. This situation may present safety considerations for occupants and affect the overall stability of the buildings. | Implement approved remedial works as required. | S21 + 3 months | Factory will ensure implementation of approved remedial works as required. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S24 | Potential Overstress | Highly stressed columns | This issue refers to Building-04. Building-04: The basement-floor external column of Building-04, on the cantilevered side, has been found to be potentially stressed due to the large number of stories above it. There is a concern that these columns may not fully support the required loads, which could potentially compromise the structural integrity. This situation may present safety considerations for occupants and affect the overall stability of the buildings. | Continue to implement approved load plan. | S22 + 1 months | Factory will ensure the continuation of implementation of approved load plan. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S25 | Structural System | Vertical load path | This issue refers to the ground floor of Building-01. On the ground floor of Building-01, the different placement of columns and beams could result in structural inefficiencies, potential instability, and complications in load distribution. | This issue requires the production of as-built information and for the engineer to review the load paths for both vertical and horizontal loading capacities to ensure compliance with safety and design standards. These documents should then be submitted to Pakistan Accord for review. | 3 months | Facility third party hired engineer will make new as-built and review the load paths for both vertical and horizontal loading capacities to ensure compliance with safety and design standards. Moreover, factory will Submit the report to Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S26 | Structural System | Lateral stability system | This issue concerns Part Building-02, which has a flat slab system from grids 11 to 20. The lack of an apparent lateral stability system in the flat slab structure may lead to inadequate resistance against lateral loads, compromising structural stability and safety. | Building Engineer to review the design and check the overall design and individual element capacity is sufficient for global lateral stability for the mentioned building part. This should include a macro analysis of the lateral load path within the building and then calculations to confirm the elements within that lateral load resisting system are of sufficient capacity to resist the design loading. Submit the report to Pakistan Accord for Review. | 3 months | Factory Building Engineer will review the design and check the overall design and individual element capacity is sufficient for global lateral stability for the mentioned building part. This will include a macro analysis of the lateral load path within the building and then calculations to confirm the elements within that lateral load resisting system are of sufficient capacity to resist the design loading. factory will submit the report to Pakistan Accord for Review. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S27 | Structural System | Lack of local stability | This issue refers to the Building-01. The steel shed’s column in Building-01 lacks lateral stability, which could result in damage to the covered storage area during high wind loads. | Building engineer to ensure to add vertical and horizontal bracing to improve lateral stability of the steel structure. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. | 3 months | Building engineer will ensure to add vertical and horizontal bracing to improve lateral stability of the steel structure. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. |  |  |  | In Progress
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S28 | Structural System | Lack of local stability | The steel bridge between Building-01 and Building-02 acts as a primary means of escape in case of emergency in either building. From visual inspection, the structural capacity appears to be inadequate for high live loads as would be experienced during evacuation in a fire emergency. Additionally, it is a steel structure and therefore its structural fire resistance is unclear (e.g. intumescent paint). | Building Engineer should assess the structural capacity, structural fire resistance and allowable live loading of the existing bridge. Design and implement upgrades the bridge accordingly to ensure it meets required structural standards (load capacity and structural fire resistance) and therefore provides a reliable evacuation route for occupants in case of a fire. Coordination with the fire safety strategy will be essential to ensure that structural upgrades align with the requirements of this strategy. Submit the report and recommendations to Pakistan Accord for review and approval before implementing remedial work. | 3 months | Building Engineer will assess the structural capacity, structural fire resistance and allowable live loading of the existing bridge. Design and implement upgrades the bridge accordingly to ensure it meets required structural standards (load capacity and structural fire resistance) and therefore provides a reliable evacuation route for occupants in case of a fire. Coordination with the fire safety strategy will be essential to ensure that structural upgrades align with the requirements of this strategy. Facility will submit the report to Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S29 | Cracking | Beams | This issue refers to the Building-01. Flexural cracks have been observed in the beam of Building-01. These cracks may be caused by overloading, or there could be another underlying reason. There is a risk that this may lead to local failure of the structure. | Building Structural Engineer to assess load capacity of the as-constructed building and submit to Pakistan Accord for review. | 3 months | Building Structural Engineer will assess load capacity of the as-constructed building and submit the report to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S30 | Cracking | Beams | This issue refers to the Building-01. Flexural cracks have been observed in the beam of Building-01. These cracks may be caused by overloading, or there could be another underlying reason. There is a risk that this may lead to local failure of the structure. | Review the safe loading plans for all floor plates within the factory, considering floor capacity and column capacity. Submit to Pakistan Accord for review. | S29 + 3 months | Factory will review safe loading plans for all floor plates, considering floor capacity and column capacity. Submit to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S31 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Building-01. The slab in Building-01 has developed cracks due to excessive corrosion in the reinforcing bars (rebar), which could lead to the spalling of concrete and pose a risk of injury to individuals. Over time this can lead to loss of structural capacity of the element. | Building Engineer to inspect the areas which is damaged and propose measures to prevent further damage and carry out repair works to restore the structure to its original design capacity. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. | 6 months | Building Engineer will inspect the areas which is damaged and propose measures to prevent further damage and carry out repair works to restore the structure to its original design capacity. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. | 2025-09-01 |  |  | In Progress
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S32 | Other Damage/Defects | Corrosion of reinforcement | This issue refers to the Building-02. The slab in Building-02 has developed cracks due to excessive corrosion in the reinforcing bars (rebar), which could lead to the spalling of concrete and pose a risk of injury to individuals. Over time this can lead to loss of structural capacity of the element. | Building Engineer to inspect the areas which is damaged and propose measures to prevent further damage and carry out repair works to restore the structure to its original design capacity. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. | 6 months | Building Engineer will inspect the areas which is damaged and propose measures to prevent further damage and carry out repair works to restore the structure to its original design capacity. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. | 2025-09-01 |  |  | In Progress
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S33 | Other Damage/Defects | Corrosion of structural steel | This issue refers to the Building-02. In Building-02, the steel stair providing access to the upper roof, which has a steel shed over it, is corroded and lack proper connections and stability. This poses risks such as collapse risk and injury hazard. | For Building-02, Building Engineer should further inspect and repair or replace damaged sections, and reinforce the structure as needed. Also ensure rust treatment is in place to prevent further corrosion damage in future. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. | 6 months | Building Engineer should further inspect and repair or replace damaged sections, and reinforce the structure as needed. Also ensure rust treatment is in place to prevent further corrosion damage in future. Submit the recommendations to Pakistan Accord for review and approval before implementing remedial work. |  |  |  | In Progress
No | 3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S34 | Other Damage/Defects | Corrosion of structural steel | This issue refers to the Building-03. In Building-03, the outdoor MS stairs are used for accessing each floor. Pigeon waste has been observed on the stairs, contributing to corrosion, which compromises both the structural integrity and material of the stairs. | For Building-03, the stairs should be thoroughly cleaned and repainted. | 1 month | Factory has cleared the stairs thoroughly and repainted. | Done |  |  | In Progress
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S35 | Other Damage/Defects | Corrosion of structural steel | This issue refers to the Building-03. In Building-03, the outdoor MS stairs are used for accessing each floor. Pigeon waste has been observed on the stairs, contributing to corrosion, which compromises both the structural integrity and material of the stairs. | For Building-03, if the corrosion has compromised the structural integrity of the stairs, the components should be replaced with new ones to ensure safety and durability. | 1 month | If the corrosion has compromised the structural integrity of the stairs, the factory will replace the component with new ones to ensure safety and durability. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S36 | Other Damage/Defects | Corrosion of structural steel | This issue refers to the Building-03. In Building-03, the outdoor MS stairs are used for accessing each floor. Pigeon waste has been observed on the stairs, contributing to corrosion, which compromises both the structural integrity and material of the stairs. | Install a ledge or pigeon spikes on the beam to prevent pigeons from perching. | 1 month | Facility will Install a ledge or pigeon spikes on the beam to prevent pigeons from perching. |  |  |  | In Progress
No | 3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S37 | Other Damage/Defects | Column impact damage | This issue refers to the Building-02. The column edges are unprotected and have been damaged on the ground floor of Building-02. The deterioration of some column edges may be due to the movement of trolleys or goods. If the damage worsens and the steel is exposed to air, it could lead to corrosion and loss of load bearing capacity of the column. | Repair the columns to restore original concrete section and protect the columns to avoid damages in future. | 1 month | Facility will repair the columns to restore original concrete section and protect the columns to avoid damages in future. |  |  |  | In Progress
No | 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S38 | Other Damage/Defects | Column impact damage | This issue refers to the Building-02. The column edges are unprotected and have been damaged on the ground floor of Building-02. The deterioration of some column edges may be due to the movement of trolleys or goods. If the damage worsens and the steel is exposed to air, it could lead to corrosion and loss of load bearing capacity of the column. | Provide suitable protection (bumpers or bollards) around all RC columns in areas with vehicle or loaded trolley movement to prevent damage or collapse of columns from potential impacts. | 1 month | Facility will provide suitable protection (bumpers or bollards) around all RC columns in areas with vehicle or loaded trolley movement to prevent damage or collapse of columns from potential impacts. |  |  |  | In Progress
No | 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S39 | Other Damage/Defects | Moisture ingress | Moisture ingress has been detected in multiple locations within Building-01. | Identify the source of water ingress in the structural element. Rectify the seepage issue. Check the affected area for any damage that has occurred and repair it accordingly as approved. | 6 months | Factory will Identify the source of water ingress in the structural element and rectify the seepage issue accordingly. Moreover, factory will check the affected area for any damage that has occurred and repair it accordingly as approved. |  |  |  | In Progress
No | 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S40 | Other Damage/Defects | Moisture ingress | Moisture ingress has been detected in multiple locations within Building-02. | Identify the source of water ingress in the structural element. Rectify the seepage issue. Check the affected area for any damage that has occurred and repair it accordingly as approved. | 6 months | Factory will Identify the source of water ingress in the structural element and rectify the seepage issue accordingly. Moreover, factory will check the affected area for any damage that has occurred and repair it accordingly as approved. |  |  |  | In Progress
No | 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S41 | Other Damage/Defects | Moisture ingress | Moisture ingress has been detected in multiple locations within Building-04. | Identify the source of water ingress in the structural element. Rectify the seepage issue. Check the affected area for any damage that has occurred and repair it accordingly as approved. | 6 months | Factory will Identify the source of water ingress in the structural element and rectify the seepage issue accordingly. Moreover, factory will check the affected area for any damage that has occurred and repair it accordingly as approved. |  |  |  | In Progress
No | 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S42 | Structural Documentation | Documentation unavailable | This issue refers to all the buildings. The structural drawings of the drawings of the building are not available. | Factory to engage a suitably qualified structural engineer to develop as-built drawings for all buildings. | 1 month | Factory have already Appointed qualified and competent Structural Engineer to carry out as built drawings for all buildings |  |  |  | In Progress
No | 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S43 | Structural Documentation | Documentation unavailable | This issue refers to all the buildings. The structural drawings of the drawings of the building are not available. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. Submit these documents to Pakistan Accord for review and approval. | S42 + 5 months | Facility have hired Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. Submit these documents to Pakistan Accord for review and approval. |  |  |  | In Progress
No | 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S44 | Structural Documentation | Lack of safe load plans | This issue refers to all the buildings. No safe load plans were posted in the factory. | Factory to engage a suitably qualified structural engineer to develop safe load drawings for all buildings. | 1 month | Factory will engage a suitably qualified structural engineer to develop safe load drawings for all buildings. |  |  |  | In Progress
No | 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S45 | Structural Documentation | Lack of safe load plans | This issue refers to all the buildings. No safe load plans were posted in the factory. | Building Structural Engineer to produce loading plans for all floors within the factory considering floor capacity and column capacity. Loading to be actively managed by Factory Management including display of loading plan on factory floors and visual markers within the building such as stacking heights and zones for storage. Submit these documents to Pakistan Accord for review and approval. | S44 + 5 months | Facility will ensure Building Structural Engineer to produce loading plans for all floors within the factory considering floor capacity and column capacity. Loading to be actively managed by Factory Management including display of loading plan on factory floors and visual markers within the building such as stacking heights and zones for storage. Submit these documents to Pakistan Accord for review and approval. |  |  |  | In Progress
No | 3 | 8 |  | 156 | 421 | 6 | 5 |  | Initial | [10 empty] | S46 | Other Damage/Defects | Health and Safety | This issue refers to the roof of Building-02. There is no edge protection around the periphery of the roof. The roof is accessible and has solar panels installed, which poses a safety risk to individuals. | Restrict access to the roof until protection is in place and install edge protection immediately around the roof. Submit the pictorial evidence to Pakistan Accord. | 1 month | Factory will apply Restrict access to the roof until protection is in place and install edge protection immediately around the roof. Moreover, facility will also submit the pictorial evidence to Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## E Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Cable size
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery | Fixtures
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## F Categories
Categories | Means of Escape | Fire Rated Construction | Hazardous Materials | Fire Suppression | Fire Safety Management
Means of Escape | Protection of stairs | Structural fire rating | Chemicals handling | Standpipe system | Fire drills
Fire Rated Construction | Number of exits | Extensive voids | Chemicals storage | Fire extinguishers | Records of systems maintenance
Fire Suppression | Travel distance | Separation of high-risk areas | Diesel storage | Fire pumps | Records of system testing
Hazardous Materials | Exit capacity | Separation of shafts | Gas storage | Sprinkler system | Staff training
Fire Safety Management | Exit access | Separation of occupancies |  | Water supply | Emergency Action Plan
| Escape stair condition | Floor openings |  | Exterior hydrants | Fire vehicle access
| Exit discharge | Storage |  |  | Other occupancies
| Escape doors | Atrium
Exit signage
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## S Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Damaged structural element
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type