## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
28-Mar-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Ijaz Apparel, 31 km Ferozpur Road, Opposite Main Gate Central Park Housing Scheme, Lahore, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-03-28
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | Single line diagram was not available at site during the inspection | Consult a qualified engineer to design the entire Single Line Diagrams. | 3 months | Ijaz Apparel has Hired a qualified Engineer Consultant to design the entire single Line Diagrams. Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | DBs & Elec Protection Systems | Circuit breakers | During inspection of your main electrical room, it was observed that undersized cables were terminated with oversized breakers. Also, a few areas were found equipped with obsolete circuit breakers that might not perform appropriately during faults. • Office adjacent to Generator room, circuit breaker is mounted on a wall that have signs of water seepage through the roof refer Figure 3 • Circuit breaker mounted on wall for an external light, the condition of wall is poor/cracked, it can cause damage to both breaker and the wall refer Figure 4 • Poorly maintained circuit breakers found in main distribution board of CEO office refer Figure 5 • A Circuit breaker found having some past distress on it refer Figure 6 • Two circuit breakers found at time office, placed inappropriately below wooden blocks with no rating and type mentioned refer Figure 7 | Ensure removing the circuit breaker from the cracked wall referred in Figure 4 | 1 months | The circuit breaker from the cracked wall has been removed on an immediate basis 15-12-2024 : Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Circuit breakers | During inspection of your main electrical room, it was observed that undersized cables were terminated with oversized breakers. Also, a few areas were found equipped with obsolete circuit breakers that might not perform appropriately during faults. • Office adjacent to Generator room, circuit breaker is mounted on a wall that have signs of water seepage through the roof refer Figure 3 • Circuit breaker mounted on wall for an external light, the condition of wall is poor/cracked, it can cause damage to both breaker and the wall refer Figure 4 • Poorly maintained circuit breakers found in main distribution board of CEO office refer Figure 5 • A Circuit breaker found having some past distress on it refer Figure 6 • Two circuit breakers found at time office, placed inappropriately below wooden blocks with no rating and type mentioned refer Figure 7 | Identified circuit breakers need to be checked and replaced as per their application. Ensure not to mount circuit breakers on external wall and area where rain water ingress, move their respective circuits inside a weather proof distribution panel. | E2 + 1 month | Consultant will check and will replaced to perform adequately as per their application, It will be ensured that not to mount circuit breakers on external wall and area where rain water ingress, move their respective circuits inside a weather proof distribution panel. 31-01-2025 : Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | During inspection of your main electrical room, it was observed that undersized cables were terminated with oversized breakers. Also, a few areas were found equipped with obsolete circuit breakers that might not perform appropriately during faults. • Office adjacent to Generator room, circuit breaker is mounted on a wall that have signs of water seepage through the roof refer Figure 3 • Circuit breaker mounted on wall for an external light, the condition of wall is poor/cracked, it can cause damage to both breaker and the wall refer Figure 4 • Poorly maintained circuit breakers found in main distribution board of CEO office refer Figure 5 • A Circuit breaker found having some past distress on it refer Figure 6 • Two circuit breakers found at time office, placed inappropriately below wooden blocks with no rating and type mentioned refer Figure 7 | Schedule a proper maintenance records to monitor, control and rectify weak electrification works. | E3 + 3 months | It will be started to maintain a Proper Maintenance Record to monitor, control, and rectify weak electrification works. 31-01-2025 : Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. 1. Neutral of main LT Panel in generator room at 86.4 ℃ refer Figure 8 2. Hotspot at terminal connector in main LT panel of production building at 157 ℃ refer Figure 10 3. Hotspot at loose power plugs at various location such as Kitchen, office and stitching area at 40 ℃ to 60 ℃ refer Figure 12 Figure 16 4. Hotspot found on one phase of various circuit breakers indicating system imbalance refer Figure 18 Figure 19 . It can be also witnessed from overloading of a neutral in stitching area. | Finding 2 exemplify in Figure 10. They show that high temperatures need immediate rectification by addressing and repairing the cause of abnormal temperature in cable joint, which may involve overloading, connection tightening, or replacement of faulty cable joint. | 1 months | Concerned Joint reflecting in Figure 10 has been rectified on an immediate basis. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. 1. Neutral of main LT Panel in generator room at 86.4 ℃ refer Figure 8 2. Hotspot at terminal connector in main LT panel of production building at 157 ℃ refer Figure 10 3. Hotspot at loose power plugs at various location such as Kitchen, office and stitching area at 40 ℃ to 60 ℃ refer Figure 12 Figure 16 4. Hotspot found on one phase of various circuit breakers indicating system imbalance refer Figure 18 Figure 19 . It can be also witnessed from overloading of a neutral in stitching area. | Inspect the finding 1,3 and 4 all electrical panel to identify the source of abnormal temperatures, which may be caused by phase imbalance, loose connections, overloaded circuits, or other issues. Create a schedule to have a thermograph survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. | E5 + 1 month | Our Qualified Engineer Will Inspect the finding 1,3 and 4 all electrical panel to identify the source of abnormal temperatures, which may be caused by phase imbalance, loose connections, overloaded circuits, or other issues. We will Create a schedule to have a thermograph survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. 15-12-2024 : Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Hot Spots | Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. 1. Neutral of main LT Panel in generator room at 86.4 ℃ refer Figure 8 2. Hotspot at terminal connector in main LT panel of production building at 157 ℃ refer Figure 10 3. Hotspot at loose power plugs at various location such as Kitchen, office and stitching area at 40 ℃ to 60 ℃ refer Figure 12 Figure 16 4. Hotspot found on one phase of various circuit breakers indicating system imbalance refer Figure 18 Figure 19 . It can be also witnessed from overloading of a neutral in stitching area. | Carry out independent thermographic survey. | E6 + 5 months | An independent thermograph survey will be carried out by our qualified engineer & the Report will be submitted to Accord Pakistan for review. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | During the inspection no earth pits witnessed on-site, however there were earth terminal bars present in generator area with few earth connections. Few areas were lacking with earth arrangement which are listed below: • Main changeover panel at Generator Room • Main junction panel for 400 Volt overhead and power cable. • Distribution board of stitching unit and power plugs of stitching machines. | All earth connections must be connected to earth pits via their respective distribution board. Connect all metal bodies of Electric panels to the earth terminal within electric panels. | 3 months | All earth connections will be connected to earth pits via their respective distribution board & Connecting all metal bodies of Electric panels to the earth terminal within electric panels. Our consultant will work to complete this task. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Earthing system | In most of the areas, earth bonding of cable tray, metal structures, metal tables and motor frames found missing such as: • Metering panel enclosure mounted on pole of main transformer • Generator changeover panel in generator room. • Shed Lights on Roof • UPS frame in plotter room • Distribution board production area • Lace and Button making machine at Ground Floor of Building 03 Cutting | Metal that is likely to be live near electrical installation shall be bonded with earth to avoid any hazard. | E8 + 1 month | Metal that is likely to be live near electrical installation shall be bonded with earth to avoid any hazard. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Panel/cabling/busbar | During inspection many of the distribution board found to have undress electrical wiring and bunching. In some Distribution Boards, idle or dismantled cables were found, which could pose a potential hazard and ignite a fire. Few of the areas are listed below: • LT Panel generator room having loose internal wires tied on busbars. • Distribution Panels at CEO office and Meeting Room Building 02 lack of panel cable dressing. • Main LT panel building 03 stitching unit and its emergency lighting panel. • Distribution boards of stitching unit. | Removal/Dismantling of Idle cables and cable dressing need to be done for each distribution board. Ensure no cable bunching and splicing at all. All electrical components must be protection against fire risk factors. Replace it with properly designed switchboard mounted on wall surface with no exposed wiring. | 1 months | Ijaz Apparel's consultant will ensure to remove / Dismantle of Idle cables and cable dressing that is need to be done for each distribution board. It will be Ensured that no cable bunching and splicing at all. All electrical components must be protection against fire risk factors.It will be Replaced with properly designed switchboard mounted on wall surface with no exposed wiring. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Panel/cabling/busbar | During inspection many areas were found to have poor condition of electrification works. Below are few examples: • Water containers placed in place of rubber mats at meeting room distribution board. • Electrical power plugs and sockets are mounted deep inside the account’s office furniture, also covered with combustible. • Terminal Strip, Connector and Locally joint cables of neutral was observed in many of the stitching machine panels. • Rusted terminal strip found in stitching area panels with no earth connection to it. | Cable dressing need to be done for each distribution board. Ensure proper maintenance, control and rectify weak electrification works. | E10 + 2 months | Cable dressing will be done for each distribution board. It will be Ensured that proper maintenance, control and weak electrification works will be rectified. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Multiple Connections | During the inspection it was observed that there was cross-circuiting (Looping, Bunching at Moulded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) in the panels. In some Distribution Boards, multi looping was found on circuit breakers at various locations, below examples can be refer below: • Circuit Breakers in Stitching, Cutting and Packing distribution boards. • Circuit Breakers in CEO office and meeting room distribution boards. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. | 2 months | Qualified Engineer will Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Openings | During inspection it was observed at various location that the distribution board have unsealed openings having sharp edges which can damage insulation of the cables. This could provide passage for rodents to enter which could lead to a potential hazard of short circuit such as: • Main Generator panel in generator room. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 1 months | All openings in electrical panels will be sealed (using plates and cable glands) to prevent the ingress of dust and dirt. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Openings | During inspection it was observed at various location that the distribution board have unsealed openings having sharp edges which can damage insulation of the cables. This could provide passage for rodents to enter which could lead to a potential hazard of short circuit such as: • Main Generator panel in generator room. | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. | E13 + 1 month | A regular maintenance and cleaning schedule will be started to maintain for all electrical panels. It will also be Ensured that electrical panels are cleaned, inspected, and free from dust and dirt. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Adequate accessibility | During the survey, it was noted that various locations exhibited inadequate work clearance within facility such as • Cutting store distribution board was completely inaccessible. • Old mosque area (which as store nowadays), the distribution board was stuck behind the iron racks even during inspection the racks were hurdling. • The LT panel of building 04 near boiler has very less accessibility area, the clearance from the panel to was is less than 1.2 m. | The accessibility to the distribution board of cutting store and old mosque area needs to be clear by shifting of racks and managing storage in-order. Check feasibility and ensure clear working space in front of panel not less than 1.2m. | 1 months | The accessibility will be ensured to the distribution board of cutting store and old mosque area needs to be clear by shifting of racks and managing storage in-order. Feasibility and ensure clear working space will be checked in front of panel not less than 1.2m. 31-01-2025 : Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection many of the distribution boards places on external walls were in very rusted condition. Weather impacts are clearly visible in below pictures. All distribution boards being placed in external environment must be waterproof from rain, rust and dust. Few areas with such distribution boards are: • Metering Panel on transformer poles (at main date) • Distribution board at building 02 – CEO Office and Meeting Room • Distribution panel of water-cooling machine and emergency lighting. | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. All external electrical distribution boards must be IP rated for protection against environmental factors. | 1 months | A regular maintenance and cleaning schedule will be Initiated for all electrical panels. It will be Ensured that electrical panels are cleaned, inspected, and free from dust and dirt. All external electrical distribution boards will be IP rated for protection against environmental factors. 30-12-2024: Our mechanical team has replaced the all external distributions boards with IP rated boards that's are now fully protected against environmental factors. Also a schedule for cleaning and maintenance of electrical panels is being followed and maintained now. Moreover the record of cleaning and maintenance of all areas/Panels has been also maintained now. Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection many of the distribution boards places on external walls were in very rusted condition. Weather impacts are clearly visible in below pictures. All distribution boards being placed in external environment must be waterproof from rain, rust and dust. Few areas with such distribution boards are: • Metering Panel on transformer poles (at main date) • Distribution board at building 02 – CEO Office and Meeting Room • Distribution panel of water-cooling machine and emergency lighting. | Develop a periodic maintenance record of distribution boards. | E16 + 1 months | A periodic maintenance record of distribution boards will be maintained. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During inspection it was observed that two of the roofs were equipped with Solar Panels but there was no Lightning Protection system (LPS) is installed in the facility. Any document related to LPS assessment was also not found | Risk assessment for Lightning Protection System should be carried out by qualified engineer and design system accordingly if required. | 6 months | Risk assessment will be done for Lightning Protection System that will be carried out by qualified engineer and design system accordingly if required. Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system, not a listed system that does not provide alarm and notification features consistent with building standards. It’s a push button type notification system that triggers hooters. Detectors of stand-alone type were found that were incorrectly installed or obstructed which could cause delayed activation mostly in production area. Fire detection and alarm cabling is not listed fire rated. | Ensure effective operation of currently installed alarm and detection system in the building. | 3 months | We have ensured the effectiveness of the operation of the currently installed alarm and detection system in the building. 15-12-2024: Our existing Fire alarm system has been inspected, repaired where necessary, and is now calibrated twice weekly to ensure it remains fully functional and well-maintained at all times also the proper record of calibration has been maintained now . Moreover we Marked Numbering at all alarm buttons for identification & in this way we feel very easy to monitor alarm performance Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Fire Alarm was less audible throughout the facility as it was divided building by building having a push button approach. Many areas were lacking coverage of fire detection such as: • Generator Rooms • Record Room • Canteen • Kitchen Area • CEO/Meeting & Accounts Office • Guest Room • Scrap Room • Cutting Area Storage | Fire detection and alarm system in the factory shall be rectified or replaced with a system that fully complies with NFPA 72. Provide design for fire detection and alarm system with a listed addressable fire alarm system in accordance with NFPA 72. Submit design to Pakistan Accord for review prior to completing installation of the system Replace the fire detection and alarm system wiring with fire resisting cables Provide or replace manual fire alarm boxes (MCPs) with listed devices located in accordance with NFPA 72 | E20 + 1 months | A design of Correction or Replacement fire detection and alarm system with a listed addressable fire alarm and detection system (FADS) in accordance with NFPA 72. Design documentation will be submitted to Accord Pakistan for review and further advice. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Fire Alarm was less audible throughout the facility as it was divided building by building having a push button approach. Many areas were lacking coverage of fire detection such as: • Generator Rooms • Record Room • Canteen • Kitchen Area • CEO/Meeting & Accounts Office • Guest Room • Scrap Room • Cutting Area Storage | Install addressable fire detection and alarm system as per reviewed design and in accordance with NFPA 72. Provide a new, listed addressable fire alarm panel in accordance with NFPA 72, or confirm current alarm panel meets requirements. Design shall be submitted to Pakistan Accord for review prior to installation of the system. | E21 + 4 months | A design of improvement or Replacement fire detection and alarm system with a listed addressable fire alarm system in accordance with NFPA 72. will be submitted to Accord Pakistan for review and further advise. If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened. Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Manual Call Points | Fire alarm test was conducted by push button notification. There was no any arrangement available to test the stand-alone smoke detectors placed in few areas. Overall fire alarm audibility is only subjected to that building whose push button is pressed. However, building 02 and 03 are equipped with a hooter siren for notifying the fire. | Consult a qualified engineer to design and implement FADS system as per NFPA standard as recommended in Section 8.1 | E22 + 5 months | Consultation is being done with a qualified engineer to design and implement Factory will install Manual Call points as part of the FADS system as per NFPA standard as recommended in Section 8.1. Once installation of full FADS is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Detectors | The fire alarm system was test by smoke detectors and manual call point from two locations. During test following are the audibility levels on each floor. • Storage area Building 03, detectors are not at the highest point • In Stitching Area building 03, detectors are not at highest point | Consult a qualified engineer to design and implement FADS system as per NFPA standard as recommended in Section 8.1 | E23 + 3 month | Our Qualified Engineer Consultant will prepare Design of Factory will install Detectors as part of the FADS system as per NFPA standard as recommended in Section 8.1. Factory will advise Accord when the full FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Emergency Lighting | No emergency lighting | During the inspection of emergency lighting system, it was noted that several emergency lights were non-operational and did not comply with building standards. Additionally, they have a UPS arrangement for backup lighting that they utilize as an emergency lighting | All emergency lights of an area must be supplied by dedicated circuit, having separate circuit breaker in the main panel, also need to regularly check the battery backup of lights for necessary replacement. | E13 + 3 months | Our Qualified Engineer will design the layout for of Emergency lights as per the recommended Criteria, and the drawing and full design documentation will be submitted to the Accord for Review and Approval. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Emergency Lighting | No emergency lighting | During the inspection of emergency lighting system, it was noted that several emergency lights were non-operational and did not comply with building standards. Additionally, they have a UPS arrangement for backup lighting that they utilize as an emergency lighting | A qualified engineer needs to be consulted to design an emergency lighting system. | 6 months | It will be consulted to a qualified engineer to design and instal an emergency lighting system in accordance with the design previously reviewed by Accord. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Generator, Transformer & Sub-Station Room | Battery | During inspection, it was observed that the batteries of generator had some fluid spills as we had seen fluid spread off the batteries. Furthermore, the battery placement for generator was inadequate and their terminal are bare. This is not safe and have a risk of electrocution as well as causing fire if exposed to combustible materials | Bare terminals covering and battery water spills need to be addressed. | 1 month | Bare terminals covering and battery water spills will be addressed. 31-12-2024: Our Mechanical Team has replaced terminals with new ones. Moreover, batteries are now clean and safe-conditioned. Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Generator, Transformer & Sub-Station Room | Battery | During inspection, it was observed that the batteries of generator had some fluid spills as we had seen fluid spread off the batteries. Furthermore, the battery placement for generator was inadequate and their terminal are bare. This is not safe and have a risk of electrocution as well as causing fire if exposed to combustible materials | Inspection and maintenance of batteries need to be done periodically. | 1 months | Inspection and maintenance of batteries will be done periodically. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Cabling & Wiring | Cables support and protection | During the inspection it was observed that the cables are not protected and supported properly throughout the facility. This includes many of the following areas such as: • Main Transformer cables are separated by a wooden plank. (main entrance) • Loose cable found near metallic pipe of gas. (main entrance) • Generator Room, Guard Room, Canteen and wall adjacent to CEO office. • Kitchen, roof solar and boiler area. | All kind of exposed wiring must be laid with proper dressing and their relevant conduits. | 3 months | All Exposed wiring will be laid with proper dressing and their relevant conduits. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Cabling & Wiring | Cables support and protection | During the inspection it was observed that the cables are not protected and supported properly throughout the facility. This includes many of the following areas such as: • Main Transformer cables are separated by a wooden plank. (main entrance) • Loose cable found near metallic pipe of gas. (main entrance) • Generator Room, Guard Room, Canteen and wall adjacent to CEO office. • Kitchen, roof solar and boiler area. | Install appropriate cable containment arrangement for the electrical system. | 3 months | Our Qualified Engineer will conduct an Assessment and will ensure an appropriate cable containment arrangement for the electrical system. A report will be submitted to Accord Pakistan for review. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. PVC Tapping joints found in different distribution boards. Some areas of our finding are listed below: • Spliced cables joint with PVC taping at kitchen area. • Multiple cable joints found main distribution panel of ground floor • In cutting area tape joints found between two cables of different sizes. • Of distribution board of stitching units 1srt floor, 2nd floor and marketing office, kitchen and meeting rooms have numerous PVC tape joints. | Replace the affected cables with: • continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or • use joint boxes and appropriate connectors to joint cables. All stranded cables terminations shall be installed with proper cable lugs. | 3 months | Affected cables will be replaced with: • continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or • use joint boxes and appropriate connectors to joint cables. All stranded cables terminations shall be installed with proper cable lugs. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Cabling & Wiring | Colour coding | It was noted that within various panels and distribution boards, the phase of the cables could not be determined based on their colour coding in accordance with the building standard at multiple locations such as: 1. The wrong-coloured cable has been installed in stitching area first floor. 2. Also, few distributions board in production building lack with the colour coding. | All distribution board need to be wired with correct colour coding as per building standard. | 2 months | All distribution boards will be wired with correct color coding as per building standards. |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
28-Mar-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Ijaz Apparel, 31 km Ferozpur Road, Opposite Main Gate Central Park Housing Scheme, Lahore, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-03-28
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable doors on escape routes observed in all Buildings including -Emergency exits, Stores, Workshops, Production areas | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard | 1 month | We are actively working on removing all non-compliant locking features from egress doors and will remove completely till end of December. 30-12-2024: The factory has removed all locking features from doors on all egress paths. However with office doors, we installed locking devices that are always openable from the inside. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable doors on escape routes observed in all Buildings including | Provide easily opening mechanisms complying with Pakistan Accord Building Standard Section 1 Clauses 1.4 & 1.5 | 3 months | We are actively working on removing all non-compliant locking features from egress doors and waiting for a meeting between Accord engineers and our management to finalize a security solution that ensure both safety and ease of access. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Protection of stairs | Exit stairways not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies in Building #3 & Building #4 . Storage of Combustible materials on stairs in Building # 4 and Combustible material stored under stairs Building # 3 | Remove all combustible material stored along stairs | 1 month | Combustible material has been removed from along the stairs. Factory will ensure to keep clear all areas near the stairs. 15-12-2024 : Corrective Done. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Exit stairways not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies in Building #3 & Building #4 | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs; - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | We are working to prepare drawings showing the proposed fire-separating construction to protect the stairs. We ensure that the Drawings will cover the location of Fire Rated walls/doors to protect the stairs according to advised door features and criteria and submit to Accord for review. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies in Building #3 & Building #4 | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. | F4 + 4 months | Factory is working to submit a proposed plan to ensure that all stairs are fire-separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. After Approval, all stairs will be provided with fire separation from the rest of the building. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Exit access | Reduced exit capacity due to temporary obstruction with stored goods along means of egress • Building #3 - Lab & Office area - Combustible material Stored along access obstructing exit • Building #3 – Ground floor Production area & Storage area – Combustible material obstructing exit | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 1 month | The obstruction of escape paths have been cleared now, Factory will ensure to maintain them free of all obstructions all time. 15-12-2024 : Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Fire Rated Construction | Storage | Excess material storage was observed in following areas -Building #2 – Merchandiser office -Building #3 – Ground floor quality area -Building # 4 - 1st Floor Store not separated from Production area -Building # 4 – Ground Floor production not separated from Store | Identify all designated storage areas. For all storage areas where storage cannot be managed within in-process storage limitations described above, prepare drawings showings proposed fire separation details of storage areas. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors. Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review . |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Fire Rated Construction | Storage | Excess material storage was observed in following areas -Building #2 – Merchandiser office -Building #3 – Ground floor quality area -Building # 4 - 1st Floor Store not separated from Production area -Building # 4 – Ground Floor production not separated from Store | Provide the required fire separation as per documentation reviewed by Pakistan Accord. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | F7+ 4 months | Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Fire Rated Construction | Separation of high-risk areas | Following are the Observations : • Building #1 - Electrical workshop – High voltage panels inside work shop near building #1 – UPS system not separated from storage • Building #1 – Gas burners inside office areas | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review prior to the rectification works. The drawings should cover the following: - Locations of all increased fire hazard areas in the building (e.g Electrical rooms, Generator, mechanical rooms etc.) - Locations of fire rated walls and doors to protect these rooms; - Details of proposed fire walls and fire doors (e.g. door listing, self-closers, door opening direction); - Remove portable gas burners from offices and storage areas. | 4 months | We are working to prepare drawings showing the proposed fire-separating details of increased fire hazard areas. These shall be submitted to Accord for review prior to the rectification works. The drawings will cover the following: - Locations of all increased fire hazard areas in the building (e.g Electrical rooms, Generator, mechanical rooms etc.) - Locations of fire rated walls and doors to protect these rooms; - Details of proposed fire walls and fire doors (e.g. door listing, self-closers, door opening direction), Moreover burners have been removed from offices. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Fire Rated Construction | Separation of high-risk areas | Following are the Observations : • Building #1 - Electrical workshop – High voltage panels inside work shop near building #1 – UPS system not separated from storage • Building #1 – Gas burners inside office areas | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F9+ 4 months | It will be provided the 2-hour fire rated construction including 90-minute fire rated doors assemblies upon approval of our submitted designs and drawings. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Hazardous Materials | Diesel storage | Following is the Observation : Generator area – Electric Panels – Generator – Diesel storage in same area | Interior diesel storage (maximum 1265 litres on ground level) is permitted if it is fire separated from other areas by 1-hr fire rated construction and stored in accordance with other requirements of NFPA 30. Diesel storage is permitted within generator rooms and fire pump rooms if adequately stored and that room is separated from adjacent occupancies. | 3 months | We would like to clarify that the container in question has not been used for an extended period and is currently being kept as scrap. We understand the concern regarding the size of the container exceeding permitted limits. To address this non-compliance, we are committed to remove the container within the next six months. We will ensure that this action is taken in a timely manner to align with compliance requirements. |  |  |  | In Progress
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2024-03-28
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Ijaz Apparel, 31 km Ferozpur Road, Opposite Main Gate Central Park Housing Scheme, Lahore, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-03-28
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | For the area indicated in Red outline in the report; all loads, including equipment, garments, and personnel, at the 1st floor level to be completely removed within the highlighted floor zone. This area can be used for the normal circulation of workers. | 1 month | The area indicated in the Red outline in the report is not being used now for any type of load like equipment, garments, and personal, all loads from the concerned area have been suspended. 30-11-2024 : Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | Remove the concrete cover around the columns marked in yellow to check the size of RCC column without render, number, and diameter of the reinforcing bars. | 2 months | Our consultant engineer will remove the concrete cover around the columns marked in yellow to check the size of RCC column without render, number and diameter of the reinforcing bars. The report will be submitted to Accord for review. 23-12-2024: Our consultant reviewed the structural design of said building based on original design drawings / collected data and proposed retrofitting of few columns as shown in attached drawing. Retrofitting also includes the overstressed columns as highlighted in ACCORD Pakistan detailed report. Retrofitting will be performed after to get go ahead from your esteemed organization. Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | Verify in-situ concrete strengths either by 100mm diameter cores taken by approved laboratory or existing cylinder strength data for the identified columns recorded during the construction period. | 2 months | Our consultant will Verify in-situ concrete strengths either by taking 100mm diameter cores from an approved laboratory or using existing cylinder strength data for the identified columns recorded during the construction period. The report will be submitted to Accord for review, and then further corrective actions will be taken. 23-12-2024: The highlighted electric board were placed in 50mm thick cement plaster not in column RCC. Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | Inform Accord about the results to allow re-checking of column stress. Further instruction on use of the affected area will be given by Accord based on further analysis. | S3+ 1 month | The consultant engineer will work to reach the results that allow re-checking of column stress. The report will be submitted to Accord for Review and further proceedings. 23-12-2024: The highlighted electric board were placed in 50mm thick cement plaster not in column RCC. Corrective Action Done |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | Appoint qualified and competent Structural Engineer to carry out Detailed Engineering Assessment (DEA) on the full building, in accordance with the attached requirements and Scope, and commence DEA. | 19 months | Ijaz Apparel has hired a qualified and competent structural engineer to carry out a detailed engineering assessment (DEA) on the full building, according to the attached requirements and Scope, and commence DEA. The report will be submitted to Accord Pakistan for Review. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | 1. Development of Full Engineering As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings. | 1 month | Engineer will work on Development of Full Engineering As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings. Once Drawings will be completed it will be submitted to Accord Pakistan. 28-02-2025: Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | 2. The Structural Engineering team are to carry out supporting calculations with a model-based design check to assess the safety and serviceability of the building against loading as set out in Building Code of Pakistan. Lower rate provisions can be applied in accordance with the Pakistan Accord Building Standard. Following international engineering practice, justification for these lower rate provisions must be made. | S6 + 3 months | Ijaz Apparel's Consultant Structural Engineering team will carry out supporting calculations with a model-based design check to assess the safety and serviceability of the building against loading as set out in the Building Code of Pakistan. Lower rate provisions can be applied under the Pakistan Accord Building Standard. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | 3. A Geotechnical Report describing ground conditions and commenting on foundation systems used/proposed. | S7 + 4 months | Ijaz Apparel's consultant Engineer will work on a Geotechnical Report reflecting ground conditions and commenting on foundations systems used/Proposed. Once report will be completed it will be submitted to Accord Pakistan for review. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | 4. A report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied. | S8 +4 months | A report consisting on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied will be submitted to Accord once our consultant completes it. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | 5. Detailed load plans shall be prepared for each level showing current and potential future loading with all key equipment items shown with associated loads. | S9 +6 months | Our Consultant will prepare Detailed load plans for each level showing current and potential future loading with all key equipment items shown with associated loads. A report consisting on Load plan will be submitted to Accord for review. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | 6. The Structural Engineering team will prepare an assessment report that covers the following: .) As-built drawings including .) Plans at each level calling up and dimensioning all structural components. .) Cross sectional drawings showing structural beams, slabs, floor to floor heights, roof build-ups and basic design information of the structure. .) Highlight any variation between As built compared to the designed structure .) Results of testing for strength and materials .) Results of geotechnical assessment and testing/investigation .) Details of loading, inputs and results of computer modelling .) Commentary on adequacy/inadequacy of elements of the structure .) Schedule of any required retrofitting required for safety or performance of structure. | S 10 + 1 month | Our Consultant Structural Engineering team will prepare an assessment report that covers the following: .) As-built drawings including .) Plans at each level calling up and dimensioning all structural components. .) Cross-sectional drawings showing structural beams, slabs, floor-to-floor heights, roof build-ups, and basic design information of the structure. .) Highlight any variation between As built compared to the designed structure .) Results of testing for strength and materials .) Results of geotechnical assessment and testing/investigation .) Details of loading, inputs, and results of computer modeling .) Commentary on adequacy/inadequacy of elements of the structure .) Schedule any required retrofitting required for the safety or performance of the structure. The Report will be submitted to Accord For Review and then will be proceeded for further. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | Submit proposals for retrofitting works to be undertaken to demonstrate the adequacy of the structure to Pakistan Accord for review | 6 months | After Complete Assessment, our consultant will Submit proposals for retrofitting works to be undertaken to demonstrate the adequacy of the structure to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | Carry out all retrofitting works as proposed and previously reviewed by Pakistan Accord. | 6 months | Once all reports and Plans will be submitted to Accord Pakistan then proposed retrofitting work by Accord will be Planned to carry out. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns on the ground floor of the two-story main production building appear to be overstressed due to the applied loads. Factors contributing to this issue include 250mm floor finishes on the first floor, a potential 15-50mm render around all the ground floor columns making the column size unclear, and indications of lower concrete strength from the rebound hammer test. Additionally, the installation of electric boards inside the reinforced concrete columns may have damaged or cut the columns vertical reinforcement, which needs to be confirmed and assessed on-site as these columns were in the highlighted zone. | Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then DEA will be complete | 1 months | Factory will advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Structural Documentation | Differs from as-built structure | As-built structural layouts of the Main Production building will be updated as part of the DEA. As-built structural layouts of the Yarn stores, Canteen, and Wastage store buildings to be prepared. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | Our Consultant Building Structural Engineer to carry out an on-site survey, collect information, and produce accurate and complete as-built documentation. Report will be submitted to Accord Pakistan for review. 28-02-2025 : Corrective Action Done |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in the factory. | Factory to post the safe load for Main production building that are obtained from DEA of the building. | 3 months | Once our consultant will complete Detailed Engineering Assessment then the safe load plan will be posted for Main production building that are obtained from DEA of the building. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in the factory. | Continue to implement load plan and manage floor loading. | 3 months | Once our consultant will complete Detailed Engineering Assessment then safe load plan will be Managed & posted for Main production building that are obtained from DEA of the building. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Cracking | Non structural | Significant masonry cracks were observed in the boundary walls between the CEO Office building and the waste store.These cracks appear to be caused by either ground settlement or lateral movement of the boundary wall. Notably, no cracks have extended into the CEO Office building. They are confined to the wall joints. Likewise, a masonry crack is observed in the corner of the Generator room. The crack appears to be a result of poor jointing detail. | Prop the boundary wall from the outer side to avoid the collapse of the wall. | 2 months | Concerned Wall has been re-built on an immediate basis. 30-11-2024 : Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S19 | Cracking | Non structural | Significant masonry cracks were observed in the boundary walls between the CEO Office building and the waste store.These cracks appear to be caused by either ground settlement or lateral movement of the boundary wall. Notably, no cracks have extended into the CEO Office building. They are confined to the wall joints. Likewise, a masonry crack is observed in the corner of the Generator room. The crack appears to be a result of poor jointing detail. | Dismantle and rebuild the wall section. Submit wall joint details for Accord reviews, proceed with the remedial work. | S18 + 4 months | The concerned Wall has been rebuilt, our consultant will share details regarding wall joints. 15-01-2025: Since Our Mechanical work team is engaged to install the roof railing ( S20 ), once they complete the railing they will start work for the stairs. 12-03-2025: 100% Corrective Action Done. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Other Damage/Defects | Health and Safety | This relates to all roofs which require access for services and maintenance. No parapet walls or lower parapet height walls were observed along the roof edges of Main Production and Finishing buildings. According to cl. 15.3.3.1 of the BCP Fire Safety Provisions – 2016, railings or guards should not be less than 1065mm above the aisle surface. Similarly, lack of edge protection is observed along the 1st floor balcony edge of the Office building. These items present a risk of potential injury resulting from slip, trip or fall from roof/floor during the access and maintenance – Health & Safety concern. | Provide appropriate edge protection to the areas. | 3 months | The roof access to the areas with a lack of roof parapet/railing is restricted till the installation of the roof railing. The railing plan reflecting the parameters, will be shared to Accord Pakistan for review and approval. 15-01-2025: Since Our Mechanical work team is engaged to install the roof railing ( S20 ), once they complete the railing they will start work for the stairs. 12-03-2025: 100% Corrective Action Done. |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Other Damage/Defects | Health and Safety | Roof of the Main Production building generally requires regular access for services and maintenance due to the presence of solar panels. Presently, workers use a bamboo ladder for the roof access, a practice deemed unsafe in standard industry due to various reasons such as (non-exhaustive). - Defective or poorly maintained ladders - Slippery surfaces and inclement weather conditions result into workers to lose footings on steps. - Workers fail to grip ladders adequately. - Toppling of ladders due to high winds | Provide appropriate and safe stairs for the roof access | 3 months | The roof access to the areas with a lack of roof parapet is restricted till the provision of safe roof stairs. The Stairs Plan reflecting the parameters, will be shared to Accord Pakistan for review and approval. 15-01-2025: Since Our Mechanical work team is engaged to install the roof railing ( S20 ), once they complete the railing they will start work for the stairs. 12-03-2025: 100% Corrective Action Done. |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1