## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
28-Nov-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Knittex Garments, Plot # 103, Sector 15, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 28-Nov-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | Single Line Diagrams were not updated. | Consult a qualified engineer to design the entire Single Line Diagrams and rectify design issues. | 3 months | We have consulted a qualified engineer to design SLD . As he has visited us and suggested some requirements for the single line diagram. We will start working on it asap. Factory will appoint a qualified person to produce a SLD and submit to Accord for review Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | Thermographic & Insulation Test Reports were not provided. Earth testing report were not available on site. | Thermographic, Insulation Testing and Earth Testing report shall be prepared. | 6 months | We have consulted a qualified engineer for this. He has suggested to Tighten Connections , Checking of Earthing Readings and after that we will for Outsourcing test reports Factory will provide an electrical layout drawing and submit to Accord for review and feedback |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | As-built Layout drawings were not updated. | Consult a Qualified Engineer complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation | 6 months | For AS-Built Layout , we have consulted a qualified engineer and we are working to estimate the quantities for lighting, power outlets, and fans , Layout and Dimensions. After that we will process the as built diagram. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | Lightning protection system is not installed in the facility. Any document related to LPS assessment was not presented. | Risk assessment for Lightning Protection System should be carried out by qualified engineer and design system accordingly if required | 6 months | We are taking quotation for this and checking the feasibility. Further , we have also consulted with a qualified engineer to assess risk and suggest us accordingly Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Earthing system | Earthing connections are missing from some panels. Termination bars are not being used to connection earth cable in panels where there is earthing. | Earthing connections should be provided for all panels, using proper clamps, lugs, and bolts, to connect the earth continuity conductor to the earth electrode. This will ensure that the panels are effectively earthed and will not become live in case of a fault | 2 months | We are testing the earthing (grounding) reading that is a crucial first step to ensure safety and proper functioning of electrical systems. After confirming that the earthing values are within the safe range, we can proceed for the final earthing with all equipments. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Earthing system | Earthing connections are missing from some panels. Termination bars are not being used to connection earth cable in panels where there is earthing. | Hire a qualified and experienced electrical engineer to carry a full design of an earthing system for the entire building and submit to Pakistan Accord for review. An entirely new earthing systems shall be designed and installed across the facility. | E5 + 3 months | We have consulted with an electrical engineer and testing the earthing (grounding) reading that is a crucial first step to ensure safety and proper functioning of electrical systems. After confirming that the earthing values are within the safe range, we can proceed for the final earthing with all equipments. and will submit report accordingly. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Hot Spots | Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 1 month | We have consulted a qualified electrical engineer and as per the recommendation we will start working to Replace the affected cables, Breakers Tightening loose connections and addressing overloaded circuits . |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. | Inspect the electrical equipment fed from the panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, replacing faulty components, or be moved to alternative phase to address neutral imbalance. | 1 month | We have consulted a qualified electrical engineer and as per the recommendation we will start working to Replace the affected cables Breakers Tightening loose connections and addressing overloaded circuits . |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Hot Spots | Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. | Create a schedule to have a thermographic survey carried out by a training person on the entire electrical system at intervals of no less than 6 months. | E7 + 6 months | We have consulted a qualified electrical engineer and as per the recommendation we will start working to Replace the affected cables Breakers Tightening loose connections and addressing overloaded circuits . After that activities we will proceed for the thermographic survey to get the best results. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. Also noted direct feeding of equipment wires into an electrical outlet without the presence of a proper socket. | Replace the affected cables with -continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or -use joint boxes and appropriate connectors to joint cables. | 3 months | We have aligned the internal team to prepare a assessment regarding affected cable issues , joint connections etc. we will start to replace all affected cables and ensure to meet the requirements. In consultation with a qualified engineer. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. Also noted direct feeding of equipment wires into an electrical outlet without the presence of a proper socket. | Enclose and protect any exposed wires using conduit, cable trunking, or other appropriate means to prevent contact and minimize the risk of electrical shock. | E10 + 1 month | We have aligned internal team to list out all the gaps regarding the said issues and take action as per the recommendation of our electrical consultant. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. Also noted direct feeding of equipment wires into an electrical outlet without the presence of a proper socket. | Install a socket outlet suitable for the equipment's electrical requirements. Securely terminate and connect the equipment wires to the newly installed socket outlet. Ensure that wiring is properly insulated, color-coded, and follows standard electrical practices. | E11 + 1 month | We have aligned the internal team to prepare a assessment regarding affected cable issues , joint connections etc. we will start to replace all affected cables and ensure to meet the requirements. In consultation with a qualified engineer. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Cabling & Wiring | Cables support and protection | Combustible material found very close to multiple electrical switches and on trunking. | Remove all combustible material from within and around all electrical devices and trunking in the facility & Ensure that all electric circuitry is clear of combustible materials. | 1 month | We have removed all combustible material from within and around all electrical devices and trunking in the facility. And will ensure in the future that all electric circuitry is clear of combustible materials. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | There are signs of distress at the cable termination, indicating sustained and persistent high temperatures at breaker and cables. Panel is damaged, showing visible signs of wear and deterioration | Equipment should be isolated from the electrical distribution system (turned off). If the equipment is required to operate it should be replaced before doing so. | 2 months | We have consulted a qualified engineer and as per the recommendation we are checking the breaker conditions and load on it . After this activities we will change or improve system accordingly. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Loop Connection | There is cross-circuiting (Looping, Bunching at Molded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. | For any future work avoid looping and bunch of cable at MCCB/MCB or bus bar terminal, use individual circuit and overcurrent device for every incoming and outgoing circuit at the distribution boards | 1 month | We have consulted a qualified engineer and as per the recommendation we are working on it. For the first step we are checking the current system and how to improve or change the installation gradually with production process. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Loop Connection | There is cross-circuiting (Looping, Bunching at Molded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels. | 1 month | We have consulted a qualified engineer and as per the recommendation we are working on it. For the first step we are checking the current system and how to improve or change the installation gradually with production process. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Cabling & Wiring | Cables support and protection | Protection is not provided to prevent damage to hanging cables. | Secure all cable to a method of cable containment (for example cable tray). | 2 months | We are working on it . |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Cabling & Wiring | Cables support and protection | Cables to sewing machine are under tension | Reposition the sewing machine or the socket to reduce the tension on the cable. Ensure that there is enough slack in the cable to prevent it from being under tension | E17 + 1 month | We are working to change the cables under tension or change the location of the machines to remove that cable tension. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Lint & dust inside panel board | It was noted in several locations that the cleanliness was not being maintained | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. | 1 month | We have started maintenance and cleaning schedule and our internal team looks after it. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L00 - Ground Floor: Busbars missing from electrical panel which can cause electric shock, burns, fire or explosion | Install busbar in electrical panel for power distribution | 1 month | We have consulted a qualified electrical engineer. And as per the recommendation we working on it. We will check the feasibility to update electrical panels with the production challenges. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | Main Building on level(s) L03 - 3rd Floor: No lugs or earthing in panel, cleanliness was not being maintained, cable colours are not correct | Earthing connections should be provided for all panels, using proper clamps, lugs, and bolts, to connect the earth continuity conductor to the earth electrode. This will ensure that the panels are effectively earthed and will not become live in case of a fault. | E21 + 1 month | We are testing the earthing (grounding) reading that is a crucial first step to ensure safety and proper functioning of electrical systems. After confirming that the earthing values are within the safe range, you can proceed for the final earthing with all equipments. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Openings | Main Building on level(s) L03 - 3rd Floor: No lugs or earthing in panel, cleanliness was not being maintained, cable colours are not correct | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 2 months | We have aligned our internal team to address this issue . Gradually our team will work on panels by ensuring other ongoing activities. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Cabling & Wiring | Colour coding | Main Building on level(s) L03 - 3rd Floor: No lugs or earthing in panel, cleanliness was not being maintained, cable colours are not correct | Install correct cable colours to electrical equipment (red, yellow, blue) | 1 month | We have aligned our internal team to address this issue . Gradually our team will work on panels by ensuring other ongoing activities. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | DBs & Elec Protection Systems | Circuit breakers | Main Building on level(s) L03 - 3rd Floor: Cable connection size to breaker is incorrect and cable requires protection (2.5mm2 cable to 32A breaker) | Replace cables with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 1 month | We have consulted a qualified electrical engineer and as per the recommendation we will start working to Replace the affected cables Breakers Tightening loose connections and addressing overloaded circuits . |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Earthing system | Main Building on level(s) L03 - 3rd Floor. Fan casing is not earthed. | Earthing cables should be extended from panels to sockets and equipment, using a suitable size and type of conductor, to provide a low-resistance path for fault currents to flow to the earth. This will ensure that any exposed metal parts of the electrical system are at the same potential as the earth and will not cause electric shock to anyone who touches them. | 1 month | We are testing the earthing (grounding) reading that is a crucial first step to ensure safety and proper functioning of electrical systems. After confirming that the earthing values are within the safe range, you can proceed for the final earthing with all equipments. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | DBs & Elec Protection Systems | Earthing system | Main Building on level(s) L03 - 3rd Floor. Fan casing is not earthed. | Hire a qualified and experienced electrical engineer to carry a full design of an earthing system for the entire building and submit to Pakistan Accord for review. An entirely new earthing systems shall be designed and installed across the facility. | 1 month | We are testing the earthing (grounding) reading that is a crucial first step to ensure safety and proper functioning of electrical systems. After confirming that the earthing values are within the safe range, you can proceed for the final earthing with all equipments. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) M01 - Mezzanine: Floor Boxes are not earthed. Cleanliness was not being maintained in the floor boxes | Ensure that floor boxes are cleaned, inspected, and free from dust and dirt. Seal all openings in floor boxes (using plates and cable glands) to prevent the ingress of dust and dirt. | 1 month | We are testing the earthing (grounding) reading that is a crucial first step to ensure safety and proper functioning of electrical systems. After confirming that the earthing values are within the safe range, you can proceed for the final earthing with all equipments. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | DBs & Elec Protection Systems | Earthing system | Main Building on level(s) M01 - Mezzanine: Floor Boxes are not earthed. Cleanliness was not being maintained in the floor boxes | Earthing cables should be extended from panels to equipment, using a suitable size and type of conductor, to provide a low-resistance path for fault currents to flow to the earth. This will ensure that any exposed metal parts of the electrical system are at the same potential as the earth and will not cause electric shock to anyone who touches them. | 2 months | We are testing the earthing (grounding) reading that is a crucial first step to ensure safety and proper functioning of electrical systems. After confirming that the earthing values are within the safe range, you can proceed for the final earthing with all equipments. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L02 - 2nd Floor: Cable trays are bending due to cable weight | Install cable tray supports along the entire cable tray to prevent further deformation | 2 months | We have planned the replacement of bent cable tray and checking the feasibility to work on it as per production challenges. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L00 - Ground Floor: Exposed live connections on the generator batteries | Cover electrical connections using suitable insulating material. | 1 month | We have covered electrical connection using suitable insulating material. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L00 - Ground Floor: Indoor electrical equipment located externally | All external electrical items to be IP rated, add weatherproof cover to equipment. | 3 months | We have provided weatherproof cover to the equipment. |  |  |  | Pending Verification
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) L00 - Ground Floor: It was noted that cleanliness was not being maintained in the electrical room and in the electrical panels in the room | Initiate a regular maintenance and cleaning schedule for the electrical room and panel. Ensure that the electrical room and panels are cleaned, inspected, and free from dust and dirt. | 2 months | We have started maintenance and cleaning schedule and our internal team looks after it. |  |  |  | Pending Verification
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | DBs & Elec Protection Systems | Lint & dust inside panel board | Main Building on level(s) L00 - Ground Floor: It was noted that cleanliness was not being maintained in the electrical room and in the electrical panels in the room | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 2 months | We have started maintenance and cleaning schedule and our internal team looks after it. |  |  |  | Pending Verification
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 2 months | We have aligned our internal team to address this issue . Gradually our team will work on panels by ensuring other ongoing activities. |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Cabling & Wiring | Cables support and protection | the Main Building on level(s) L00 - Ground Floor: Electrical cables in panel were not installed correctly | Secure all cable to a method of cable containment | 2 months | We have consulted with a qualified engineer to address all the electrical issues. And as per the recommendation we are taking steps to re install the improper wirings. Our internal team will work on it. |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Diagrams & Drawings | Electrical layout drawing | An electrical load balance document was not available during the inspection. The absence of an electrical load balance document during an inspection indicates that there might not be a record of the distribution of electrical loads in the factory. This document is crucial as it helps prevent issues like overheating, power-quality problems, and energy loss that can occur with unbalanced loads. | Create an Electrical Load Balance Document: Engage a certified electrical engineer to conduct a thorough assessment of the electrical loads in the factory. This should include all equipment, machinery, lighting, and any other systems that use electricity | 6 months | We have consulted with a qualified electrical engineer to conduct a thorough assessment of the electrical loads in the factory to accurately evaluate energy consumption, identify any inefficiencies, and ensure that our equipment is safely supported by the electrical infrastructure |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Diagrams & Drawings | Electrical layout drawing | An electrical load balance document was not available during the inspection. | Keep the electrical load balance document, the as built drawings and single line diagrams drawings updated and readily available for future inspections. This will ensure that the document can be easily accessed and reviewed during inspections. | 6 months | We have consulted with a qualified electrical engineer to conduct a thorough assessment of the electrical loads in the factory to accurately evaluate energy consumption, identify any inefficiencies, and ensure that our equipment is safely supported by the electrical infrastructure |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Emergency Lighting | No emergency lighting | Emergency lighting throughout all buildings. No emergency lighting provided along external escape routes including walkways and stairways, and insufficient lighting provided throughout, such as: - Main Building on level(s) L02 - 2nd Floor. No external general or emergency lights to the stair - Level 3 where the walkways, stairs and working areas have no emergency lights. | Submit design for an emergency lighting system that meets Accord Pakistan Building Standards for review | 3 months | We are working on it. And will share the design as per target date. |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Emergency Lighting | No emergency lighting | Emergency lighting throughout all buildings. No emergency lighting provided along external escape routes including walkways and stairways, and insufficient lighting provided throughout | Provide emergency lighting in accordance with Pakistan Building Code and NFPA 101 | 3 months | We have listed out the areas where emergency lighting is required. Our internal team is working with a qualified electrical engineer for the installation and wiring of lighting system as per requirement. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The building has no automatic detection and alarm system. There is a button in a centralized location which sends an audible signal throughout the facility, which is typically used to indicate lunch time and end of the workday. Factory management said this is also used as a manual fire alarm in the event of a fire. It is unclear if the buttons throughout the facility marked ‘fire alarm’ would operate this system as well. 1. Sounders inaudible due to low volume or high ambient noise. - No audibility from manual alarm on roof and Level 2 and 3 - Low audibility on south side of Level 1 and in fabric store, fabric department and sampling on Ground Level 2. Additionally, there were some standalone battery-operated smoke detectors in the facility. | Fire detection and alarm system in the building shall be provided that complies fully with NFPA 72 and BCP Clause 9.7.1.1 & 9.7.1.2, with approved and listed equipment. | 3 months | We have contacted with fire safety vendors to get the site surveyed by the fire team to get the quotation and feasibility of installation as per NFPA 72 and BCP clause. At first we will work on drawing as per NFPA 72. |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The building has no automatic detection and alarm system (FADS). There is a button in a centralized location which sends an audible signal throughout the facility, which is typically used to indicate lunch time and end of the workday, also used as a manual fire alarm in the event of a fire. Also: 1. Sounders inaudible due to low volume or high ambient noise. - No audibility from manual alarm on roof and Level 2 and 3 - Low audibility on south side of Level 1 and in fabric store, fabric department and sampling on Ground Level 2. Some standalone battery-operated smoke detectors in the facility. | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | We have contacted with fire safety vendors to get the site surveyed by the fire team to get the quotation and feasibility of installation as per NFPA 72 and BCP clause. Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E10 + 1 months | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E11 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E12 + 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E45 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E12 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E46 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E13 + 3 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
28-Nov-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Knittex Garments, Plot # 103, Sector 15, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 28-Nov-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 2 weeks | Factory will remove all locking devices from doors on all egress routes that could prevent opening from inside |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Factory will purchase and fit easily opening mechanisms on doors on exit routes, complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5y. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Doors on all escape routes, including those leading to outside or away from the building, must swing in the direction of travel to an emergency exit. A door to the interior stair was observed to swing in the wrong direction (inwards) on Level 2. | Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard | 3 months | We are planning to order new door as per requirement and it is in progress. Moreover , all the inward opening door (if any) will be replaced accordingly. Factory will amend doors to ensure that are side swinging and open in the direction of travel to an exit |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Sliding exit doors observed where only swinging doors provide an acceptable level of risk. Several sliding doors were observed throughout the facility, especially from Levels 1, 2, and 3 | Replace sliding door(s) or provide pocket door in existing sliding panel, with side hung swinging door(s) which swing in the direction of egress travel | 3 months | We are removing the slider doors and will install door as per the requirements. We have initiated a survey of door makers to check the feasibility that how can we use existing doors and effectively meet the requirements as well. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Number of exits | There are areas where a single means of egress is provided, but more than one means of escape is required. This was observed on the roof, Level 1 female toilet (single exit is a spiral stair not separated from the boiler and generator below), Ground Level security guard rest area, and female prayer / rest mezzanine. | Provide alternative means of egress from the areas identified to ensure there are sufficient number of exits and sufficient exits to accommodate the occupant load and travel distance requirements, in accordance with the Pakistan Accord Building Standard | 4 months | We are working to make the feasibility of two egress. And we will ensure accordingly. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Exit access | Separation of exits in on Level 2 and 3. The two exits available are not sufficiently separated from each other. Exit access shall be arranged so that the distance between exits is not more than one half of the diagonal dimension of the area (buildings that are not protected by an automatic sprinkler system | Propose modification to existing means of escape to provide an acceptable level of safety, or alternatively an additional protected exit stair to meet the required distance between emergency exits. Submit proposals to Pakistan Accord for review. | 4 months | We are in process to finalize the feasibility of the exit issue. As we have less options to manage the requirement but still we are finding ways as per our legal obligations and utilizing existing space. Factory will prepare drawings showing proposal for protecting access to building exit or alternative arrangement to ensure safe egress from internal stairway and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Exit access | Separation of exits in on Level 2 and 3. The two exits available are not sufficiently separated from each other. Exit access shall be arranged so that the distance between exits is not more than one half of the diagonal dimension of the area (buildings that are not protected by an automatic sprinkler system | Implement modifications or provide an additional exit stair in accordance with Pakistan Accord Building Standard | F6+ 4 months | We are in process to finalize the feasibility of the exit issue. As we have less options to manage the requirement but still we are finding ways as per our legal obligations and utilizing existing space. Factory will provide protection or alternative arrangement to allow safe passage from internal stair to outside, in accordance with proposals submitted previously to Accord for review |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Automatic door closers are not installed/functioning in several locations - Doors normally required to be kept closed are secured in the open position by being tied open or by obstructions being wedged between the door and door frame. | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as needed. | 2 weeks | We have ordered to install new door as per requirement and it is in progress. Moreover , all the inward opening door (if any) will be replaced accordingly. We will ensure all the highlighted requirements. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Combustible materials stored in stairway | Remove all chemicals and combustible materials stored in stairways. | 2 weeks | We have removed all the materials stored in stairways. |  |  |  | Pending Verification
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors - Lift shafts which are not protected by fire and smoke resistant construction and are open into protected escape stairs. - Exit stairway exposed to unprotected openings - Automatic door closers are not installed/functioning in several locations | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge. | 4 months | We are in contact with fire safety vendor to get the feasibility of the work in view of our existing structure. How much we can adjust or meet the requirements. Factory will prepare drawings showing proposed fire separating construction and door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings:. - Exit stairway exposed to unprotected openings | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. - All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. | F10 + 4 months | We are working to replace all doors at emergency exits , once we will will start installing new door , the same requirement will be fulfilled. Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed on Level 3 where exit access from production area through storage area. | Propose modifications to exit from production areas without having to pass through other higher risk areas and submit to Pakistan Accord for review | 4 months | We are working to readjust or provide new provision of exits at all highlighted locations. We will share final plan of exits once feasibility checks have been completed. Factory will prepare drawings showing proposal for protecting access to building exit or alternative arrangement to ensure safe egress from internal stairway and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed on Level 3 where exit access from production area through storage area. | Arrange exit access so that it is not necessary to pass through any hazardous areas as per Pakistan Accord Building Standard | F12 + 4 months | We are working to readjust or provide new provision of exits at all highlighted locations. We will share final plan of exits once feasibility checks have been completed. Factory will provide protection or alternative arrangement to allow safe passage from internal stair to outside, in accordance with proposals submitted previously to Accord for review |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm which was observed throughout most of the office mezzanine above Ground Level as well as from the bathroom on the roof and the female prayer / rest area mezzanine. | Provide headroom height safety signage and propose other safety measures to ensure safe passage where clearance height is less than 2.05 m on the escape route. | 1 months | We have provided safety signage and installed foamic material to avoid any direct contact with the low clearance height. However , more modification cannot be made due to the beam or column has been passing by the location . But still we are finding ways for safe emergency routes. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm which was observed throughout most of the office mezzanine above Ground Level as well as from the bathroom on the roof and the female prayer / rest area mezzanine. | Propose design modifications to ensure a safe passage where clear headroom on the escape route is insufficient or propose alternative paths that comply with Pakistan Accord Standard and BCP 10.5 and present to Pakistan Accord for review. | 4 months | We have provided safety signage and installed foamic material to avoid any direct contact with the low clearance height. However , more modification cannot be made due the beam or column has been passing by the location . But still we are finding d ways for safe emergency routes. Factory will prepare drawings showing proposal for arrangement to ensure safe egress along exit paths and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm which was observed throughout most of the office mezzanine above Ground Level as well as from the bathroom on the roof and the female prayer / rest area mezzanine. | Implement proposals previously reviewed to provide safe passage from areas where clear headroom is not sufficient to ensure safe passage in the event of an emergency | F15 + 4 months | We have provided safety signage and installed foamic material to avoid any direct contact with the low clearance height. However , more modification cannot be made due the beam or column has been passing by the location . But still we are finding d ways for safe emergency routes. Factory will implement arrangement to allow safe passage, in accordance with proposals submitted previously to Accord for review |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Travel distance | The common path of travel exceeding the limit of 15 m (50 occupants or more) on Level 2 and 3 where the common path of travel is was measured to be almost 50m. | Propose alternative exiting arrangements to limit travel distances and submit to Pakistan Accord for review. | 4 months | We are in process to finalize the feasibility of the exit issue. As we have less options to manage the requirement but still we are finding ways as per our legal obligations and utilizing existing space. Factory will prepare drawings showing proposal for reducing travel distance to exits to within limits and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Travel distance | The common path of travel exceeding the limit of 15 m (50 occupants or more) on Level 2 and 3 where the common path of travel is was measured to be almost 50m. | Provide alternative exiting arrangements to limit the travel distances to be in accordance with the Pakistan Accord Building Standard. | F17 + 4 months | We are in process to finalize the feasibility of the exit issue. As we have less options to manage the requirement but still we are finding ways as per our legal obligations and utilizing existing space. Factory will provide additional exits or alternative arrangement reduce travel distance to within limits, in accordance with proposals submitted previously to Accord for review |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. The following is a non-exhaustive list of issues observed during the inspection - Exit discharge pathways from interior and exterior stairways to public way are exposed to unprotected openings. Exit discharge pathways on the east side of the building are especially susceptible to exposure because of their narrow widths. | Remove exterior storage within 3.05m horizontally and vertically of unprotected openings in such a way so that do not interfere with exit discharge route clear widths. | 4 months | We are working to close the unprotected opening on all exits routes. And we are making arrangement to remove exterior storage within 3.05 m horizontally and vertically of unprotected openings . |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. The following is a non-exhaustive list of issues observed during the inspection - Exit discharge pathways from interior and exterior stairways to public way are exposed to unprotected openings. Exit discharge pathways on the east side of the building are especially susceptible to exposure because of their narrow widths. | Propose means for providing protected routes of two escape stairs away from the building and submit to the Pakistan Accord for review | F19 + 4 months | We are in process to finalize the feasibility of the exit issue. As we have less options to manage the requirement but still we are finding ways as per our legal obligations and utilizing existing space. Factory will prepare drawings showing proposed protection to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification work. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. The following is a non-exhaustive list of issues observed during the inspection - Exit discharge pathways from interior and exterior stairways to public way are exposed to unprotected openings. Exit discharge pathways on the east side of the building are especially susceptible to exposure because of their narrow widths. | Protect exit route at exterior of the building from unprotected openings to allow a safe, free and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standard | 8 months | We are working to close the unprotected opening on all exits routes. And we are making arrangement to remove exterior storage within 3.05 m horizontally and vertically of unprotected openings . Factory will ensure external exit discharge routes are adequately fire separated from the rest of the building |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Means of Escape | Escape stair condition | Handrails are not provided or are defective on one or both sides of exit stairs, which can cause falls during evacuation | Provide handrails on both sides of emergency exit stairs in accordance with Pakistan Accord Building Standard | 2 months | We are working to install handrails on all the stairs. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Means of Escape | Escape stair condition | Stairways serving escape path components not being wide enough. One of the exterior stairways from Level 1 is less than 560mm wide. In existing buildings, the width of exit access shall be permitted to be not less than 710 mm | Submit proposals for design of means of escape to show adequate capacity for the maximum number of occupants from all areas and submit to Pakistan Accord for review. | 4 months | We are in process to finalize the feasibility of the exit issue. As we have less options to manage the requirement but still we are finding ways as per our legal obligations and utilizing existing space. We will share designs accordingly. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Means of Escape | Escape stair condition | Stairways serving escape path components not being wide enough. One of the exterior stairways from Level 1 is less than 560mm wide. In existing buildings, the width of exit access shall be permitted to be not less than 710 mm | Rearrange means of escape to provide sufficient exit capacity with sufficient width from all areas of the building. | F23 + 4 months | We are in process to finalize the feasibility of the exit issue. As we have less options to manage the requirement but still we are finding ways as per our legal obligations and utilizing existing space. We will share designs accordingly. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Means of Escape | Exit signage | It was observed that there is insufficient exit signage throughout the facility. | Remove any misleading exit signage and/or floor markings and provide exit signage so access to exits are marked by approved readily visible signs along full length of the escape route | 2 weeks | We have corrected and posted right exit signage . |  |  |  | Pending Verification
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Means of Escape | Exit signage | It was observed that there is insufficient exit signage throughout the facility. | Provide exit signage so access to exits are marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | 4 months | We have corrected and posted right exit signage . |  |  |  | Pending Verification
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Separation of shafts | Per Pakistan Accord Standard, shafts should be enclosed in 2 hour fire resisting construction with 90 minutes fire rated doors. The following deficiencies have been observed on site, including (list not exhaustive): - Lift shafts which penetrate floor that are not protected by fire and smoke resistant construction. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | We will work on it and installed as lift shaft as per the requirement. And will share the design accordingly. Factory will prepare drawings showing proposed fire separating construction to shafts, with details of door assembly, location in relation to escape routes and lift door operation, and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Rated Construction | Separation of shafts | Lift shafts which penetrate floor that are not protected by fire and smoke resistant construction | Separate lift shaft by fire-rated construction with fire rated opening protective assemblies, in accordance with the previously reviewed design proposal | F27 + 4 months | We will work on it and installed as lift shaft as per the requirement. And will share the design accordingly. Fire rated separation of shaft will be completed, including brickwork/ fire rated assemblies and adequate and door operating mechanism, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required. Observations relate to the chute openings in fire-rated floor assemblies, two of which connect three floors and the third chute connects two floors | Maintain fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure Submit design documentation to the Pakistan Accord giving proposals for providing fire protection to openings between floors. | 4 months | We are working to close out or seal the openings with the fire rated enclosure. And will submit design accordingly. Factory will prepare drawings showing proposed fire separating construction to floor openings, and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required. Observations relate to the chute openings in fire-rated floor assemblies, two of which connect three floors and the third chute connects two floors | Provide fire protection to floor openings that meet the requirements of the Pakistan Accord Building Standard. | F29 + 4 months | We are working to close out or seal the openings with the fire rated enclosure. And will submit design accordingly. Fire rated separation of shaft will be completed, including brickwork/ fire rated assemblies and adequate and door operating mechanism, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Different occupancy types not separated by fire and smoke resisting construction were observed between office and production areas and rest/prayer area and production areas | Propose design and layout showing how different occupancies can be rearranged and/or enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | We are working on it and will submit design accordingly. Factory will prepare drawings showing proposed fire separating construction between occupancies and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Different occupancy types not separated by fire and smoke resisting construction were observed between office and production areas and rest/prayer area and production areas | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies. | 4 months | We are working on it and will submit design accordingly. Fire rated separation of occupancies will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Different occupancy types not separated by fire and smoke resisting construction were observed between office and production areas and rest/prayer area and production areas | Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | F33 + 4 months | We are working on it and will submit design accordingly. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Storage | Per Pakistan Accord Standard, extensive storage areas need to be fire separated from the rest of the building using 2 hour fire resisting walls with 90 minutes fire rated doors. Limited in-process storage is permitted in production areas, subject to meeting all of the following criteria (unsprinklered building): - Combined storage areas do not exceed 10% of the production floor area, - Storage height is less than 2.45m, - Storage areas are grouped into islands not exceeding 23 m2, and - Islands are separated from other storage islands by at least 3m gap. The following deficiencies have been observed on site, including (list not exhaustive): - Areas where storage did not appear to meet miscellaneous storage requirements - Storage areas are not fire separated from the rest of the building - Storage areas on production floor exceed permitted limits in Accord standard | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | We are checking feasibility to readjust as per requirement. And we are evaluating and taking suggestion from production team to address this issue and manage floor accordingly. Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Storage | Miscellaneous (in process) storage in non-storage occupancies, where - storage areas exceed 10 percent of the floor area, meaning it is not accessory to the other occupancy type - storage areas exceed 2.45m (8ft) in height (non-sprinklered buildings) - storage areas exceed 23m² (250ft²) in one area (non-sprinklered buildings) - storage areas are not separated from other storage areas by at least 3m (10ft) - Storage occupancies are not separated from other occupancies, such as offices and production areas | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F34 + 4 months | We are checking feasibility to readjust as per requirement. And we are evaluating and taking suggestion from production team to address this issue and manage floor accordingly. Factory will mark up areas designated for in-process storage on floors Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Electrical room not separated by fire and smoke resisting construction | Separate electrical room by 2-hr fire rated construction | 4 months | We have seperated and rearranged our main panel room and we are also working for other locations to meet the requirement. Fire rated door installation is in process. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Rooms with boilers and/or steam generators not separated by fire and smoke construction | Separate room with boiler(s) and/or steam generator(s) by 2-hr fire rated construction | F36 + 4 months | We are working on it to separate it by 2 hrs fire rated construction. |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Generator room not separated by fire and smoke resisting construction | Separate generator room by 2-hr fire rated construction | 8 months | We are working on it to separate it by 2 hrs fire rated construction. |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Hazardous Materials | Diesel storage | Storage of flammable and combustible liquids and/or solids: - Diesel storage is only permitted within generator rooms and fire pump rooms if adequately stored and that room is separated from adjacent occupancies - Interior diesel storage (maximum 1265 litres on ground level) is permitted if it is fire separated from other areas by 1-hr fire rated construction and stored in accordance with other requirements of NFPA 30 | Propose measures for diesel storage at ground level that meet fire rated separation and other requirements of NFPA 30. Submit to Pakistan Accord for review | 4 months | We are making arrangements to store as per the requirement. |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Hazardous Materials | Diesel storage | Storage of flammable and combustible liquids and/or solids: - Diesel storage | Implement measures to ensure compliance with fire protection and other requirements of NFPA 30 | 4 months | We are making arrangements to store as per the requirement. |  |  |  | Pending Verification
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Hazardous Materials | Gas storage | Storage gas cylinders within the building envelope serving as backup fuel for the boilers: Up to two (2) gas cylinders (each 50 kg maximum) are permitted to be stored in an interior control area if the cylinders are adequately secured and the room is appropriately ventilated and protected as per NFPA 58. Ventilation must be direct to outside meaning the room needs to have at least one exterior wall, which cannot be adjacent to exterior exits or exterior exit discharge pathways. Protection refers to 2-hr fire rated separation of the room with cylinders and assuring the cylinders and their storage room is not within 3.05 meters of an escape route or exit | Provide area for safe storage of gas cylinders complying with requirements of NFPA 58 | 4 months | We are making arrangements to store as per the requirement. |  |  |  | Pending Verification

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
28-Nov-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Knittex Garments, Plot # 103, Sector 15, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 28-Nov-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Structural Design | Non-engineered structure | This relates to the upper roof level. Upper roof steel structure appears not to have had engineering input in the design and construction. Steel beams have deformed under the light-weight roof deck load and there is no apparent lateral stability system. | Structural engineer to carry out an assessment of the structural stability of the roof , with calculations and propose additional reinforcement and stability system, if required. Submit proposal for any remedial works if necessary to Pakistan Accord for review. | 3 months | We have consulted with a structural engineer to carry out the assessment . For our first step we are working to get the following reports. 1. Soil testing 2. Core testing After getting these reports we will take further actions. Furthermore , additional reinforcement or stability assessment will also be done and we will share proposal for any remedial work with Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Structural Design | Non-engineered structure | This relates to the upper roof level. Upper roof steel structure appears not to have had engineering input in the design and construction. | Carry out the remediation works, if required. | S1 + 3 months | We have consult with a structural engineer to carry out the assessment . We will carry out remediation work after getting the recommendations. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Transfer beams | This relates to the transfer beams picking up off-grid columns at 1st floor level. Based on an initial assessment, the RC transfer beams at the 1st floor level appear to be overstressed under the applied load. | - Building Structural Engineer to review design, loads and transfer beams stresses in area identified below. - Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the identified beams. - Submit concrete strength data to Pakistan Accord for review. - Submit the design assessment and the proposed remedial works if required to Pakistan Accord for review. | 3 months | We have consult with a structural engineer to carry out the assessment . For our first step we are working to get the quotation of the following 1. Soil testing 2. Core testing After getting these reports we will take further actions. Furthermore , additional reinforcement or stability assessment will also be done and we will share proposal for any remedial work with Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Transfer beams | This relates to the transfer beams picking up off grid columns at 1st floor level. Based on an initial assessment, the RC transfer beams at the 1 st floor level appear to be overstressed under the applied load. | - Carry out remediation works as required. - Review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to current or remediated floor and column capacity. | S3+ 3 months | We have consult with a structural engineer to carry out the assessment . For our first step we are working to get the quotation of the following 1. Soil testing 2. Core testing After getting these reports we will take further actions. Furthermore , additional reinforcement or stability assessment will also be done and we will share proposal for any remedial work with Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Other Damage/Defects | Brickwork instability | This relates to the brickwork on the stair core on the north-west side of the building. From the visual inspection, the wall appears to be bulging out and that may be due to the slenderness of the panel under gravity loads and could become overstressed under lateral wind load conditions. | - Building Engineer to review the design of wall for the gravity and wind loads. - Verify the thickness and buildup of the wall and assess the structural stability of the wall panel. - Submit justification of wall panel stability, with remedial works if required, to Pakistan Accord for review before implementing any remedial works. | 3 months | We have consulted with a structural engineer to carry out the assessment . We are in process to get recommendation , we will work on it accordingly. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Brickwork instability | This relates to the brickwork on the stair core on the north-west side of the building. | Provide additional restraint to the wall panel if necessary. | S5+ 3 months | We have consulted with a structural engineer to carry out the assessment . We are in process to get recommendation , we will work on it accordingly. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural System | Lateral stability system | This relates to the lower roof level steelwork. No apparent bracing system in the horizontal plane for the lower roof steelwork. | - Building Engineer to assess whether existing lateral restraint mechanisms are sufficient to resist all anticipated lateral loading on the lower roof steel structure - Propose the remedial works, if required, and submit to Accord for review. | 3 months | We are working to reinforce the steel structure and after getting recommendation form the structural engineer we will proceed accordingly. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural System | Lateral stability system | This relates to the lower roof level steelwork. No apparent bracing system in the horizontal plane for the lower roof steelwork. | Implement any remedial works required in accordance with Pakistan Accord Standard. | S7 + 4 months | We are working to reinforce the steel structure and after getting recommendation form the structural engineer we will proceed accordingly. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Loading | Uncontrolled loading | This relates to a number of floors in the building. Loading observed in some areas on 1st and 4th Floors appeared excessive and not taking into account the design load of the supporting structure. There were no safe loading indicators noted on these floors, and no safe load plans seen anywhere in factory. | Building Engineer to produce loading plans for all floors within the factory. Loading plans are to be displayed on the walls of each floor level. Loading to be actively managed by Factory Management. | 3 months | We have consult with a structural engineer to carry out the assessment . For our first step we are working to get the quotation of the following 1. Soil testing 2. Core testing After getting these reports we will take further actions. Furthermore , additional reinforcement or stability assessment will also be done and we will share proposal for any remedial work with Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Structural Design | Drawings differ from as-built | Structural as-built drawings to be updated. | Building Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | we are working on taking quotation for the activity , moreover , we have consulted with a structural engineer to carry out the work as per engineering standard requirements. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Other Damage/Defects | Corrosion of reinforcement | This relates to the main building at 3rd floor level. A few precast slab tiles were observed to be showing cracks and rusted reinforcement underneath. | - Building Engineer to inspect the areas and propose remedial measures to prevent further corrosion damage to slab. - Complete the remedial works. | 6 months | We have aligned our internal team to work on it. We are in process to inspect the area and feasible action to be taken after the final discussion with structural engineer. |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1