## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
02-May-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Multinational Export Bureau, Plot No. L-10/D & L-11/A, block 22, Sector 22, FB Industrial Area Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | May 2nd, 2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Escape doors are lockable – All emergency exits for stair S-1, 5th floor emergency exit for stair S-3, 3rd floor emergency exit for stair S-5 Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Sliding doors observed - All floors Emergency Exits for stair S-1, 1st floor Main Emergency Exit for S-5 stair | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | We have removed locking devices from all the door. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Escape doors are lockable – All emergency exits for stair S-1, 5th floor emergency exit for stair S-3, 3rd floor emergency exit for stair S-5 Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Sliding doors observed - All floors Emergency Exits for stair S-1, 1st floor Main Emergency Exit for S-5 stair | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | We have removed all the sliding door from means of escape. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Escape doors are lockable – All emergency exits for stair S-1, 5th floor emergency exit for stair S-3, 3rd floor emergency exit for stair S-5 Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Sliding doors observed - All floors Emergency Exits for stair S-1, 1st floor Main Emergency Exit for S-5 stair | Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, which are side swinging and open in the direction of travel to an exit. | 3 months | We have removed all the sliding door from means of escape. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Escape doors are lockable – All emergency exits for stair S-1, 5th floor emergency exit for stair S-3, 3rd floor emergency exit for stair S-5 Non Compliant Locking / sliding door mechanism has been observed in following areas -Examples are: -Sliding doors observed - All floors Emergency Exits for stair S-1, 1st floor Main Emergency Exit for S-5 stair | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | 3 months | We have removed locking devices from all the door. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Fire load in stairs - Basement (Emergency Exit from Basement) chemical storage along exit access & S-2 stairs, Fire load below stair S-3 Unprotected openings into stairs - All floor levels S-5 stairs not protected, 3rd floor – S-4 exit stairs not protected, All floor levels S-1 stairs not protected -Fire doors propped open – All buildings -all floor levels -Doors are not fire doors – All buildings -Stair discharge route is not fire separated from the building – Ground floor all buildings, 4th floor S-3 transition to S-5 is not separated | Remove fire load from stairs | 2 weeks | Factory will remove all storage and other obstacles in emergency escape stairs |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Fire load in stairs - Basement (Emergency Exit from Basement) chemical storage along exit access & S-2 stairs, Fire load below stair S-3 Unprotected openings into stairs - All floor levels S-5 stairs not protected, 3rd floor – S-4 exit stairs not protected, All floor levels S-1 stairs not protected -Fire doors propped open – All buildings -all floor levels -Doors are not fire doors – All buildings -Stair discharge route is not fire separated from the building – Ground floor all buildings, 4th floor S-3 transition to S-5 is not separated | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and approval prior to rectification works. The drawings should cover: -Layout showing the location of fire rated walls/doors to protect the stairs. -Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). -Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | Factory will prepare drawings showing proposed fire separating construction and door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Fire load in stairs - Basement (Emergency Exit from Basement) chemical storage along exit access & S-2 stairs, Fire load below stair S-3 Unprotected openings into stairs - All floor levels S-5 stairs not protected, 3rd floor – S-4 exit stairs not protected, All floor levels S-1 stairs not protected -Fire doors propped open – All buildings -all floor levels -Doors are not fire doors – All buildings -Stair discharge route is not fire separated from the building – Ground floor all buildings, 4th floor S-3 transition to S-5 is not separated | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: -All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not always locked). -All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. -Where stairs discharge within a building, a fire separated corridor shall be provided that leads outside building. Provide all fire doors with self-closing and self-latching devices, and push-bar panic hardware where required in accordance with Pakistan Accord Building Standard. If fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system. -Provide fire-rated separation between staircase enclosure and lift in accordance with the Pakistan Accord Building Standard, implementing the previously approved design proposal. | F6 + 4 months | Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit access | Obstructions on escape route - Building 1– Roof floor & 5Th floor – 0.2 m high step, Building 1– 5th floor slope Elevations on emergency exit , Building 1 – Basement – Emergency access high step -0.28m | Remove obstructions on escape routes and keep them clear for escape | 2 weeks | We have removed all the obstructions from escape routes. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Escape stair condition | There are no handrails-Building 1- Stair S-1– All level stairs without handrails, Building 1-Stair S-5 – 3rd floor Emergency exit stairs without handrails ,Building 1 – Basement Stairs S-7 without handrails & uneven steps can cause slip / trip during emergency exit | Remove all trip hazards from stairs | 2 months | Factory will ensure even surface at stairways to ensure safe use in the event of an emergency |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Escape stair condition | There are no handrails-Building 1- Stair S-1– All level stairs without handrails, Building 1-Stair S-5 – 3rd floor Emergency exit stairs without handrails ,Building 1 – Basement Stairs S-7 without handrails & uneven steps can cause slip / trip during emergency exit | Ensure the following are provided: -Stair structure to be fixed so that stairs are safe for escape. -Ensure all stairs have balustrades. -Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. | 2 months | We have installed handrails on every stairs. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit signage | Missing exit signs at stair discharge routes – Building 1 all stairs - Missing exit signs in production areas – Building 1 - Missing exit signs in offices and back of house areas – Building 1 - Missing exit signs at roof – Building 1 - Electrically powered exit signs are not a tested and listed system – Building 1 | Provide exit signage. Access to exits is marked by approved readily visible signs along the escape route | 2 months | Work in progress |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit signage | Missing exit signs at stair discharge routes – Building 1 all stairs -Missing exit signs in production areas – Building 1 -Missing exit signs in offices and back of house areas – Building 1 -Missing exit signs at roof – Building 1 -Electrically powered exit signs are not a tested and listed system – Building 2 | Provide exit signage. Access to exits is marked by approved, readily visible signs in all areas of the floor and clearly visible at exits. These must comply with BCP 10.15.1, 10.15.2 and 10.15.3 | F11 + 1 month | Factory will provide exit signange in all areas to comply with BCP 10.15.1, 10.15.2 and 10.15.3 |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated -S-1,S-4,S-5 stairs exit discharge routes - Final exit from building is not adequately away to ensure occupant safety – Main assembly point and all main exits of building | Remove obstructions on external escape routes and keep them clear for escape Cover any holes and uneven areas in external escape routes | 1 month | Factory will remove obstructions on external escape routes and keep them clear to allow people to move away from the building exits to a place of safety outside Cover any holes and uneven areas in external escape routes |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated -S-1,S-4,S-5 stairs exit discharge routes - Final exit from building is not adequately away to ensure occupant safety – Main assembly point and all main exits of building | ¬For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge routes. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: -Layout showing the location of fire rated walls/doors to protect stair discharge routes -Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | Factory will prepare drawings showing proposal for protecting access to building exit or alternative arrangement to ensure safe egress from internal stairway and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit access | Exit discharge routes are not fire separated -S-1,S-4,S-5 stairs exit discharge routes - Final exit from building is not adequately away to ensure occupant safety – Main assembly point and all main exits of building | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Accord Building Standard. Some of the key requirements include: -All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into exit discharge routes should be kept closed (but not always locked). -All penetrations through walls into stair discharge routes need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. -Ensure external escape routes are relocated so that they do not pass via high-risk areas. | F14 + 4 months | Factory will provide protection or alternative arrangement to allow safe passage from internal stair to outside, in accordance with proposals submitted previously to Accord for review |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated -S-1,S-4,S-5 stairs exit discharge routes - Final exit from building is not adequately away to ensure occupant safety – Main assembly point and all main exits of building | Ensure external exit discharge routes are adequately fire separated from the rest of the building. Ensure external escape routes do not pass close to unprotected high-risk areas | 8 months | Factory will provide protection on external routes to ensure that people can move safely away from the buolding in the event of emergency |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Safety Management | Records of systems maintenance | The following deficiencies have been observed on site, including (list not exhaustive): - Inadequate records of maintenance of Fire Pumps - Inadequate records of maintenance of Standpipes - Inadequate records of maintenance of Fire Extinguishers - Inadequate records of maintenance of Fire Doors | Prepare maintenance schedule for all life safety systems. | 3 months | We have prepared a maintenance schedule for all safety system, every fire system equipement/devices will be maintain on every 06 months. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Safety Management | Records of systems maintenance | The following deficiencies have been observed on site, including (list not exhaustive): - Inadequate records of maintenance of Fire Pumps - Inadequate records of maintenance of Standpipes - Inadequate records of maintenance of Fire Extinguishers - Inadequate records of maintenance of Fire Doors | Prepare a schedule of proposed system maintenance. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Accord for review and approval. | 3 months | We have prepared a maintenance schedule for all safety system, every fire system equipement/devices will be maintain on every 06 months. Further will discuss in meeting. Factory will share maintenance schedule with Accord for review |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Safety Management | Records of systems maintenance | The following deficiencies have been observed on site, including (list not exhaustive): - Inadequate records of maintenance of Fire Pumps - Inadequate records of maintenance of Standpipes - Inadequate records of maintenance of Fire Extinguishers - Inadequate records of maintenance of Fire Doors | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep maintenance records. | F18 + 3 months | We have prepared a maintenance schedule for all safety system, every fire system equipement/devices will be maintain on every 06 months. Further will discuss in meeting |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Safety Management | Records of system testing | The following deficiencies have been observed on site, including (list not exhaustive): - Inadequate records of testing of Fire Pumps - Inadequate records of testing of Standpipes - Inadequate records of testing of Fire Extinguishers - Inadequate records of testing of Fire Doors | Prepare testing schedule for all life safety systems. | 3 months | We have prepared a maintenance schedule for all safety system, every fire system equipement/devices will be maintain on every 06 months. Further will discuss in meeting |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Safety Management | Records of system testing | The following deficiencies have been observed on site, including (list not exhaustive): - Inadequate records of testing of Fire Pumps - Inadequate records of testing of Standpipes - Inadequate records of testing of Fire Extinguishers - Inadequate records of testing of Fire Doors | Prepare a schedule of proposed system maintenance. -Identify how systems will be tested and who is responsible. -The schedule to be submitted to Accord for review and approval. | 3 months | We have prepared a maintenance schedule for all safety system, every fire system equipement/devices will be maintain on every 06 months. Further will discuss in meeting |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Safety Management | Records of system testing | The following deficiencies have been observed on site, including (list not exhaustive): - Inadequate records of testing of Fire Pumps - Inadequate records of testing of Standpipes - Inadequate records of testing of Fire Extinguishers - Inadequate records of testing of Fire Doors | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep testing records. | F21 + 3 months | We have prepared a maintenance schedule for all safety system, every fire system equipement/devices will be maintain on every 06 months. Further will discuss in meeting |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant- Production Buildings | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, | 4 months | Factory will appoint consultant and submit design documentation for suppression system (SUPS), including sprinkler and standpipe system and supporting infrastructure complying with NFPA 13, NFPA 14, 20, 22, and 24, to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant- Production Buildings | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F23 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant- Production Buildings | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F24 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and proceed with installation |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant- Production Buildings | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F25 + 3 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant- Production Buildings | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F26 + 3 months | Factory will advise Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Standpipe system | The following deficiencies have been observed on site, including (list not exhaustive): - Standpipe outlets are Non listed/ Non-compliant- Production Buildings | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F27 + 3 months = 18 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Suppression | Fire pumps | Fire pump set is not listed – Main fire pump & with negative suction -Jockey pump is not listed -Diesel backup pump is not listed | Prepare design and drawings showing how the fire pump room and equipment will be rectified to comply with NFPA 20 as part of the supporting infrastructure to the SUPS system by following steps (1) to (6) above | 18 months | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Suppression | Sprinkler system | Building-1 sections B, C (24.11m), (20.9m), without sprinkler system, so the entire building needs to be covered by sprinklers | - Submit design documentation for a sprinkler system [along with required standpipe system] and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. by following steps (1) to (6) above | 18 months | Provide sprinkler system as part of the SUPS in compliance with NFPA 13 and reviewed previously by Accord |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Suppression | Water supply | The following deficiencies have been observed on site, including (list not exhaustive): - No separate fire water tank - No dedicated portion of shared water tank for fire safety purposes - Fire tank uses an external reservoir, and the water quality requirements are not met | Develop a rectification plan to provide adequate fire water supplies. The plan should demonstrate compliance with NFPA 22. Submit the plan to Accord for review and approval prior to implementation on site. | 18 months | We have multiple water supplies/tank. Factory will review arrangement of water supply and storage requirements to cover fire water supply as part of supporting infrastructure for the SUPS system, in accordance with NFPA 22 & 24, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Suppression | Water supply | The following deficiencies have been observed on site, including (list not exhaustive): - No separate fire water tank - No dedicated portion of shared water tank for fire safety purposes - Fire tank uses an external reservoir, and the water quality requirements are not met | Implement the plan agreed with Pakistan Accord. | 18 months | Factory will provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Separation of occupancies | Car park areas are not fire separated from the rest of the building – Ground floor - Large office areas not fire separated from the production areas – Building 1- Ground floor - Openings from the production floors to the emergency corridors . (Top floor to 1st floor) - No fire door installed between Canteen and production area at 3rd Floor building 1-Section D. No separation between Female rest room & childcare room from production area at 2nd Floor. - No separation between Basement floor from Ground floor office. - Multiple openings of Chutes in building 1– interconnecting different floors | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: -Different occupancy types in the building -Proposed fire separation details (including fire rating of walls and doors) | 4 months | Factory will prepare drawings showing proposed fire separating construction between different occupancies and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Separation of occupancies | Car park areas are not fire separated from the rest of the building – Ground floor - Large office areas not fire separated from the production areas – Building 1- Ground floor - Openings from the production floors to the emergency corridors . (Top floor to 1st floor) - No fire door installed between Canteen and production area at 3rd Floor building 1-Section D. No separation between Female rest room & childcare room from production area at 2nd Floor. - No separation between Basement floor from Ground floor office. - Multiple openings of Chutes in building 1– interconnecting different floors | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F33 + 4 months | Fire rated separation between occupancies will be completed where necessary, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Storage | Combined storage areas are not fire separated from the rest of the building (Building 1-4th floor, Building 1- 1st floor, Building 1-5th floor), Building 1 – 3rd floor Production and storage area not separated | Identify all designated storage areas. For all storage areas where storage cannot be managed within in-process storage limitations described above, prepare drawings showings proposed fire separation details of storage areas. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: -Locations of fire rated walls and doors. -Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Storage | Combined storage areas are not fire separated from the rest of the building (Building 1-4th floor, Building 1- 1st floor, Building 1-5th floor), Building 1 – 3rd floor Production and storage area not separated | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | F35 + 4 months | Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Separation of high-risk areas | Steam generator rooms are not enclosed in minimum 3m high sturdy construction to separate them from occupied areas – All steam generators Steam generator rooms do not have a permanent opening outside the building – All steam generators – 3rd floor and 4th floor ,Ground floor Fire pump room is not fire separated from the rest of the building (Main Fire pump)- Building # 1 section C – Ground floor No fire separation of fire pump -Electrical rooms are not fire separated (High voltage electric panels in all buildings) -Generator room is not fire separated (Building 1 -Diesel Generator not separated) | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: Separation to electric steam generator up to 3 m above the finished floor level. This should be achieved using reinforced concrete / masonry walls with a solid steel door. -The door must have a self-closer and a positive latch. -Blast vent should be provided to outside the building. | 4 months | Factory will prepare drawings showing proposed fire separating construction to high-risk areas and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Rated Construction | Separation of high-risk areas | Steam generator rooms are not enclosed in minimum 3m high sturdy construction to separate them from occupied areas – All steam generators Steam generator rooms do not have a permanent opening outside the building – All steam generators – 3rd floor and 4th floor ,Ground floor Fire pump room is not fire separated from the rest of the building (Main Fire pump)- Building # 1 section C – Ground floor No fire separation of fire pump -Electrical rooms are not fire separated (High voltage electric panels in all buildings) -Generator room is not fire separated (Building 1 -Diesel Generator not separated) | Implement the above plan on site. All buildings to be compliant with Accord Standard. | F37 + 4 months | Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress

## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
02-May-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Multinational Export Bureau, Plot No. L-10/D & L-11/A, block 22, Sector 22, FB Industrial Area Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | May 2nd, 2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | The electrical drawings for the LT room, generator placement were provided for building A and proposed substation location however the drawings were outdated and do not reflect the actual site condition. | Consult a qualified electrical engineer to provide detail as-built electrical drawings including the switchgear and other equipment including cable route, trenches, ladder, trays and supports. | 3 months | We have Hired Consultant ( Decent Engineering Associates PEC Reg # 2345 ), we have available digram of sub-station layout provided by K.E. Meanwhile, we are working with a consultant to update SLD and all cable, trenches, ladder trays and routes drawings) K.E team also work on Load upgradation, it will take at least 4 to 6 months |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | The provided drawings for single line diagram does not depict the sufficient information of the electrical system | Consult a qualified electrical engineer to update the Single Line Diagram to include information on all panels, distribution boards and on sub-distribution boards. Ensure all relevant details are accurately depicted to maintain the integrity and safety of the electrical system. | 6 months | We have hired a Consultant ( Decent Engineering Associates PEC Reg # 2345 ), Our and DEA's engineers team are working as per your guidance to complete SLD, to maintain the integrity and safety of the electrical system. Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | It has been found that the electrical drawings for the factory was missing the details necessary to evaluate the electrical system for faults and maintenance. The electrical drawings were only restricted to the markings of fixture only | Consult a qualified electrical engineer to provide drawings for complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. | 6 months | Our team is working on this subject with DEA's engineers, to check each panel and machine, make a drawing to show visible and up-to-date electrical installation |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | The circuit breakers are installed with inappropriate rating in the facility. MCCB for KE incoming line is rated at 800A however the cable size for this is 300 Sq.mm | Evaluate the breaker rating with respect to the cable sizes. The rating of the breaker must not be more than the cable ampacity further adjustable setting of breaker (if any) must be selected to allow current within the cable ampacity after derating factor implementation. The operational cycles of the ACB must be taken into account to ensure functionality of the breaker. | 6 months | Its K.E (Government) property, we already case file on K.E to increase load and as well as upgard our system. We will have documents received from K.E . we already paid all dues to K.E for V.C.B and K.Elecltric team is planning to execute their work. ACB has already installed in our main L.T panels. Factory will provide Accord with all reference documents for review |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | hot spots were found at numerous including the following. - CT of changeover panel near generators. - Inside the distribution baord behind the fire pumps. | Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 6 months | Under the Supervision of Qualified Engineers, we are resolving all issue like faulty componenets, redistributions. We are working on Load Management plan to identify power losses. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Thermographic report was not provided by the factory | Create a schedule to have a thermograph survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. Carry out independent thermograph survey. | E4 + 6 months | MEB has own thermal scanner, and we have a team for thermography, we make sure to conduct thermography after 5 months and prperare report and share with Accord for review |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | Earth pits were inaccessible and inappropriately located.Also the test results for earth pits were missing. | Relocated the earth pits to accessible location and provided earth test report for the earth pits at an interval no less then 6 months | 6 months | At the time of the Inspection, we had a report on a register, but after the Accord intervened, we updated the format of the record. We have our own testing meter for earth testing and we installed a plate with a detailed description to make all earth pit visible. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | .Earthing system was missing in distribution baords -Many distribution boards lacked earthing bus bars. -At panels next to the generators -Electrical machines and cable trays were not connected to earth at numerous location. Machines at ground floor specifically. .- | Consult a qualified electrical engineer to design and evaluate the earthing system. Submit the design to Pakistan Accord for review prior to completing the installation of the earthing system The grounding system should be provided for all facility panels, distribution boards, equipment, and cable trays. Separate earth bar of appropriate size shall be installed in electrical panels and distribution. The size of the earth conductor should comply with IEC standards. Additionally, ensure that the earth pits are located appropriately for easy accessibility. | E7 + 6 months | We are getting updated drawings of earth pits, and we will submit them soon. Eathring work start on all missing panels and distribution |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Panel/cabling/busbar | The inspection of the panels and distribution boards carried the following observations not limited to specific panels. -Missing front and back covers on electrical panels and distribution boards exposed internal components. -Obseved at changeover panels adjacent to generators area. | The IP rating of the panels/Distribution boards must be in compliance with the BS 7671 standards. All measurements should be taken to ensure compliance to standards this may include replacing the panels/Distribution boards. Further the placement shall be such to allow for necessary clearance around for ease of maintenance.39. | 6 months | We are replacing Panels as per standard, as per compliance |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Panel/cabling/busbar | The cable dressing and equipement placement was inappropriate in the distribution baords and panel at the following locaitons. -Distribution baordsa at building B | Consult a certified electrical engineer to rectifty the distribution baords cable dressing and equipment placement in complaince to IEC-61439. | E9 + 3 months | MEB engineers is working with DEA's team to complete all panels and power distribution work complete in compliance with IEC-61439 |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Panel/cabling/busbar | The cable dressing and equipement placement was inappropriate in the distribution baords and panel at the following locaitons. -Distribution baordsa at building C | Consult a certified electrical engineer to rectifty the distribution baords cable dressing and equipment placement in complaince to IEC-61439. | E9 + 3 months | MEB engineers is working with DEA's team to complete all panels and power distribution work complete in compliance with IEC-61439 |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | The enclosure cover of the distrubution boards were missing inlcuding the following. -Lift distribution baord. -Distrubution baords adjacent to generators | The IP rating of the panels/Distribution boards must be in compliance with the BS 7671 standards. All measurements should be taken to ensure compliance to standards this may include replacing the panels/Distribution boards. Further the placement shall be such to allow for necessary clearance around for ease of maintenance. | E9 + 3 months | MEB engineers is working with DEA's team to complete all panels and power distribution work complete in accordance with compliance. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Loop Connection | there were multiple cable connections originating from a single breaker, as well as instances of cables being looped multiple times within the distribution boards. -Observed in building A, B & C. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 2 months | MEB believes in safe work place. With the help of Electrical Consultant, we are removing loope connection, utilize maximum earth and neutral every circuit |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Loop Connection | there were multiple cable connections originating from a single breaker, as well as instances of cables being looped multiple times within the distribution boards. -Observed in building B | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | E13 + 2 months | MEB believes in safe work place. With the help of Electrical Consultant, we are removing loope connection, utilize maximum earth and neutral every circuit |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Loop Connection | there were multiple cable connections originating from a single breaker, as well as instances of cables being looped multiple times within the distribution boards. -Observed in building C | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | E13 + 2 months | MEB believes in safe work place. With the help of Electrical Consultant, we are removing loope connection, utilize maximum earth and neutral every circuit |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. -Distribution baords near the geneator area -At Building C | The IP rating of the panels/Distribution boards must be in compliance with the IEC-61439 standards. All measure should be taken to ensure compliance to standards this may include replacing the panels/Distribution boards. | 3 months | We are replacing this old panels with new panel as per compliance with new Breakers to follow IEC-61439 standards |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Adequate accessibility | Many electrical panels lack adequate accessibility, and the LV room panels do not have enough space for easy inspection or access. Additionally, distribution boards in several locations are installed too high, making components difficult to reach Including the following locaitons. Building A LV panel room | All panels should have sufficient space allocated for maintenance and inspection purposes providing compliance to IEC 60204-1. Further the installation height of distribution boards must not exceed 6’-0” from the top of distribution board. | 6 months | Civil work is under going. And after completing Civil work,, we will change LV panels postions |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Adequate accessibility | Many electrical panels lack adequate accessibility, and the LV room panels do not have enough space for easy inspection or access. Additionally, distribution boards in several locations are installed too high, making components difficult to reach Including the following locaitons. -Distribution boards at ground floor at building C | All panels should have sufficient space allocated for maintenance and inspection purposes providing compliance to IEC 60204-1. Further the installation height of distribution boards must not exceed 6’-0” from the top of distribution board. | E17 + 2 months | Civil work is under going. And after completing Civil work,, we will replace Old panel to new Electric Panels as per compliance |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Lint & dust inside panel board | Lint and dust found in most of the distribution boards and panels incluiding the following. Distribution baords at building C | Schedule maintenance should be caried out for cleaning of panels and distribution boards. All measure should be taken to ensure the removal of dust, dirt, and any other sort of containment inside the panels. | E18 + 2 months | we have maintain a schedule for weekly and monthly cleaning panels and machines. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning arrestor was installed for the solar modules only , lacking design criteria or risk assessments for the protection system. Surge protective devices were also absent from electrical panels and distribution boards. | Consult a qualified electrical engineer to provide risk assessment report for lightning protection as per the IEC 63205 Standards and submit to Pakistan Accord prior to any modification on site in this regard. Consult a qualified electrical engineer to design the lightning protection system as per the IEC 62305 standards. The design drawings shall be submitted to Pakistan Accord prior to installation on site. | 8 months | Our Consultant DEA's is working on it, He will submitt proposals on us, then we will submit you soon. Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review and if required, will install new LPS system as per design previously reviewed by Accord. Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. Some of the related issues include: - Incomplete coverage of fire alarm devices in some areas - Non functional heat detectors installed in the process area - Automatic detection of the fire is not provided. - type of detection devices not appropriate - conventional non listed panel installed - Sounders inaudible due to low volume, or without distinctive audible signals | (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 5 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E21 + 1 months | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation | E22 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E23 + 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E24 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E25 + 3 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Emergency Lighting | Provided but insufficient | During the test it has been found that most of the emergency lights in the factory area except for office block are non-functional. Including the following locations. Building A | Consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements. Submit the design to Pakistan Accord prior to installation. All emergency lights must be listed and in proper working condition | 6 months | Factory will consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements, submit the design to Pakistan Accord prior to installation and instal in Building A in accordance with reviewed design. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Emergency Lighting | Provided but insufficient | During the test it has been found that most of the emergency lights in the factory area except for office block are non-functional. Including the following locations. Building B | Consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements. Submit the design to Pakistan Accord prior to installation. All emergency lights must be listed and in proper working condition | E27 + 2 months | Factory will consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements, submit the design to Pakistan Accord prior to installation and instal in Building B in accordance with reviewed design. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Emergency Lighting | Provided but insufficient | During the test it has been found that most of the emergency lights in the factory area except for office block are non-functional. Including the following locations. Building C | Consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements. Submit the design to Pakistan Accord prior to installation. All emergency lights must be listed and in proper working condition | E28 + 2 months | Factory will consult a qualified electrical engineer to design emergency lighting system as per the NFPA standard requirements, submit the design to Pakistan Accord prior to installation and instal in Building C in accordance with reviewed design. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Emergency Lighting | Independent power source | the emergency lights have been energized by utilizing by centralized battery using a UPS.however these lights are further connected to light switches which need to be switched on for emergency lights to work. The changeover of the emergency lights from utility to UPS is done manually which pose significant risk of non-availability of power during the blackout | The circuit for emergency lighting with centralized battery must be fire rated and it should be automatically activating emergency lights. Each zone should have its own dedicated emergency lighting circuit. | 6 months | Factory will provide centralized fire rated battery that automatically activates emergency lights, each zone with its own dedicated emergency lighting circuit |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Emergency Lighting | General Lighting | It was observed that most of the factory area lights are being switched on and off directly from the circuit breakers. Operating a circuit breaker directly from the breaker itself is unsafe and not recommended. This | Lighting should not be switched off at the breakers instead, it should be controlled via light switches for individual and group of lights. | 3 months | General lights already in switches, while for Department shutdown, we use Breaker. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | It has been observed that’s the generator area lacks sufficient illumination. The LV room does not have exhaust fans or air conditioning for temperature control and ventilation. | Consult a Qualified Engineer to install an exhaust mechanism in the LV room to improve air circulation. Also to upgrade the existing air conditioning system that can provide sufficient air changes for the room. The illumination of the geneator area should be addressed in comlaince to BS-7671 . | 2 months | Civil Work is under progress, after civil work we have a plan to air conditioning system on LT room. |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Generator, Transformer & Sub-Station Room | Working clearance | It has been observed that on numerous location the accessibility of the electrical panels in the room was inadequate including the following. LV room at Building A | The electrical room should be devoid of miscellaneous items, and equipment must be easily accessible from all sides for maintenance, with evacuation routes clearly marked and ensured | 2 months | After completion of civil work, we solve thid issues |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Cabling & Wiring | Cables support and protection | It is observed from the inspection that at the numerous locations that cables are laid without appropriate support and dressing.inlcuding the following locaitons. -Distribution baords near generators | All cables must be contained within cable trays and conduits, properly dressed, and organised as per the standards. All cables must be contained within suitable enclosures, properly dressed, and organised as per the BS 7671 standard. | 3 months | After Civil work completed, we will CLEAR all sides and evacuation marks clearly as per compliance. |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Cabling & Wiring | Cables support and protection | It is observed from the inspection that at the numerous locations that cables are laid without appropriate support and dressing.inlcuding the following locaitons. -At Building A buhind the LV room | All cables must be contained within cable trays and conduits, properly dressed, and organised as per the standards. All cables must be contained within suitable enclosures, properly dressed, and organised as per the BS 7671 standard. | E34 + 2 months | After Civil work completed, we will CLEAR all sides and evacuation marks clearly as per compliance. |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Cabling & Wiring | Cable trench and channel cleanliness | It was observed that the cable trenches and channel were significantly contaminated with lint and dust. The significant accumulation of dust in cable trenches and channels is a cause for concern, as it can lead to various operational issues and safety hazards. specially at geneator trenches | The cable trenches must be kept clear of debris and dirt, and any open trenches must be covered to prevent entry by rodents and other contaminants. | 3 months | DONE |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Cabling & Wiring | Splicing of cables | It was noted on numerous cables that the cables were not terminated appropriately in several panels and equipment, wires are directly connected to endpoints without the use of suitable lugs. At numerous locations that the wire was joint using tape inside the distribution boards on cable trays/channels -At cable tray through out the facility. -At building C | Tape joints should be avoided at all costs. Cable terminations shall done with appropriate cable lugs. | 6 months | WORK IN PROGRESS |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Cabling & Wiring | Colour coding | It was noted that within various panels and distribution boards, the phase of the cables could not be determined based on their colour coding at multiple locations e.g lift panels and Cables at LV room panels | Each cable must be colour coded according to the respective phase colour. further colour sleeves must be applied on buss bars for phase identification. | 3 months | WORK IN PROGRESS |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Cabling & Wiring | Fixtures | It is observed that at the numerous location the receptacle for the appliance lacks the earth connection and found broken/unsafe to use specifically on roof floor | Secure the loose power receptacles with appropriate fixed supports to prevent movement and ensure stable connections. | 6 months | WORK IN PROGRESS |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
02-May-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Multinational Export Bureau, Plot No. L-10/D & L-11/A, block 22, Sector 22, FB Industrial Area Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | May 2nd, 2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Other Damage/Defects | Health and Safety | Following items present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of roof/solar panels – Health & Safety concern. • Building C - OHWT roof/Solar panels: a) Steel ladder providing access to the OHWT roof exhibited significant instability, indicating inadequate attachment to the structural system | Provide safe access across the building for services and maintenance. Consider installation of crossover stairs. | 3 months | Work has been started as your mark areas. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Other Damage/Defects | Health ans Safety | Following items present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of roof/solar panels – Health & Safety concern. • Building C - OHWT roof/Solar panels: b) No edge protection is provided to the roof of OHWT and Solar panel over lightweight steel shed. | Provide an appropriate roof edge protection to all accessible roofs. | 3 months | WORK IN PROGRESS |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Other Damage/Defects | Column impact damage | This is related to the Building B. Impact damage in an RC column is observed near the backside boundary which suggests the cracks is developed in the concrete is due to the impact while fixing the MS angle on the corners of column, might result in corrosion of rebar by the penetration of water. We have visually inspected the loading in this area and observed there is no concerns regarding overstressing. | Building engineer to inspect the damage. Repair the column. | 6 months | After accord visit monitoring of column creak through 2 mm thick glass strip. The glass strip fixed with column and monitor 3 weeks after final inspection fourth weeks find creak still same position same as on day one after this, we have removed column plaster and fixed wire mesh on concrete surface with steel wire nails and applying 1:4 ¾” thick cement sand plaster |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Structural System | Lateral stability system | This refers to the Building A roof, where the vertical extension over roof observed to have inadequate lateral stability and it is more heighted as well | Building Engineer to check that canopy has a positive connection to the main building, otherwise Engineer to design bracing or alternative system to provide lateral stability. Strengthening works to be implemented. | 7 months | The structural Engineer visited our ste. He will submit his report soon. Strengthen is enough, but for more strengthen , he will prepare a plan, After receiving we will submit you . |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Structural Documentation | Differs from as-built structure | This relates to building C. The as-built structural drawings provided do not match in on all the floors as observed on site and need to be updated to include the following discrepancies (non-exhaustive): • Secondary beams on all the floors were not documented as observed in as-built structure. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation | 6 months | During construction as per requirement the roof framing plan has been revised But unfortunately the said location changes has been overlooked unintentionally during the preparation of As Built drawing. However, the revised As Built drawing is under preparation which will be submitted at the earliest. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural Documentation | Undocumented extension | This relates to building A, B, C and D. • Vertical extension is observed in the all the buildings which are not indicated on the layouts • External steel stairs are not shown on the structural drawings. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | we are working on it to complete as built diagram |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Loading | Uncontrolled loading | This relates to Building B and C. Heavy leftover garment storage is observed at the roof level of building in disorganised pattern. Heavy storage of fabric observed on the roof along with the trolleys containing fabric bags. Fabric has been stacked up to a height of 3.4m over several bays. A Raising machine place over the roof observed to be heavily loaded over a concentrated area. | Reduce the height of stack load up to 2m so that weight is reduced | 1 month | Now, Loading will be under 2 meter, raising machine is now removing from top floor |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Loading | Uncontrolled loading | This relates to Building B and C. Heavy leftover garment storage is observed at the roof level of building in disorganised patter. Heavy storage of fabric observed on the roof along with the trolleys containing fabric bags. Fabric has been stacked up to a height of 3.4m over several bays. A Raising machine place over the roof observed to be heavily loaded over a concentrated area. | Keep monitoring the portion of the building where Raising machine is placed for signs of any distress in structure. | 6 months | Controlled. Raising machine is now replaced from roof. |  |  |  | Pending Verification
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Structural Documentation | Lack of safe load plans | Factory lacks the load plan as most of the roofs and few production floors were observed to have heavy storage. | Building Engineer to review design documentation to determine the safe load capacity and develop safe load plans. Submit load plans to Pakistan Accord for review. | 6 months | work in progress |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Structural Documentation | Lack of safe load plans | Factory lacks the load plan as most of the roofs and few production floors were observed to have heavy storage. | Factory management to actively manage the floor loading. | 6 months | We are Constructing new building, After Construction, this problem can be solved automatically |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
anotehr electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1