## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
2024-07-05
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | Amna Apparel Pvt Ltd, Plot No. F-271, Site Area, Karachi City, Sindh 75700, Pakistan, Karachi.
[9 empty] | Date of Initial Inspection | [12 empty] | 2024-07-05
[22 empty] | Remediation Schedule | Financing Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | There were no substation room layout drawings available for the factory. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). | 1 months | we already hire an credible electrical engineer / consultant to develop required drawings. But we need some assistance regarding Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Factory will provide a layout showing location of transformer and dimensions for clearance on all sides and submit to Accord for review. Factory will provide adequate separation, ventilation and even floor surface for transformer room in accordance with previously reviewed layout |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but missing necessary details. | Upgrade comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). | 6 months | we already hire an credible electrical engineer / consultant to develop required drawings. But we need some assistance regarding Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Factory will appoint a qualified person to produce a SLD and submit to Accord for review. Once completed Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | The factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. | Upgrade comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). | 8 months | we already hire an credible electrical engineer / consultant to develop required drawings as per Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Factory will provide electrical layout drawings showing lighting, power, earthing, main cable containment and submit to Accord for review. Factory to ensure on-site electrical infrastructure matches approved layout drawings |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | It was found at main LT Room panels old obsolete type circuit breakers (CB) are mounted inappropriately. | Replace old obsolete circuit breakers (CB) and mount them properly within the panel. | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and replace the old obsolete circuit breakers (CB) where required. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Circuit breakers | Circuit breakers are mounted Externally on the wall at the rear of the building at ground floor in front of compressor and washing area. | Cover all circuit breakers that are openly installed throughout the facility with concealed metallic enclosure to ensure safety and compliance with standards. | E4 + 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes at main LT room. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). | E5 + 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. - Ground floor main LT room, Ground floor office power DB In Front of main gate and a distribution board in Production Area . | Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will arrange Thermographic reports after internal inspection of all panels.Once Thermographic switchgears is done, will share with Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | It was found that a thermographic report was not available at the site. | A thermographic Testing report shall be prepared periodically. | E7 + 5 months | factory will create schedule to arrange thermograph survey carried out by a qualified surveyor for the entire electrical system bi-annually. Once schedule will be done. Will share with Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Earthing system | The earth pits were inaccessible and unsuitably located near main gate. | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 4 months | We have 3 earth pits which are very much accessible although as recommended we will change the location of earthing distribution point at generator room |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections near main LT Room. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | E9 + 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54 |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | Equipotential bonding for the cable trays, machines body and metallic panel covers was missing production area 1st floor and street light poles near washing. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | E9 + 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. |  |  |  | In Progress
No | 3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Earthing system | It was also found that the Earth testing record was available but the Earth distribution layout drawing was not available. Without Earth drawings, it is difficult to ensure that the grounding system is functioning correctly and maintenance activities. This can compromise the safety of personnel and equipment, increasing the risk of electric shock and equipment failure. | Develop the earth distribution layout drawing, earth testing record and submit them to the Pakistan Accord. | E11+ 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. Factory will submit earth distribution layout drawing and earth testing record to the Pakistan Accord for review |  |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | In a number of external areas, it was observed that electrical components were not suitable for the environmental conditions in which they were installed. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed. |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was found that in many distributions board lack of dedicated neutral connection for outgoing power circuits. | Conduct a thorough inspection of the existing wiring to identify circuits sharing a neutral wire. Provide dedicated neutral wires for each circuit, ensuring that each circuit's return path is properly isolated. | E13 + 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will Provide dedicated neutral wires for each circuit, ensuring that each circuit's return path is properly isolated. |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | There was loose wiring, cables had joints, improper bus-bar arrangement, cables touching with bus-bars and panel body inside the distribution boards. Loose wiring and cable joints create high resistance points, leading to excessive heat generation which can cause the insulation to melt and potentially lead to fire. | Install wire ducts to organize and route wires neatly, remove loose cables, remove inside panel cable joints, and ensure that no cables are attached to the bus bars. | E13 + 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will evaluate all panels and ensure the dressing of the cables as as per compliance. |  |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed in a number of electrical panels such as main CB of VFD in production and at washing machine main CB. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022) | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will ensure ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Openings | During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements such as LT room Distribution Panels. | Corrective actions are required to seal all openings and replace missing panels covers to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will seal all openings and replace missing panels covers to restore the integrity and safety of the electrical systems. |  |  |  | In Progress
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Adequate accessibility | During the visit, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components such as DB in front of Main gate and generator room. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022) | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems such as power switch boards in sample room and compressor panel. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022) | 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will ensure all electrical panels and trunking runs shall be cleaned of any dust or lint. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was not provided, however, there was no study available to confirm its adequacy. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. | 6 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review. If required, Factory will install new LPS system as per design previously reviewed by Accord Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
No | 3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was also Surge protection devices (SPD) were not found in any distribution boards. If a surge occurs without the device, it can be the cause of an accident or any equipment damage. | Install surge protective devices with each main distribution board. | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | - The Fire Alarm Panel installed in the facility were non-compliant and non-listed. - The cabling used to complete the installation of the FADS is not fire rated. - There is insufficient back-up power supply to the FADs. - Fire alarm interfaces are not provided for the FADS to control the building's gas supply, HVAC system (including dampers), elevators, and electronic access control equipment. | (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | it will be discussed in meeting for more clarification but it takes some time to accomplished because of heavy cost and arrangements. Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
No | 3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E23 + 1 months | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E23 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E24 + 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E25 + 3 month | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non-compliant fire detection and alarm system. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E26 + 3 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Emergency Lighting | Provided but insufficient | Several areas lack sufficient emergency lighting coverage such as. • Yarn Storage Area and Knitting entrance ground floor • Ground Floor till the Second Floor Stairs. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional listed emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation | 3 months | Factory will conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional listed emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation The layouts for emergency lights layouts including exit sign shall be submitted to Accord for approval. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Emergency Lighting | Provided but insufficient | During the inspection, Multiple emergency luminaires indicate the need for maintenance. | Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies. | 3 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The layouts for emergency lights layouts including exit sign shall be submitted to Accord for approval. |  |  |  | In Progress
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Emergency Lighting | Provided but insufficient | In some areas installed emergency lights are too dim to provide adequate illumination. | Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s) | E29 + 3 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Storage area emergency light found non-operational on battery backup and mezzanine floor emergency light test on less battery backup. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. The factory will configure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. |  |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Emergency Lighting | General Lighting | During the inspection following observations were noted: - Several locations were identified as lacking sufficient general lighting including building external areas, stairs, walkways such as storage area beside Knitting ground floor, Ground Floor Yarn storage area & carton storage area at backyard. | Conduct a thorough assessment of lighting throughout the facility to find areas with insufficient illumination. Install additional lighting fixtures in these spots to ensure adequate brightness. Ensure the new lighting design meets safety and efficiency guidelines to provide clear visibility for all tasks and emergency situations. | 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Emergency Lighting | General Lighting | - General lighting was controlled directly from the breakers within the Distribution Boards rather than through standard light switches. | Reconfigure the electrical control system to ensure that general lighting is operated via standard wall-mounted light switches instead of circuit breakers. This involves installing appropriate switches and rewiring the control circuits as per the National Electrical Code (NEC) and other relevant electrical safety standards. Ensure that all switches are easily accessible and clearly labelled to enhance operational efficiency and safety. | 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Emergency Lighting | General Lighting | At many locations found the general lights' fixtures were rusted and broken hanged with ropes. Fixtures hung with ropes are unstable and may fall, causing injury to personnel or damage to equipment. Rusted and broken fixtures can lead to exposed wiring, increasing the risk of electrical shocks and short circuits. | Need to check regularly the lights and repair or replace the broken and faulty lights. Remove the lights fixed with ropes and properly fix them with a fastener. | 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Cabling & Wiring | Cables support and protection | Proper supports were not provided for cables such as Inappropriate cable support found at ground floor near compressor. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). | 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Cabling & Wiring | Cables support and protection | During the inspection It was noted in several locations that the electrical connections were open and exposed, which may cause some fatal incidents. In the future do not leave any connection exposed such as in LT Room. | Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). | E25 + 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Cabling & Wiring | Cables support and protection | During the inspection it was noted that numerous loose connections were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections. | Establish a routine maintenance schedule to regularly check and secure electrical connections, and train personnel on safe wiring practices | E36 + 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Cabling & Wiring | Cables support and protection | It was found that at many locations, the insulation of cables was damaged. Damaged insulation can expose live conductors, posing a risk of electrical shock to anyone who comes into contact with the cables. | Upgrade insulation or replace damaged cables to prevent electrical hazards. | E36 + 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk such as all cable trays above stiching of first floor and second floor. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022) | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | E40 + 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Cabling & Wiring | Fixtures | At many locations loose power receptacles were found. This poses a significant risk of equipment damage or electrical incidents due to the instability of the receptacles. Loose connections can lead to electrical arcing, which increases the risk of fire and can cause serious injury or equipment failure. | Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed. | 2 months | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress
No | 3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Cabling & Wiring | Fixtures | It was found that the power stabilizer was placed under the office table. The area under a table often has dust, paper, or other flammable materials that can ignite if the stabilizer overheats. Also placing the power stabilizer under a table makes it harder to access for maintenance, inspection, or emergency shutdown. | Place the voltage stabilizer in an appropriate location, away from flammable materials and where it is easily accessible for maintenance and emergency switching operation. | E43 + 1 month | we already hire an credible electrical engineer / consultant to evaluate our system and ensure safety & compliance with standards and remediation as required. |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
2024-07-05
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Amna Apparels Pvt Ltd, Plot No. F-271, S.I.T.E Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | July 5th, 2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Some emergency doors were jammed and inoperable from inside, such as the door on the Lower Roof Floor at Stair S-2. Opening mechanism is noncompliant, for example, at Stair S-2. | All doors should be easily openable from the inside and all locking mechanisms removed to emergency exit doors. | 1 month | We already starts evaluating the observation & recommendations also ensure to comply our needs as per given standard |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Some emergency doors were jammed and inoperable from inside, such as the door on the Lower Roof Floor at Stair S-2. Opening mechanism is noncompliant, for example, at Stair S-2. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | We already starts evaluating the observation & recommendations also ensure to comply our needs as per given standard. But it needs more clarification which will be discussed in meeting |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Some emergency doors were jammed and inoperable from inside, such as the door on the Lower Roof Floor at Stair S-2. Opening mechanism is noncompliant, for example, at Stair S-2. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F2 + 2 months | We already starts evaluating the observation & recommendations also ensure to comply our needs as per given standard |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Fire Safety Management | Fire drills | Production Building, Lower Roof have excessive common path travel distances from stitching area to a safe exit access. | Train fire wardens to assist with evacuation to the nearest available exit. | 2 months | We already starts evaluating the observation & recommendations also ensure to comply our needs as per given standard but its not more than 150 feet distance. All fire wardens are proper trained and evacuation drills are held according to schedule. Factory will provide documentation of training and latest fire drill to Accord for review |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Travel distance | Production Building, Lower Roof have excessive common path travel distances from stitching area to a safe exit access. | Review travel distances throughout the site to ensure that all travel distances meet the limits in Accord Building Standard. Develop a plan for providing additional exits. Submit to Accord for review and approval prior to commencing rectification works on site. | 4 months | We already starts evaluating the observation & recommendations also ensure to comply our needs as per given standard but its not more than 150 feet distance. But for more safety concerns we have a plan to accommodate another exit route from lower roof top. Factory will prepare drawings showing proposal for providing additional exits or re-arrangement of escape routes to provide travel distances to exits within limits and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Travel distance | Production Building, Lower Roof have excessive common path travel distances from stitching area to a safe exit access. | Implement the above plan agreed with Accord. All travel distances on site should be compliant with Accord Building Standard. | F5+ 4 months | We already starts evaluating the observation & recommendations also ensure to comply our needs as per given standard but its not more than 150 feet distance. All fire wardens are proper trained and evacuation drills are held according to schedule. Kindly revise this NC Factory will ensure travel distances within limits determined in the Pakistan Accord Building Standard and in accordance with proposals submitted previously to Accord for review |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Exit access | Obstructions/storage in escape route e.g. 1st and Lower Roof Floor Production Area. | Remove obstructions on escape routes and keep them clear for escape Immediately | 1 month | all the storages and obstructions have been removed |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Unprotected openings into stairs e.g. S-3 and S-2. Fire Doors are not installed e.g. S-1: Ground, 1st and Lower Roof Floor. Door Self closure is not functioning at Mezzanine Floor Storeroom at Emergency Stair S-1 Stair discharge route is not fire separated from the building e.g. S-1 from storage are at Ground Floor. | Remove fire load / Storage from all stairs | 1 month | all the storages and obstructions have been removed. We already purchase the listed fire doors and will be installed in next 20-25 days |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | Unprotected openings into stairs e.g. S-3 and S-2. Fire Doors are not installed e.g. S-1: Ground, 1st and Lower Roof Floor. Door Self closure is not functioning at Mezzanine Floor Storeroom at Emergency Stair S-1 Stair discharge route is not fire separated from the building e.g. S-1 from storage are at Ground Floor. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. | 4 months | all the storages and obstructions have been removed. We already purchase the listed fire doors and will be installed in next 20-25 days Factory will prepare drawings showing proposed fire separating construction and certification for door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Protection of stairs | Unprotected openings into stairs e.g. S-3 and S-2. Fire Doors are not installed e.g. S-1: Ground, 1st and Lower Roof Floor. Door Self closure is not functioning at Mezzanine Floor Storeroom at Emergency Stair S-1 Stair discharge route is not fire separated from the building e.g. S-1 from storage are at Ground Floor. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. Note that the final exit door from a stair to outside the building does not need to be fire rated. - All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. - Where stairs discharge within a building, a fire separated corridor shall be provided that leads outside building. | F9+ 4 months | We already purchase the listed fire doors and will be installed in next 20-25 days Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Escape stair condition | There are no handrails e.g. S-1. Obstacles in stairs e.g. S-1 and S-2. Emergency Stair S-1 is not structurally safe for escape more than 100 occupants at a time. | Remove all obstructions from stairs. | 1 month | handrail have been installed |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Escape stair condition | There are no handrails e.g. S-1. Obstacles in stairs e.g. S-1 and S-2. Emergency Stair S-1 is not structurally safe for escape more than 100 occupants at a time. | Remove all trip hazards from stairs. | 1 month | handrail have been installed |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Escape stair condition | There are no handrails e.g. S-1. Obstacles in stairs e.g. S-1 and S-2. Emergency Stair S-1 is not structurally safe for escape more than 100 occupants at a time. | Ensure the following are provided: - Stair structure to be fixed so that stairs are safe for escape. -Ensure Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height | 3 months | handrail have been installed |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit signage | Exit signs are not clear / misleading e.g. Mezz Storage Area. | Remove misleading direction arrows from the means of egress. | 1 month | misleading sign have been removed from store. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit signage | Missing exit signs at stair discharge routes in all buildings. Missing exit signs in corridors and circulation areas in all buildings. Missing exit signs in production areas e.g. Production Building. Missing exit signs in offices. Missing exit signs at exits from site . Missing exit signs at roof in all buildings. Exit signs are not clear / misleading e.g. Mezz Storage Area. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | needs more clarity and discussion. Factory will provide drawing showing type, size and location of exit signage that demonstrates compliance with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3 |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit signage | Missing exit signs at stair discharge routes in all buildings. Missing exit signs in corridors and circulation areas in all buildings. Missing exit signs in production areas e.g. Production Building. Missing exit signs in offices. Missing exit signs at exits from site . Missing exit signs at roof in all buildings. | Rectify signs and provide new signage to comply with Accord Standard. Ensure that all exit signage is checked periodically and in good working condition. | F15 + 3 months | Exit signage will be provided according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Rated Construction | Separation of high-risk areas | Steam generator is not fire separated e.g. at Ground and Lower Roof Floor. Steam generator rooms do not have a permanent opening outside the building e.g. Lower Roof Floor Electric Steam generators. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Separation to electric steam generator up to 3 m above the finished floor level. This should be achieved using reinforced concrete / masonry walls with a solid steel door. - The door must have a self-closer and a positive latch. - Blast vent should be provided to outside the building. - Provide Fire separation from the internal areas by constructing a minimum 3-meter-high reinforced concrete or block masonry wall, installing a solid steel door with a self-closer and positive latch, and creating an opening in the steam generator room that directs any potential blast safely outside the building. | 4 months | needs more clarity and discussion. Factory will prepare drawings showing proposed fire separating construction to high-risk areas and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Separation of high-risk areas | Steam generator is not fire separated e.g. at Ground and Lower Roof Floor. Steam generator rooms do not have a permanent opening outside the building e.g. Lower Roof Floor Electric Steam generators. | Implement the above plan on site. All buildings to be compliant with Accord Standard. | F17 + 4 months | needs more clarity and discussion Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building e.g. Ground Floor Storage area and Offices. Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) e.g. 1st Floor and Lower Roof Floor. Storage in exit stairs routes e.g. 1st Floor and Lower Roof Floor S-1 and S-3. Storage in exit stairs discharge routes e.g. Ground Floor Stair S-1. Storage areas are not fire separated from the rest of the building e.g. Ground Floor offices with storage areas. | Identify all designated storage areas. For all storage areas where storage cannot be managed within in-process storage limitations described above, prepare drawings showing proposed fire separation details of storage areas. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors. - Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). - Storage area has to be separated from a protected stair with a lobbied separation | 4 months | needs more clarity and discussion Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Storage | Storage areas are not fire separated from the rest of the building e.g. Ground Floor Storage area and Offices. Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above) e.g. 1st Floor and Lower Roof Floor. Storage in exit stairs routes e.g. 1st Floor and Lower Roof Floor S-1 and S-3. Storage in exit stairs discharge routes e.g. Ground Floor Stair S-1. Storage areas are not fire separated from the rest of the building e.g. Ground Floor offices with storage areas. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F19 + 4 months | needs more clarity and discussion Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Safety Management | Fire drills | No regular fire drills. No evidence of fire drills Fire drill documentation is of poor standard. | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | records are available for review |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Safety Management | Fire drills | No regular fire drills. No evidence of fire drills Fire drill documentation is of poor standard. | Ensure fire drills are performed a minimum 2 times per year. | F21+ 2 months | records are available for review |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System. No records of maintenance of Emergency Lighting. No records of maintenance of Fire Doors. | Prepare maintenance schedule for all life safety systems. | 2 months | records are available for review |  |  |  | Pending Verification
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System. No records of maintenance of Emergency Lighting. No records of maintenance of Fire Doors. | Prepare a schedule of proposed system maintenance. Identify how systems will be maintained and who is responsible. The schedule to be submitted to Accord for review and approval. | 2 months | records are available for review |  |  |  | Pending Verification
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Detection and Alarm System. No records of maintenance of Emergency Lighting. No records of maintenance of Fire Doors. | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep maintenance records. | F24 + 2 months | records are available for review |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Safety Management | Records of system testing | No records of testing of Fire Detection and Alarm System. No records of testing of Emergency Lighting. No records of testing of Fire Extinguishers. No records of testing of Fire Doors. | Prepare testing schedule for all life safety systems. | 2 months | records are available for review |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Safety Management | Records of system testing | No records of testing of Fire Detection and Alarm System. No records of testing of Emergency Lighting. No records of testing of Fire Extinguishers. No records of testing of Fire Doors. | Prepare a schedule of proposed system testing. Identify how systems will be tested and who is responsible. The schedule to be submitted to Accord for review and approval. | 2 months | records are available for review |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Safety Management | Records of system testing | No records of testing of Fire Detection and Alarm System. No records of testing of Emergency Lighting. No records of testing of Fire Extinguishers. No records of testing of Fire Doors. | Ensure all systems are being tested as per the schedule agreed with Accord. Keep testing records. | F27 + 2 months | records are available for review |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Prepare an Emergency Action Plan report. | 2 months | records are available for review |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F29 + 2 months | records are available for review |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2024-07-05
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Amna Apparels Pvt Ltd, Plot No. F-271, S.I.T.E Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 5-Jul-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal column at marked location on Ground floor level appear to be potentially overstressed for the applied load. This column supports the mezzanine floor as well. | Factory Engineer to review design, loads and columns stresses in area identified. | 3 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. We started our detailed structure assessment to measure the loads and stress accordingly. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal column at marked location on Ground floor level appear to be potentially overstressed for the applied load. This column supports the mezzanine floor as well. | Verify insitu concrete stresses either by existing cylinder strength data for the identified columns or 100mm dia. cores from 4 columns and submit to Pakistan Accord for review | 2 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. We started our detailed structure assessment to measure the loads and stress accordingly. Factory will submit data on actual concrete strength determined from cores or cylinder strength data taken during construction to Accord for review |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal column at marked location on Ground floor level appear to be potentially overstressed for the applied load. This column supports the mezzanine floor as well. | Review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. | S1 + 3 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. We started our detailed structure assessment to measure the loads and stress accordingly. Factory will submit analysis details based on actual concrete strength to Accord for review, as well as safe load plans to suit |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Column | During the inspection of the production building, two columns were observed to have cracks. The portion of the building along with the mezzanine floor, exhibits cracks in the perimeter column. These cracks appear to be due to degraded condition of the concrete and the excessive corrosion of rebar leading to the loosen up connection between concrete and rebar. The condition of the concrete also seems to be degraded when checked. Also, the column in this area at the middle are highly stressed as well. Another column at the lower roof level along with the stairs, observed with cracks and degraded concrete. | Building Engineer to carry out survey of the RC columns to investigate the cause and impact of these cracks on the loading capacity of the cracked columns and highly stressed columns in this region. | 2 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. as observed during the initial assessment we starts remediate the highlighted columns and beams where cracks found |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Cracking | Column | During the inspection of the production building, two columns were observed to have cracks. The portion of the building along with the mezzanine floor, exhibits cracks in the perimeter column. These cracks appear to be due to degraded condition of the concrete and the excessive corrosion of rebar leading to the loosen up connection between concrete and rebar. The condition of the concrete also seems to be degraded when checked. Also, the column in this area at the middle are highly stressed as well. Another column at the lower roof level along with the stairs, observed with cracks and degraded concrete. | Building Engineer to ensure that the columns are not loaded beyond its capacity. | 2 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. as observed during the initial assessment we starts remediate the highlighted columns and beams where cracks found. Factory will submit report on analysis done to ensure capacity of columns to Accord for review |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Cracking | Column | During the inspection of the production building, two columns were observed to have cracks. The portion of the building along with the mezzanine floor, exhibits cracks in the perimeter column. These cracks appear to be due to degraded condition of the concrete and the excessive corrosion of rebar leading to the loosen up connection between concrete and rebar. The condition of the concrete also seems to be degraded when checked. Also, the column in this area at the middle are highly stressed as well. Another column at the lower roof level along with the stairs, observed with cracks and degraded concrete. | Building Engineer to propose a remedial action after assessing the root cause of cracks and share that with Pakistan Accord for the review. | 2 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. as observed during the initial assessment we starts remediate the highlighted columns and beams where cracks found after then we analyze the root cause of it Factory will submit details of proposed remedial works to Accord for review |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Cracking | Column | During the inspection of the production building, two columns were observed to have cracks. The portion of the building along with the mezzanine floor, exhibits cracks in the perimeter column. These cracks appear to be due to degraded condition of the concrete and the excessive corrosion of rebar leading to the loosen up connection between concrete and rebar. The condition of the concrete also seems to be degraded when checked. Also, the column in this area at the middle are highly stressed as well. Another column at the lower roof level along with the stairs, observed with cracks and degraded concrete. | Implement the remedial solution. | S6 + 4 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. as observed during the initial assessment we starts remediate the highlighted columns and beams where cracks found after then we analyze the root cause of it and permanent remedial solution Factory will implement remedial actions required if necessary in accordance with analysis and proposals reviewed previous ly by Accord |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural Documentation | Differs from as-built structure | This observation pertains to all buildings across the entire premises, where the provided architectural and structural drawings differ from the as-built structures in various instances, as detailed below: 1) The available as-built architectural drawings do not match the as-built structures of the production building for upper roof. 2) Cross section of the building is not documented. 3) The provided DEA report does not provide details for the jacketing done one of the columns at ground floor. | Provide details for the reasons for and method used for jacketing done on the columns at ground floor | 6 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. Although we already jacket out high risk column as per standard and method given by our last consultant. Report will be submitted to Accord for review. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Structural Documentation | Differs from as-built structure | This observation pertains to all buildings across the entire premises, where the provided architectural and structural drawings differ from the as-built structures in various instances, as detailed below: 1) The available as-built architectural drawings do not match the as-built structures of the production building for upper roof. 2) Cross section of the building is not documented. 3) The provided DEA report does not provide details for the jacketing done one of the columns at ground floor. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built structural and architectural layouts. | 6 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. The last available drawing were shown on that day although new and proper drawings will be available in given time. Factory will submit accurate as-built drawings to Accord for review |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Structural Documentation | Lack of safe load plans | During the inspection, it was observed that certain production floors were being used for storage, including the roof slab under the vertically extended fibre shed, where finished goods cartons and loose fabric were stacked in an unorganized manner. While the factory has load plans, these plans lack detailed information, such as the loading capacity of the floor and also, they are not posted on the floors. | Building Structural Engineer to carry out on-site survey, collect information and produce the load plans for all the floors. | 6 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly.The last available load plans were shown on that day although new and proper load plan will be available in given time. Factory will submit safe load plans based on structural assessment carried out previously using actual concrete strength, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Other Damage/Defects | Moisture ingress | This is related to the production building 1st floor. Dampness in structural members (slab) of concrete observed with the signs of ingress of water from roof impacting damage to the structure and might result in corrosion of rebar by the penetration of water. Furthermore, signs of cracks have also been observed in production building roof slab and beams resulting in concrete to fall which appears to be due to water ingress. | Building engineer to inspect the locations (in production building) of water ingress and possible reason of cracks and propose the remedial solution to repair the structure distress caused by ingress of water. | 3 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remiadiate it accordingly.as observed during the initial assessment we starts remediate the highlighted areas where structure distress found after then we analyze the root cause of it |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Other Damage/Defects | Moisture ingress | This is related to the production building 1st floor. Dampness in structural members (slab) of concrete observed with the signs of ingress of water from roof impacting damage to the structure and might result in corrosion of rebar by the penetration of water. Furthermore, signs of cracks have also been observed in production building roof slab and beams resulting in concrete to fall which appears to be due to water ingress. | Provide suitable protection on roof for ingress of water to prevent damage to structure from potential ingress on all buildings | S11 + 3 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. as observed during the initial assessment we starts remediate the highlighted areas where structure distress found after then we analyze the root cause of it |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Other Damage/Defects | Health and Safety | This regards the unsafe lift cabin that lacks Edge protection and presents a risk of potential injury resulting from a fall from the lift cabin during any operation of maintenance times. Lift cabin railing doors found to be open while being in operation at 2nd floor level toward the open passage of the plot. This poses a significant risk of workers falling from this access point, which could result in serious injuries or fatalities. | Secure these access points to ensure worker safety and prevent accidents. | 2 months | we already hire a credible civil engineer / consultant to develop and evaluate our structure requirements and remediate it accordingly. On that day our lift is not in working conditions and on maintenance. Although our cargo lits have Operational limit switches and proper closer gates with lift operator to operate safely. |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1