## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
25-Oct-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Amna Ashraf Apparels, F-748/H, Sindh Industrial Trading Estate, Karachi, Karachi City, Sindh 75400
[8 empty] | Date of Initial Inspection | [12 empty] | 25-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | DBs & Elec Protection Systems | Earthing system | The earthing system throughout the facility is inadequate. Earthing is missing from panels and final socket outlets throughout the facility. | Earthing connections should be provided for all panels, using proper clamps, lugs, and bolts, to connect the earth continuity conductor to the earth electrode. This will ensure that the panels are effectively earthed and will not become live in case of a fault. | 6 months | Most distribution boxes already have earthing connections; however, our electrical team is currently working to ensure that the earthing system is properly installed everywhere it’s required. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | DBs & Elec Protection Systems | Earthing system | In some panels where earthing connections are present the cables appear under sized. Earthing cables are not extended from panels to sockets and equipment. | Earthing cables should be extended from panels to sockets and equipment, using a suitable size and type of conductor, to provide a low-resistance path for fault currents to flow to the earth. This will ensure that any exposed metal parts of the electrical system are at the same potential as the earth and will not cause a risk of electrocution to personel. | 6 months | Our team is currently working on extending the earthing cables from the panels to the sockets and equipment. We are ensuring that we use suitable sizes and types of conductors to provide a low-resistance path for fault currents. Rest assured, we are committed to securing all electrical components so that every exposed metal part is at the same potential as the earth, minimizing any risk of electrocution to personnel. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Earthing system | The as built schematics do not show the details of the earthing system. | Provide revised as built schematics to show details of the earthing system, such as the type, size, and location of the earth electrode, the size and type of the earth continuity conductor, the earthing lead, and the earthing connections. | 6 months | We'll review the electrical diagram to ensure all details of the earthing system are included. If any information is missing, we'll provide the revised as-built schematics. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Hot Spots | Within the electrical panels at a cable termination points, there are signs of overloading and a poor connections, resulting in abnormal temperatures. | Inspect the electrical panels to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 1 month | Fault you mentioned and are actively working to resolve it. Our electrical team is addressing the issues related to abnormal temperatures, including tightening connections and redistributing loads. We will ensure all unresolved matters are taken care of promptly. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | Within the electrical panels at a cable termination points, there are signs of overloading and a poor connections, resulting in abnormal temperatures. | Create a schedule to have a thermograph survey carried out by an appropriately qualified and trained person on the entire electrical system at intervals of no less than 6 months. | 6 months | We have arranged for a qualified electrical engineer to conduct a comprehensive thermograph survey of our entire electrical system. This survey will take place at regular intervals of no less than 8 months to ensure optimal performance and safety. The engineer will also address any issues detected during the survey. Factory will share schedule for regular thermographic surveys in the facility |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Within the electrical panels at a cable termination points, there are signs of overloading and a poor connections, resulting in abnormal temperatures. | Carry out independent thermograph survey as per schedule. | 6 months | Yes, our team is also conducting the independent thermograph survey as scheduled. Factory will share thermographic survey report with Accord for review |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Lint & dust inside panel board | It was noted in several locations that there was an excessive buildup of lint, dust & dirt and cleanliness was not being maintained. | Implement a regular cleaning schedule for all electrical panels to ensure that electrical panels are cleaned, inspected, and free from lint, dust & dirt. | 1 month | Yes, our team is already implementing a regular cleaning schedule for all electrical panels, ensuring they are cleaned, inspected, and free from lint, dust, and dirt on a daily basis. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Circuit breakers | Breaker installed does not provide the connected cable protection. | Consult a qualified electrical engineer to review the entire installation and advise the correct combination of cable and breaker sizes. | 3 months | We would like to inform you that we already have a qualified electrical engineer on board, and he is currently reviewing the entire installation. We appreciate your input and will ensure that he considers the appropriate combination of cable and breaker sizes. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Circuit breakers | Breaker installed does not provide the connected cable protection. | Replace cables with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable as required by the electrical engineers report | 3 months | We are currently working on replacing the cables to ensure that the breaker size is less than the current carrying capacity of the cables, in line with the electrical engineer's report. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method (tape). | Replace the affected cables with continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or use joint boxes and appropriate connectors to join cables. | 4 months | We have replaced most of the cables and will use joint boxes as needed to ensure a direct, uninterrupted electrical connection |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust, lint & dirt. | 3 months | The electrical team is currently sealing all openings in the panels to prevent dust, lint, and dirt ingress. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | Cross-circuiting (Looping, Bunching at Moulded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. | Modify the installation so that circuits do not share breakers. This may mean the introduction of new breakers within existing panels. | 3 months | We will modify the installation to ensure that circuits do not share breakers, introducing a new distribution box as per standard. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Cabling & Wiring | Cables support and protection | Electrical outlets are installed on combustible material, in this case a wooden plank. | Ensure that all electric circuitry and outlets are mounted on non-combustible materials and separated from combustible materials. | 3 months | We identified an issue with electric circuitry and outlets being mounted on combustible materials in our factory. However, we have resolved this and are actively working to ensure it does not happen again. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Cabling & Wiring | Fixtures | Electrical outlets are installed on combustible material, in this case a wooden plank. | Conduct periodic inspection and maintenance program to ensure that no electrical wiring and components are mounted on combustible materials and maintain the records. | 3 months | We identified an issue with electric circuitry and outlets being mounted on combustible materials in our factory. However, we have resolved this and are actively working to ensure it does not happen again. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Earthing system | Earthing neutral link observed in sub-distribution board. This is an unusual arrangement. | A qualified electrical engineer to inspect, review and report on the earthing arrangements in accordance with required standard and corrective actions to be implemented. | 3 months | We already have a qualified electrical engineer who is currently inspecting, reviewing, and reporting on the earthing arrangements in accordance with the required standards. They will also identify any necessary corrective actions to be implemented. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | There is load imbalance in some panels. | Appointed a certified electrical engineer to conduct a thorough assessment of the electrical loads in the factory and update the load balance document. This should include all equipment, machinery, lighting, and any other systems that use electricity. | 3 months | We already have a qualified electrical engineer who is currently inspecting, reviewing, and reporting on the earthing arrangements in accordance with the required standards. They will also identify any necessary corrective actions to be implemented. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | There is load imbalance in some panels. | Maintain and record the electrical load balance and ensure that it is readily available for future inspections. This will ensure that the document can be easily accessed and reviewed during inspections. | 3 months | We are actively maintaining records of the electrical load balance to ensure that this information is readily available for future inspections |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Cabling & Wiring | Fixtures | Obsolete equipment is still in place at the Main Building on Level/s L00- Ground Floor, and it is unclear whether the power has been isolated to the outlets . | Disconnect power to outlets and all obsolete electrical fixtures and remove. | 3 months | The issue of obsolete equipment in the Main Building on Level 5 LOO-Ground Floor has been resolved, and the power to the outlets has been successfully isolated. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Generator, Transformer & Sub-Station Room | Battery | UPS and generator battery terminals are not protected and covered. | Cover electrical connections using suitable insulating material. | 1 month | The issue regarding the uncovered battery terminals of the UPS and generator has now been resolved. All electrical connections have been properly covered with suitable insulating material for enhanced safety. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Emergency Lighting | Provided but insufficient | Emergency lighting throughout all buildings are always on and powered through the UPS. If mains power fails at the UPS the lights will remain on, powered by the battery. If there is an issue with the UPS, all emergency lights in the building will not work. An entirely new emergency lighting system is required | Appoint a consultant to design an emergency lighting system in accordance with Pakistan Building Code and NFPA 101(6) | 3 months | Our building currently has emergency lighting powered by UPS. We are now adding additional emergency lights with independent battery backup |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The Fire Detection and Alarm System not in accordance with required standards as follows, (this list is not exhaustive):  No or antiquated fire detection and alarm system, not a listed system that does not provide alarm and notification features consistent with acceptable standards.  No or incomplete coverage of fire alarm devices in all/some areas, such as the offices on mezzanine level  Fire alarm devices not listed.  All alarm devices did not activate upon detection. The general evacuation alarm signal shall operate throughout the entire building, but there was no alarm on the ground level office area and Level 1. The fire alarm on Level 2 activated initially but then failed after 5 seconds.  Sounders inaudible due to low volume or high ambient noise in the ground level warehouse and mezzanine level.  Detectors incorrectly installed too low relative to the ceiling / roof which could cause delayed activation.  Detectors not installed top of stairs. | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Our fire detection and alarm system meets standards but requires upgrades in some areas, including adding additional sounders for improved coverage and compliance. Factory will appoint consultant and submit design documentation for an upgraded fire alarm & detections system (FADS) complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E21 + 1 month | Our fire detection and alarm system is up to the mark, and we are consulting with a specialist to assess and upgrade the system if needed. If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E22 + 4 months | We would like to confirm that the fire detection and alarm system (FADS) installed in our factory consists entirely of imported equipment and meets high-quality standards. Should there be a need for any additional installations or upgrades, we will ensure to consult with you beforehand to align with all acceptable standards. Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E23 + 5 months | We would like to confirm that the fire detection and alarm system (FADS) installed in our factory consists entirely of imported equipment and meets high-quality standards. Should there be a need for any additional installations or upgrades, we will ensure to consult with you beforehand to align with all acceptable standards. Once upgraded installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E24 + 3 months | We would like to confirm that the fire detection and alarm system (FADS) installed in our factory consists entirely of imported equipment and meets high-quality standards. Should there be a need for any additional installations or upgrades, we will ensure to consult with you beforehand to align with all acceptable standards. Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E25 + 3 months | We would like to confirm that the fire detection and alarm system (FADS) currently installed has undergone full testing and commissioning (T&C) certification. For any new installations or modifications to the system, we assure you that we will consult with you and coordinate accordingly to ensure compliance with all requirements. Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
25-Oct-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Amna Ashraf Apparels, F-748/H, Sindh Industrial Trading Estate, Karachi, Karachi City, Sindh 75400
[8 empty] | Date of Initial Inspection | [12 empty] | 25-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed at exit discharge doors on ground level, doors to access exit stairways, and along exit access pathways throughout the building. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard 1.4 & 1.5 | 1 month | We currently do not have any locking systems on the exits. However, if any are found, we will ensure they are properly removed in accordance with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | We are following the Pakistan Building Code of Conduct, including compliance with NFPA 101 and the Pakistan Accord Building Standard clauses 1.4 and 1.5. Additionally, if there are any locking systems on exit doors, we will ensure they are removed or disabled to maintain safe and easily accessible exits. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed at exit discharge doors on ground level, doors to access exit stairways, and along exit access pathways throughout the building. | Replace all exit doors, doors/gates, along egress routes and/or at exit discharge points with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard 1.4 & 1.5. | F2 + 3 months | If any doors are found not to comply with Pakistan Accord Building Standard 1.4 & 1.5, we will ensure they are replaced and modified to meet the required standards, including swinging in the direction of egress travel. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to all inspected buildings: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors - Exit stairways exposed to unprotected openings - Automatic door closers are not installed/functioning in several locations - Doors normally required to be kept closed are in the open position - Southwest interior stairway is used as storage, and not separated by 2-hr fire rated separation and opening protection (e.g., fire doors) between Mezzanine Level and Level 3. | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as required. | 1 month | We have installed fire doors in some areas, and we can also convert regular doors to include an automatic closing system if needed. Factory will prepare drawings showing proposed fire separating construction and certification for door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Provide fire rated protective enclosure to the staircase in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | 4 months | We have taken proactive steps to ensure the fire-rated protective enclosure of the staircase in accordance with the Pakistan Accord Building Standard. We have already installed fire-rated doors in some key areas, enhancing the overall fire protection. Additionally, to further strengthen safety measures, we can modify existing regular doors by adding automatic closing systems where required. This will ensure that doors remain closed in the event of a fire, preventing the spread of smoke and flames. We are committed to ensuring that all potential openings that could compromise protection are either sealed or equipped with appropriate fire-rated assemblies to comply fully with the safety standards. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies | Provide all fire doors with self-closing and self-latching devices, and push-bar panic hardware where required in accordance with Pakistan Accord Building Standard. If fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system. Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | F5 + 4 months | We want to update you regarding our current fire safety measures and the steps we are taking to comply with the Pakistan Accord Building Standard concerning fire doors. As of now, we have successfully installed five fire doors equipped with self-closing and self-latching devices. We understand the importance of these features in enhancing the safety of our premises. Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed in - Exit access from mezzanine storage area for northeast stairway - Exit access from Ground Level offices through storage and production areas - Exit access from Level 3 and Level 2 production areas need is normally via the canteen, though this is currently being used as a storage area | Exit access shall be arranged so that it is not necessary to pass through any hazardous areas and to avoid travel through intervening spaces as per Pakistan Accord Building Standard. | 4 months | While we currently have a general exit plan for our floors, we recognize the need for improvements. Moving forward, we will develop separate exit plans for each floor to enhance safety and compliance. These updated plans will ensure that all exit routes are clear of hazardous areas and provide efficient access. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit discharge | Final exit discharge at ground level does not provide safe passage/egress away from the building to a public way. Exterior exit discharge away from building from the northeast exit stairway, southeast exit stairway, and ground level exit on the west façade are exposed directly to hazards (i.e., storage) and to unprotected openings along the pathway. | Protect exit route at exterior of the building to allow a safe, free and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standards. The interior exit discharge shall lead to a free and unobstructed route to the exterior of the building by removing all storage so that the exit route and exit discharge point are readily visible, identifiable and unobstructed. | 4 months | We would like to inform you that our ground floor has four exit routes. During your recent visit, some blockchases were present, but we have since ensured that all exits are now clear and free for unobstructed passage. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Escape doors | Doors on all escape routes, including those leading to outside or away from the building, must swing in the direction of travel to an emergency exit. Doors on escape routes swinging in the wrong direction (inwards) from the mezzanine storage area to the southeast exit stairway. Additionally, on Level 3, there are two double leaf doors which should be replaced with doors that swing both ways because of the two exit stairways are either side of these doors. | Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard. | 3 months | We are considering replacing the exit doors with ones that swing in the direction of egress travel, as per the Pakistan Accord Building Standard. However, for safe and easy exit from the mezzanine floor, the door will be dismantled temporarily. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Escape stair condition | Handrails are not being provided or are defective on one or both sides of exit stairs, which can cause falls during evacuation. Handrails were only observed on one side of the southeast stairway and northeast stairway, as well as the wooden stairway connecting Level 1 to Ground Level. | Provide handrails on both sides of the exit stair in accordance with Pakistan Accord Building Standard | 2 month | Yes, we currently have handrails on one side of the exit stair. We can now provide handrails on both sides in accordance with the Pakistan Accord Building Standards. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit signage | There is insufficient exit signage throughout the building. | Provide exit signage so access to exits are marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | We have already added more exit signage throughout our facility All exits are now clearly marked and readily visible from all areas of the floor. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Escape doors | Sliding exit doors observed in production areas and on the mezzanine level where only swinging doors provide an acceptable level of risk. | Replace all sliding door(s) with side hung swinging door(s) which swing in the direction of egress travel. | 3 months | All sliding doors are non-operational and will be proper egress. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required. Observations relate to the following issues in - Floor assemblies not achieving required fire resistance ratings (Type I Construction) – e.g., storage mezzanine above Ground Level storage and production area - Openings in fire-rated floor assembly between storage ‘mezzanine’ and Ground Level below, but where the NFPA 5000 floor area limit is exceeded for mezzanines. That is, a mezzanine is not permitted to exceed one-third the open area of the room in which mezzanines are located. - Penetrations and openings in fire-rated floor assemblies. | Separate floors by fire-rated floor/ceiling assemblies in accordance with the Pakistan Accord Building Standard. | 6 months | Our safety team is currently working on addressing the issue of fire-rated floor assemblies and mezzanine area . We will update you with any results once available. Factory will prepare drawings showing proposed fire separating construction to floor openings, and submit to Accord for review prior to any rectification works. Once reviewed, fire rated separation of openings will be completed, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required. | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements | 4 months | We are currently consulting with our structural and civil engineers. Once they submit the design, we will share it with you. Factory will prepare drawings showing proposed fire separating construction to floor openings, and submit to Accord for review prior to any rectification works. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required. | Maintain fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure | F14 + 4 months | Our safety team is actively working on maintaining fire-rated floor separation, and several areas have already been protected. Once reviewed, fire rated separation of openings will be completed, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Rated Construction | Separation of shafts | Openings in floors where fire rated separations are required. Observations relate to the following issues in - Lift shaft connecting floors not separated by fire and smoke resisting construction and opening protection | Separate lift shaft by fire-rated construction with fire rated opening protective assemblies, in accordance with Accord Pakistan Standard (BCP Table 8.6.3.1). | F17 + 4 months | We have completed the fire and smoke resistance separation on two floors, with two more floors remaining for remediation. Factory will prepare drawings showing proposed fire separating construction to shafts, with details of door assembly, location in relation to escape routes and lift door operation, and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Rated Construction | Separation of shafts | Openings in floors where fire rated separations are required. Observations relate to the following issues in - Lift shaft connecting floors not separated by fire and smoke resisting construction and opening protection | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Our safety team is currently working on addressing the issue of fire-rated floor assemblies and mezzanine area . We will update you with any results once available. Fire rated separation of shaft will be completed, including brickwork/ fire rated assemblies and adequate and door operating mechanism, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies.  Different occupancy types not separated by fire and smoke resisting construction, including o Level 2 storage area (normally canteen) is not separated from adjacent production areas o Mezzanine Level storage not separated from Ground Level production area below | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies | 4 months | Our safety team is actively working on maintaining fire-rated floor separation, and several areas have already been protected. However, due to the structure of the building, it's not possible to separate the storage area, but we can implement separation for the canteen |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies - Ensure unsealed penetrations and openings are located in fire-rated separating assemblies, i | Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | F18 + 4 months | Our safety team is currently working to ensure all penetrations and openings are sealed with a firestop system or device with a minimum 1-hour rating, in full compliance with the fire resistance rating of the assembly penetrated and relevant standards. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Storage | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies - Unsealed penetrations and openings are located in fire-rated separating assemblies, including o Unprotected opening (door) between Ground Level offices and storage area o Unprotected openings (windows) between offices and storage area on Mezzanine Level | Separate storage areas by 2-hr fire-rated construction with 1.5-hr opening protective assemblies like fire rated doors. Windows assemblies not permitted. | 4 months | We will make every effort to meet the standard by ensuring separate storage areas are constructed with 2-hour fire-rated walls and 1.5-hour opening protective assemblies, such as fire-rated doors. We acknowledge that window assemblies are not permitted and will comply with this requirement. Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Storage | In process (temporary) storage piles in non-storage occupancies stored closer than 3 m (10 ft) to adjacent storage piles | Manage storage in non-storage occupancies so that each pile is less than 2.45 m (8ft) in height and less than 23m2(250ft2) in any one area, and each pile is separated by a minimum of 3.0 m (10 ft) from other storage piles, and total area of temporary storage less than 10% floor area | 1 month | Our safety team is already addressing these storage management guidelines. We are actively working on implementing measures to ensure compliance and will resolve any outstanding issues promptly. Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies.  Electrical rooms are not separated by fire and smoke resisting construction  Areas steam generators not separated by fire and smoke construction  Generator room not separated by fire and smoke resisting construction | Separate electrical room by 2-hr fire rated construction. Separate room with boiler(s) and/or steam generator(s) by 2-hr fire rated construction. Separate generator room by 2-hr fire rated construction | 4 months | We would like to confirm that we already have separate rooms for electrical equipment and steam generators, and generators, all constructed with the specified 1-hour fire-rated construction. Additionally, we are currently consulting with our safety team to explore further improvements to enhance safety in these areas. Factory will prepare drawings showing proposed fire separating construction to high-risk areas and submit to Accord for review prior to the rectification works. Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Hazardous Materials | Gas storage | Various gas cylinders noted inside and around the buildings inspected. | Up to two (2) gas cylinders (each 50 kg maximum) are permitted to be stored in an interior control area if the cylinders are adequately secured and the room is appropriately ventilated and protected as per NFPA 58. Ventilation must be direct to outside meaning the room needs to have at least one exterior wall with sufficient openings, which cannot be adjacent to exterior exits or exterior exit discharge pathways. Protection refers to 2-hr fire rated separation of the room with cylinders and assuring the cylinders and their storage room is not within 3.05 meters of an escape route or exit. | 3 months | Both cylinders are now stored in compliance with the SOP, including adequate securing, proper ventilation and separated |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
25-Oct-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Amna Ashraf Apparels, F-748/H, Sindh Industrial Trading Estate, Karachi, Karachi City, Sindh 75400
[8 empty] | Date of Initial Inspection | [12 empty] | 25-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Internal columns Main Building at Ground floor level appear to be overstressed for the applied load | (1) Appoint qualified and competent Structural Engineer to carry out DEA on full building, in accordance with the attached requirements and scope. | 1 month | We already have a qualified and competent Structural Engineer who has carried out the DEA for the entire building in accordance with the required standards and scope |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Internal columns Main Building at Ground floor level appear to be overstressed for the applied load | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | S1+3 months | We have completed the DEA report addressing all the points mentioned, including structure, loading, elements, dimensions, levels, foundations, framing, and engineering tests for material strengths and reinforcement content. Factory will submit as-built drawings to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Internal columns Main Building at Ground floor level appear to be overstressed for the applied load | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | S2+4 months | The structural engineering assessment, along with supporting calculations based on the as-built drawings and material strengths, has already been completed by the structural engineers Factory will submit detailed structural analysis based on accurate as-built drawings to Accord for review |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | Internal columns Main Building at Ground floor level appear to be overstressed for the applied load | (4) Submit proposals for retrofitting works to be undertaken to demonstrate the adequacy of the structure to Pakistan Accord for review | S3+4 months | We are currently consulting with additional engineers to determine the appropriate retrofitting methods. Once this is finalized, we will submit the proposals for review. Factory will submit details of proposed remedial works to Accord for review |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | Internal columns Main Building at Ground floor level appear to be overstressed for the applied load | (5) Carry out all retrofitting works as proposed and previously reviewed by Pakistan Accord | S4+6 months | We are currently consulting with additional engineers to determine the appropriate retrofitting methods. Once this is finalized, we will submit the proposals for review |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Potential Overstress | Highly stressed columns | Internal columns Main Building at Ground floor level appear to be overstressed for the applied load | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistan Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete | S5+1 months | We will coordinate with the structural engineer, and once we have the details, we will inform you accordingly |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Cracking | Column | Perimeter columns on the ground floor of the Main Building are significantly cracked. | Immediately remove all occupancy (people and storage) from the area identified at all levels in the building. Note that the staircase may be accessed in the case of an emergency only; as it remains an emergency exit, access must be available at all times for this purpose only | 1 months | In response to your statement, I would like to clarify that the identified area contains only the staircase, which is designated solely for use as an emergency exit. Access to this staircase must remain unobstructed at all times to ensure safe evacuation during emergencies, and it should not be used for any other purposes |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Cracking | Column | Perimeter columns on the ground floor of the Main Building are significantly cracked. | Appoint a qualified and experienced structural engineer to carry out a detailed assessment of these columns to identify the cause of the cracking and the residual load capacity. Structural Engineer to investigate whether such cracks exist in any other columns, particularly at Ground floor level. Note one possible cause of cracking may be lack of confinement of vertical bars in column through insufficient shear links | 1 months | We have already appointed a qualified structural engineer, who has conducted a detailed engineering assessment (DEA) of the entire building, including all columns. The assessment is complete, and we are currently reviewing the findings regarding the cracking and any potential issues with confinement of vertical bars. Factory will submit detailed structural analysis based on accurate as-built drawings to Accord for review |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Cracking | Column | Perimeter columns on the ground floor of the Main Building are significantly cracked | Structural Engineer to advise on required repairs to existing columns and carry out the repairs and submitted to Pakistan Accord for review. Interim measures may be required within this time frame. Assessment of this column should be carried out with reference to DEA documentation and analysis being carried out simultaneously. | 2 months | We have reviewed the DEA report and are currently consulting with our civil engineer to determine the best approach for remediation of all identified issues with the columns. We will keep you informed of the progress and any interim measures that may be required Factory will submit details of proposed remedial works to Accord for review |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Cracking | Column | Perimeter columns on the ground floor of the Main Building are significantly cracked | Carry out repairs as proposed and previously reviewed by Pakistan Accord, in agreement with DEA initiated retrofitting works. | S9+4 months | Yes, the structural engineer and civil engineer are currently reviewing the proposed repairs. We will share the details with you once the review is complete. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Structural Design | Non-engineered structure | Timber/steel mezzanine structure appears not to have had engineering input in the design and construction. | As part of DEA process, prepare accurate as-built drawings of mezzanine structure. Assess capacity of mezzanine structure to carry the applied loads, including supports/ foundations to mezzanine columns at Ground Floor. Implement any loading restrictions necessary in advance of any required remediation works. | 3 months | As part of the DEA process, we will prepare accurate as-built drawings of the mezzanine structure. We will also assess the mezzanine load-carrying capacity, including the supports and foundations of the columns at the Ground Floor. The mezzanine is designed using "H" steel as the main structure, offering flexibility and seismic resistance. Any applied loading will be factored into the assessment. Factory will submit detailed structural analysis based on accurate as-built drawings, with details of proposed remedial works, to Accord for review |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Structural Design | Non-engineered structure | Timber/steel mezzanine structure appears not to have had engineering input in the design and construction. | Identify remediation works required. Carry out remediation works to mezzanine structure. Prepare safe load plans and post in factory. | S11+3 months | We're currently carrying out some remediation works on the mezzanine structure and have posted safety posters throughout the building to ensure everyone is informed. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Structural Design | Drawings differ from as-built | The building beam framing is irregular, with many off-grid beam to beam connections and a number of beams which are cranked on plan. As-built drawings do not match conditions observed on site. There is also a large cantilever section at the front of the building with associated wall cracking due to the deflection of the cantilever. | As part of DEA process, Structural Engineer to prepare accurate as-built drawings of the as-constructed building. Carry out an assessment of all beam/ slab/ column design to determine the adequacy of the as-built structure | 6 months | We have already completed the DEA for the entire building, including the assessment of all beams, slabs, and columns to determine the adequacy of the as-built structure |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Structural Design | Drawings differ from as-built | As-built drawings do not match conditions observed on site | Complete assessment of as-built structure and identify required remediation/ strengthening works. Carry out remediation works. | 6 months | The complete assessment of the as-built structure has been finished, and remediation works are now in process |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Cracking | Column | Cracks in column on the second floor of Main Building | As part of DEA process, Structural Engineer to investigate cause of cracking and identify appropriate remediation. | 2 months | With the completion of our DEA, both the structural and civil engineers are investigating the cause of the cracking and identifying the best remediation options to address these issues |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Cracking | Column | Cracks in column on the second floor of Main Building | Carry out remediation works on column. | S15+4 months | The remediation work on the column is currently in progress. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Structural System | Lateral stability system | Steel structure at roof level (3rd Floor of the Main Building) does not have any stability system. | As part of DEA process, Structural Engineer to propose appropriate stability system for steel structure and appropriate support of metal cladding. | 3 months | The structural engineer has addressed the appropriate stability system for the steel structure and the support for the metal cladding in his report. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Structural System | Lateral stability system | Steel structure at roof level (3rd Floor of the Main Building) does not have any stability system. | Carry out remediation works required to address lack of stability system | S17+4 months | We have already completed some remediation works to address the lack of a stability system, and further suggestions from the civil engineering team are forthcoming |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S19 | Cracking | Beams | Beam cracking is visible in many locations at the upper floor levels of the Main Building (1st - 3rd Floors) | As part of DEA process, Structural Engineer to investigate cause of cracking and identify appropriate remediation | 2 months | The investigation into the cause of cracking has been completed, and remediation is currently in process |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Cracking | Beams | Beam cracking is visible in many locations at the upper floor levels of the Main Building (1st - 3rd Floors) | Carry out any remediation works required on beams. | S19+ 4 months | With the structural engineer's guidance, we are currently addressing and remediating minor issues on the beams. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Other Damage/Defects | Spalling concrete | Spalling observed on slab soffit of 3rd Floor Main Building. | Structural Engineer to propose appropriate repair solution to provide sufficient cover to reinforcement and have this implemented. | 6 months | We are continuously consulting with the structural and civil engineers to develop appropriate repair solutions for sufficient cover to the reinforcement |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S22 | Other Damage/Defects | Brickwork instability | Tall masonry panels are observed with limited lateral restraint on 3rd Floor Main Building | Structural Engineer to investigate if the panels are adequately restrained and submit proposals for strengthening if needed to Pakistan Accord for review. | 3 months | At the time of construction, we consulted with the engineer regarding the panels. Now, we are engaging with the structural engineer again to seek further confirmation and ensure that the panels are adequately restrained. Proposals for strengthening, if needed, will be submitted to the Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S23 | Other Damage/Defects | Brickwork instability | Tall masonry panels are observed with limited lateral restraint on 3rd Floor Main Building | If required, carry out remediation works as proposed. | S 22+ 3 months | We have already completed the remediation works during the construction phase with the guidance of our structural engineer |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S24 | Other Damage/Defects | Excessive deflection or vibration | Apparent lack of vibration isolation beneath generator on 3rd Floor Main Building | Structural Engineer to advise on appropriate isolation to be installed. | 3 months | With the advice of structural engineer we have already installed rubber insulation in our generator room. This has effectively reduced the vibrations. |  |  |  | Pending Verification
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S25 | Structural Design | Lack of safe load plans | Safe load plans at Ground Floor of the Main Building do not appear to take account of loading applied by mezzanine support columns | Structural Engineer to produce loading plans for all floors within the factory giving consideration to floor capacity and column capacity. Loading to be actively managed by Factory Management. | 6 months | We would like to inform you that load plans for all floors within the factory have already been produced. These plans consider the floor and column capacities, and they have been posted and pasted on each floor for easy reference. Factory management is actively managing the loading as per these plans to ensure compliance and safety. On completion of the DEA analysis based on accurate as-built drawings, provide updated safe load plans for all floors and submit to Accord for review |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixtures
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability