## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
20-Oct-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | E&M Textiles Limited, Plot 32/4, Sector 15, Korangi Industrial area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 20-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | DBs & Elec Protection Systems | Earthing system | No earth connection within electrical panels | Appoint a qualified and experienced electrical engineer to carry a full review and re-design of an earthing system for the entire building. | 4 months | Our company has an earthing system that we have done by an electrician. And plans are being made to improve the way it works. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | DBs & Elec Protection Systems | Earthing system | No earth connection within electrical panels | Earthing cables should be extended from panels to sockets and equipment, using a suitable size and type of conductor, to provide a low-resistance path for fault currents to flow to the earth. This will ensure that any exposed metal parts of the electrical system are at the same potential as the earth and will not cause electric shock to anyone who touches them. | E1 + 2 months | We have earth cables running from the LT Worm to the electric panels to all machines and switchboards and better work is being planned to ensure earthing cables should be extended from panels to sockets and equipment, using a suitable size and type of conductor. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Earthing system | No earth connection within electrical panels | Earthing connections should be provided for all panels, using proper clamps, lugs, and bolts, to connect the earth continuity conductor to the earth electrode. This will ensure that the panels are effectively earthed and will not become live in case of a fault. | E2 + 2 months | Lux and bold are used for earthing connection in all panels and all panels are cleaned. Earthing connections will be provided for all panels, using proper clamps, lugs, and bolt |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Earthing system | No earth connection within electrical panels | All machines including sewing machines should be connected with three core cables (with earth cable), and the earth wire should be connected to the metal frame of the machine. This will provide protection against electric shock if the machine develops a fault that causes the frame to become live. | E2 + 2 months | We will install three core cable and earth cable in all the machines. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Earthing system | No earth connection within electrical panels | Socket outlets should be wired in three core cable (with earth cable), and the earth wire should be connected to the metal casing of the socket. This will provide protection against electric shock if the socket or the appliance plugged into it develops a fault that causes the casing to become live. | E2 + 2 months | We will install an earth cable in the electric panel and secured it to all machines and cable trays and switchboards. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Earthing system | No earth connection within electrical panels | The as built schematics should show the details of the earthing system, such as the type, size, and location of the earth electrode, the size and type of the earth continuity conductor, the earthing lead, and the earthing connections. | 4 months | Factory will provide as built schematics that show the details of the earthing system and submit to Accord. Our ground wire can be exposed and displayed |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | No earth connection within electrical panels | A new earthing systems installation is required. | E6 + 1 months | Factory will ensure that the earthing system installation complies with Pakistan Accord Building Standard. We have double earthing system, operated by an electrician. |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that a number of electrical panels throughout the factory displayed abnormally high temperatures. Inclusive but not limited too: Production Building on level(s) L01 - 1st Floor (Office). Production Building on level(s) L00 - Ground Floor. | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 2 months | We have tightened all the loose connections in the electric panel and are working on load distribution. Factory will inspect the panel with a thermal camera and identify cause of hotspots and then implement corrective action to eliminate the problem |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that a number of electrical panels throughout the factory displayed abnormally high temperatures. Inclusive but not limited too: Production Building on level(s) L01 - 1st Floor (Office). Production Building on level(s) L00 - Ground Floor. | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 3 months. | E8 + 6 months | A thermographic visit of electric panels is being planned every three months. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Hot Spots | Thermographic testing revealed that a number of electrical panels throughout the factory displayed abnormally high temperatures. Inclusive but not limited too: Production Building on level(s) L01 - 1st Floor (Office). Production Building on level(s) L00 - Ground Floor. | Carry out independent thermograph survey as per schedule | E8 + 6 months | A thermographic visit of electric panels is being planned every three months. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Hot Spots | Production Building on level(s) L01 - 1st Floor (Office). Flex cables to portable equipment (electric kettle is this case) is cut and taped back together This taped connection is showing an elevated temperature. | Flexible cables to any portable equipment should not be cut and taped in the facility. Replace the affected cables with- continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or use joint boxes and appropriate connectors to joint cables. | E8 + 1 months | The electric kettle in the canteen has a joint in the flexible wire, this wire has been replaced |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Hot Spots | Production Building on level(s) L03 - 3rd Floor (Prayer, Storage). Breaker is showing a higher temperature than those adjacent to on the load side connection. Production Building on level(s) L01 - 1st Floor (Office). High temperature noted in breaker for air-condition unit. | Inspect the breaker in the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | E8 + 1 months | A thermographic machine is being purchased for load distribution in the electric panel of the third floor. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Hot Spots | Production Building on level(s) L03 - 3rd Floor (Prayer, Storage). Breaker is showing a higher temperature than those adjacent to on the load side connection. Production Building on level(s) L01 - 1st Floor (Office). High temperature noted in breaker for air-condition unit. | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 3 months. | E8 + 2 months | A thermographic visit of electric panels is being planned every three months. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Hot Spots | Production Building on level(s) L03 - 3rd Floor (Prayer, Storage). Breaker is showing a higher temperature than those adjacent to on the load side connection. Production Building on level(s) L01 - 1st Floor (Office). High temperature noted in breaker for air-condition unit. | Carry out independent thermograph survey as per schedule | E8 + 2 months | A thermographic machine is being purchased for load distribution in the electric panel of the third floor. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Hot Spots | Production Building on level(s) L03 - 3rd Floor (Prayer, Storage). Within the electrical panel at a cable termination point, there are signs of a poor connection and abnormal temperatures. There are signs of distress at the cable termination, indicating sustained and persistent high temperatures. | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | E8 + 2 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Hot Spots | Production Building on level(s) L03 - 3rd Floor (Prayer, Storage). Within the electrical panel at a cable termination point, there are signs of a poor connection and abnormal temperatures. There are signs of distress at the cable termination, indicating sustained and persistent high temperatures. | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 3 months. | E8 + 6 months | A thermographic machine is being purchased for load distribution in the electric panel of the third floor. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Hot Spots | Production Building on level(s) L03 - 3rd Floor (Prayer, Storage). Within the electrical panel at a cable termination point, there are signs of a poor connection and abnormal temperatures. There are signs of distress at the cable termination, indicating sustained and persistent high temperatures. | Carry out independent thermograph survey as per schedule | E8 + 6 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Loop Connection | There is cross-circuiting (Looping, Bunching at Molded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. | For any future work avoid looping and bunch of cable at MCCB/MCB or bus bar terminal, use individual circuit and overcurrent device for every incoming and outgoing circuit at the distribution boards. | 2 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Loop Connection | There is cross-circuiting (Looping, Bunching at Molded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels. | 2 months | Factory will modify each breaker separately and add new breakers. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Circuit breakers | There are several locations throughout the facility (inclusive of Production Building on level(s) L01 - 1st Floor (Office)).where damaged electrical equipment (breakers) have not been replaced. | Equipment should be isolated from the electrical distribution system (turned off) or if the equipment is required to operate it should be replaced before doing so. | 2 months | Factory will replace the broken breaker in the first floor |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Cabling & Wiring | Cables support and protection | Multi-stranded cables are not connected using lugs. | Engage qualified electricians to install appropriate lugs for the cable connections to breakers in the electrical panels | 2 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Panel/cabling/busbar | An electrical load balance document was not available during the inspection. The absence of an electrical load balance document during an inspection indicates that there might not be a record of the distribution of electrical loads in the factory. This document is crucial as it helps prevent issues like overheating, power-quality problems, and energy loss that can occur with unbalanced loads. | Create an Electrical Load Balance Document: Engage a certified electrical engineer to conduct a thorough assessment of the electrical loads in the factory. This should include all equipment, machinery, lighting, and any other systems that use electricity. | 3 months | Electricians are working on this and will create an Electrical Load Balance Document |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | DBs & Elec Protection Systems | Panel/cabling/busbar | An electrical load balance document was not available during the inspection. The absence of an electrical load balance document during an inspection indicates that there might not be a record of the distribution of electrical loads in the factory. This document is crucial as it helps prevent issues like overheating, power-quality problems, and energy loss that can occur with unbalanced loads. | Keep the electrical load balance document updated and readily available for future inspections. This will ensure that the document can be easily accessed and reviewed during inspections. | 3 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Diagrams & Drawings | Electrical layout drawing | The facility does not have updated ‘As built Electrical Layout Drawings’ (Showing outlets for light, fan, appliances, motors, etc.). | Provide updated Electrical layout drawing that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. | 4 months | Hiring an electrical engineer to provide updated electrical layout drawings |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Production Building on level(s) L01 - 1st Floor (Office), Purchase dept room, Combustible Material is being used to from part of an electrical homemade panel. Production Building on level(s) L03 - 3rd Floor (Prayer, Storage), Generator selector switch made of combustible material | Ensure that all electric circuitry, outlets and components are mounted on non-combustible materials and separated from combustible materials. | 2 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Cabling & Wiring | Splicing of cables | Several locations throughout the facility have flexible cables for equipment that have been cut and / or damaged. The cables have been jointed back together using an unsuitable method (tape). | Flexible cables should not be cut and taped in the facility. | 3 months | Complete wires will be installed by removing the flexible cable with all taping |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Cabling & Wiring | Splicing of cables | Several locations throughout the facility have flexible cables for equipment that have been cut and / or damaged. The cables have been jointed back together using an unsuitable method (tape). | Replace the affected cables with continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection | 3 months | A complete wire has been installed by removing the flexible cable with all taping |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Emergency Lighting | Provided but non-functional | Emergency lighting throughout the building, which was provided but generally did not function during the test (with a few exceptions). | Check reasons for malfunctioning and ensure full functionality of the existing emergency lighting system | 2 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Emergency Lighting | Provided but insufficient | It was not possible to determine whether adequate illumination levels are provided along egress routes due to malfunctioning of the system. | Ensure full functionality and adequate illumination levels to be provided by emergency lighting along egress routes and at exit stairs. | 3 months | Electricians are working in this work |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Emergency Lighting | Provided but non-functional | Emergency lighting throughout the building, which was provided but generally did not function during the test (with a few exceptions). | Appoint a consultant to design an emergency lighting system in accordance with Pakistan Building Code and NFPA 101. | 4 months | Factory will appoint a consultant to design the emergency lighting system as per Pakistan Building Code and NFPA 101. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The Fire Detection and Alarm System is not a listed system and does not provide complete coverage of the buildings inspected in accordance with the Pakistan Accord Building Standard. Issues observed include:  Fire detection and alarm cabling is not listed/approved fire rated  Detection devices not installed at top of interior stairway and in guard room. Otherwise, the coverage of detection devices should be reviewed/confirmed.  Some detection devices appear to be non-functional  Fire alarm panel was in ‘fire condition’ before testing commenced  Zero fire alarm audibility throughout | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Factory will appoint a competent engineer to design the system to meet Accord Standard requirements and submit for review |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E31 + 1 months | Factory will submit evidence that L/C has been opened |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E32 + 4 months | Factory will advise Accord when all materials are on site |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E34 + 5 months | Factory will submit full "as-built" documentation of the system to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E35 + 3 month | Factory Will advise Pakistan Accord when FADS installation fully completed and ready for review. |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E36 + 3 months | T&C visit will be arranged |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
20-Oct-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | E&M Textiles Limited, Plot 32/4, Sector 15, Korangi Industrial area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 20-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed at the following locations: - Exit doors to exterior stair lockable from inside and outside on all floors - Exit doors to interior stair lockable from both sides on all floors - Both gates to property locked and guarded by security, without sufficient space within property to get away from danger during a fire incident - Exit door on north side of building on Ground Level | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard | 1 month | Locking devices will be removed from all doors leading to emergency exits |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Factory will provide door mechanisms that can be easily opened from the inside where necessary |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Protection of stairs | Exits, including stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues observed during the inspection: - Interior stair is not separated by fire rated construction or opening protective assemblies on any level, e.g., interior stair is separated from offices by non-fire rated wooden panels and doors; unprotected openings to stair on lower levels exposing stair to fire pump and exterior car park - Interior stair discharges internally without protection from adjacent areas including office, storage, and lift - Exterior stair is not separated from building by opening protective assemblies, e.g., fire doors | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory will appoint a consultant to prepare drawings showing proposed fire separating construction to protect stairs and submit to Pakistan Accord for review prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Exits, including stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues observed during the inspection: - Interior stair has several windows (i.e., unprotected openings) in same location on each floor which Iist exposed to production areas - Exterior stair is exposed to unprotected openings from production and storage areas, and there is an air compressor under stairs | Provide all fire doors with self-closing and self-latching devices, and push-bar panic hardware where required in accordance with Pakistan Accord Building Standard. If fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system. Provide fire rated protective enclosure to the staircase in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F3+ 4 months | Factory will ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction by implementing proposal after review by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Exit discharge | Final exit discharge at ground level not providing safe passage away from the building to a public way. - Exit discharge pathway from interior stair to public way is not protected from car parking area, fire pumps, generators, diesel storage, and unprotected openings to Ground Level storage and production areas - Exit discharge pathway from exterior stair to public way is not protected from electrical panels, generators, diesel storage, and unprotected openings to Ground Level storage and production areas | Exit discharge pathways to be protected from non rated walls and unprotected openings as per the Pakistan Accord Building Standard | 4 months | We are planning to separate the fire pump generator and electric panel in the ground floor. Factory will protect external escape routes as per proposal submitted earlier to Accord |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | The cargo lift which opens to the interior exit stairway, as well as the lift machine room on Level 3. Options to address this issue include providing a fire-rated lift lobby around lift openings on each floor, provide opening protective assemblies for each lift opening into the stair with 2-hr fire-rated construction and 1.5-hr opening protective assemblies e.g., a fire curtain, or other solution proposed by the factory and approved by Pakistan Accord | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements | 4 months | We are planning to prepare all the documents for the cargo lift and lift machine room as part of the stair protection works |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | The cargo lift which opens to the interior exit stairway, as well as the lift machine room on Level 3. | Provide fire-rated separation between staircase enclosure and lift in accordance with the Pakistan Accord Building Standard, implementing the previously reviewed design proposal. | F6 + 4 months | Factory will ensure all emergency escape stairs are fire separated from cargo lift and machine room with 2 hour fire separating construction by implementing proposal after review by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, which was observed on Level 3 where occupants would need to pass from production areas through a storage area to access the exterior stairway. | Exit access shall be arranged so that it is not necessary to pass through any hazardous areas and to avoid travel through intervening spaces as per Pakistan Accord Building Standard. | 4 months | Factory will implement any changes required to avoid passing through high-risk area We are planning an emergency stairwell from the sample department. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Escape doors | Two sliding exit doors observed on Ground Level (one on north side of building; one on south side of building). | Door should be side hung and leaves should swing in the direction of egress travel | 3 months | We are planning to replace both the sliding doors of the cutting department |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit signage | Insufficient exit signage, which was observed, throughout the building, especially with regards to signage that indicates the direction occupants should travel to reach an exit. Additionally, there is an exit sign from the exterior exit discharge from the exterior stair pointing to the neighbouring property which is not an actual exit. | Remove any misleading exit signage and provide exit signage so access to exits are marked by approved readily visible signs along full length of the escape route. | 1 month | Factory will remove any misleading signage |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit signage | Insufficient exit signage, which was observed, throughout the building, especially with regards to signage that indicates the direction occupants should travel to reach an exit. | Provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits. | 3 months | Factory will provide exit signage to comply with BCP 10.15.1, 10.15.2 and 10.15.3 |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Escape stair condition | Handrails not being provided on both sides of exit stairs, which can cause falls during evacuation. It was observed that handrails are only provided on one side of both interior and exterior stairways | Provide handrails on both sides of the exit stair in accordance with Pakistan Accord Building Standard. | 2 month | Handrails are being installed on both sides of the entrance stairs |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Fire Rated Construction | Separation of shafts | Openings in floors from the cargo lift where fire rated separations are required. | Maintain fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure. Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Facility will prepare drawings showing the proposed fire separation details of vertical shafts and submitted to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Rated Construction | Separation of shafts | Openings in floors from the cargo lift where fire rated separations are required. | Provide fire rated protective enclosure to the staircase in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F13+ 4 months | Provide 2-hour fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Fire Rated Construction | Storage | Separate storage by fire and smoke resisting construction and opening protective assemblies. - Level 1 storage room adjacent to conference room and offices is not separated - Ground Level storage needs to be separated from the production area or limited to 10% of the floor area | Manage storage in non-storage occupancies so that each pile is less than 2.45 m (8ft) in height and less than 23m2 (250ft2) in any one area, and each pile is separated by a minimum of 3.0 m (10 ft) from other storage piles, and total area of temporary storage less than 10% floor area. | 1 month | Factory will provide a plan showing how in-process storage will be arranged to meet limitations for storage in non-storage areas |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Rated Construction | Storage | Separate storage by fire and smoke resisting construction and opening protective assemblies. | Where in-process storage limitations cannot be met, separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. | 4 months | Factory will provide separation of storage areas with 2-hour fire rated construction where in-process storage limitations cannot be met, in accordance with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. - Level 3 childcare room, production areas, and prayer area should all be separated from each other | Level 3 Childcare room and Level 1 storage room should be separated and on the route to an exit, preferable close to the exit on ground floor, so that no has to move against the flow to collect children during an evacuation. | 4 months | Factory will prepare a plan and drawings showing showing the proposed separation details. These shall be submitted to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors). A solution needs to be found to separate the childcare room from the production area taking account of lack of space |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. | Provide fire rated separations between different occupancy types in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | F17 + 4 months | Factory will provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Exterior fire pump house at Ground Level - Steam generators on Level 3 (along exit access) and Mezzanine Level (open to production) - Generator and electrical panels at Ground Level | Provide fire rated separations between high-risk plant areas and adjacent areas in accordance with Pakistan Accord Building Standard; ensure that any openings that could compromise the protection are blocked up or provided fire rated protective assemblies. | 4 months | Facility will prepare drawings showing the proposed fire separation details of high fire hazard areas. These shall be submitted to Accord for review prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Separation of high-risk areas | Portable generators were observed in the prayer room on Level 3. Portable generators shall be operated, refuelled, and maintained outside the building or in a protected area if that room has been constructed for such use | Remove portable generators from production and storage areas. | 1 month | The portable generators in the prayer room on level 3 have been removed |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Separation of high-risk areas | Portable generators were observed in the prayer room on Level 3. | Permanently relocate the portable generators in locations and with required enclosure to meet the requirements of the Pakistan Accord Building Standard. | F19 + 4 months | The portable generators in the prayer room on level 3 have been removed |  |  |  | Pending Verification

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
20-Oct-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | E&M Textiles Limited, Plot 32/4, Sector 15, Korangi Industrial area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 20-Oct-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Cracking | Beams | Floor area in north-west corner of plan cantilevers out from main structural frame and is in poor condition, with extensive cracking and concrete spalling. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, in such cases, Building Engineer to investigate cause of cracking and identify appropriate remediation. Investigation shall include confirmation of reinforcement in the beams and design assessment based on the as-constructed building and loading. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | Factory will appoint a structural engineer to assess the cause of cracking and submit proposal for remediation works to Accord for review. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Cracking | Beams | Floor area in north-west corner of plan cantilevers out from main structural frame and is in poor condition, with extensive cracking and concrete spalling. | Carry out remediation works as required. | S1 + 4 months | Factory will carry out remediation works if needed The exterior of the building on the northwest corner of the floor, where the gents washrooms are located, is undergoing plastering and cracking repairs. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Column | Cracking on the 2nd floor columns is observed due to potentially a lack of tie beam. | Remove sections of plaster finish from the columns at the locations of cracks and investigate if cracks penetrate the RC columns. If cracks penetrate through the RC columns, in such cases, Building Engineer to investigate cause of cracking and identify appropriate remediation. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | Factory will appoint a structural engineer to assess the cause of cracking and submit proposal for remediation works to Accord for review. 2nd floor has cracks due to low tie beam for which we are hiring a building engineer to check. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Column | Cracking on the 2nd floor columns is observed due to potentially a lack of tie beam. | Carry out remediation works if required. | S3 + 4 months | Factory will carry out remediation works as needed There is a crack in the second floor column which is being repaired. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Other Damage/Defects | Spalling concrete | Soffit of the roof RC slab supporting the water tank is cracking and spalling. | Building Engineer to propose an appropriate repair solution to provide sufficient cover to reinforcement. Consider providing a waterproofing layer over the roof slab to prevent water ingress. Submit the proposed remedial works to the Pakistan Accord for review. | 3 months | Hiring an engineer to suggest a suitable solution to repair the water tank to prevent water ingress and to provide a waterproof layer on the roof slab. Factory will submit report of assessment and proposed remedial works to Accord for review |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Spalling concrete | Soffit of the roof RC slab supporting the water tank is cracking and spalling. | Complete the repair works. | S5 + 3 months | The repair work will completed as soon as possible based on previously reviewed proposal |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Cracking | Beams | Consistent and repeated beam cracking on primary beams at multiple locations. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, in such cases, Building Engineer to investigate cause of cracking and identify appropriate remediation. Investigation shall include confirmation of reinforcement in the beams and design assessment based on the as-constructed building and loading. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | Hiring a building engineer to investigate the cause of cracking and identify relevant information and submit the design and specifications to Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Cracking | Beams | Consistent and repeated beam cracking on primary beams at multiple locations. | Carry out remediation works if required. | S7 + 4 months | There are cracks in the columns at many places in the building, which are being repaired. Factory will repair cracking based on reviewed proposal |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Structural Design | Lack of safe load plans | No safe load plans posted in the factory | Building Engineer to prepare safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. Safe load plans to be posted on the walls of all floor levels. | 6 months | Hiring a building engineer to prepare loading plan for each floor keeping in mind floor capacity and column capacity. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Structural Design | Documentation unavailable | Drawings do not match with the current arrangement of the structure. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | We are hiring a building engineer to visit the factory and correct all the documents |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Cracking | Non structural | Cracking in an internal non-structural brickwork walls at the 3rd floor level was observed. | Propose the remedial works, and once reviewed by Accord, implement the remedial works. | 6 months | Factory will propose remedial works and submit to Accord for review. Cracking repairs are being carried out in the interior non-structural brick walls at the third floor level |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
New | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
New | Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
New | Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1