## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
28-Oct-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Fashion Knit Industries, Plot No. F-240 S.I.T.E., Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2023-10-28
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | DBs & Elec Protection Systems | Earthing system | Block A on level(s) L00 - Ground. The earthing system is inadequate: Earthing cables are not extended from panels to sockets and equipment, Earthing connections are missing from some panels, Sewing machines are connected with two core cables (no earth cable) & Socket outlets are wired in two core cable (no earth cable). | Hire a qualified and experienced electrical engineer to carry a full design of an earthing system for the entire building. | 6 months | Facility will design earthing system for the entire building through certified engineer within the given timeline and submit documentation to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | DBs & Elec Protection Systems | Earthing system | Block A on level(s) L00 - Ground. The earthing system is inadequate: Earthing cables are not extended from panels to sockets and equipment. | Earthing cables should be extended from panels to sockets and equipment, using a suitable size and type of conductor, to provide a low-resistance path for fault currents to flow to the earth. This will ensure that any exposed metal parts of the electrical system are at the same potential as the earth and will not cause electric shock to anyone who touches them. | 6 months | Facility has taken step to extend the earthing cables from panel to sockets and other equipments. Furthermore factory also provided electrical safety & hazard training in their induction training program on daily basis in order to reduce the risk of electrical shock. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Earthing system | Block A on level(s) L00 - Ground. The earthing system is inadequate: Earthing connections are missing from some panels. | Earthing connections should be provided for all panels, using proper clamps, lugs, and bolts, to connect the earth continuity conductor to the earth electrode. This will ensure that the panels are effectively earthed and will not become live in case of a fault. | 6 months | Factory has taken corrective action and provided the earthing connection where required. Furthermore, factory has also maintained compliance checklist on monthly basis to check safety of electrical panels (e.g. Proper earthing, labeling, rubber matt etc) |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Earthing system | Block A on level(s) L00 - Ground. The earthing system is inadequate: Sewing machines are connected with two core cables (no earth cable). | All machines including sewing machines should be connected with three core cables (with earth cable), and the earth wire should be connected to the metal frame of the machine. This will provide protection against electric shock if the machine develops a fault that causes the frame to become live. | 6 months | Facility has taken corrective action and made all sewing machines connected with three core cables (with earth cable), and the earth wire connected to the metal frame of the machine. Furthermore factory also provided electrical safety & hazard training in their induction training program on daily basis in order to reduce the risk of electrical shock |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Earthing system | Block A on level(s) L00 - Ground. The earthing system is inadequate: Socket outlets are wired in two core cable (no earth cable). | Socket outlets should be wired in three core cable (with earth cable), and the earth wire should be connected to the metal casing of the socket. This will provide protection against electric shock if the socket or the appliance plugged into it develops a fault that causes the casing to become live. | 6 months | Facility has taken corrective action and made all Socket outlets wired in three core cable (with earth cable), and the earth wire connected to the metal casing of the socket. Furthermore factory also provided electrical safety & hazard training in their induction training program on daily basis in order to reduce the risk of electrical shock |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Earthing system | Block A on level(s) L00 - Ground. The earthing system is inadequate: Earthing cables are not extended from panels to sockets and equipment, Earthing connections are missing from some panels, Sewing machines are connected with two core cables (no earth cable) & Socket outlets are wired in two core cable (no earth cable). | The as built schematics should show the details of the earthing system, such as the type, size, and location of the earth electrode, the size and type of the earth continuity conductor, the earthing lead, and the earthing connections. | 6 months | Facility has already schematic diagrams of some panels but some panel diagrams are remaining that will be completed within the given timeline. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | In Block B it was observed that some earth cables have not been connected | Connect all earth cables into earthing terminals within panels. | 6 months | Facility has taken corrective action and connected all earth cables with earthing terminals in panels. Furthermore, factory has made checklist to inspect all the panels on monthly basis. |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | Through the facility body earthing missing from the metical frame of the panels. This was noted in several locations | Connect all metal bodies of electrical panels to the earth terminals within electrical panels. | 6 months | Facility has taken corrective action and connected all metal bodies of electrical panel to the earth terminals in panels. Furthermore, factory has made checklist to inspect all the panels on monthly basis. |  |  |  | Pending Verification
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility where the flexible cables have been connected to other cables incorrectly. | Replace connections / cables with a manufactured product in compliance with a recognised product standard. | 4 months | Facility has taken corrective action and inspected all the cables and connection along with internal team and Replaced connections / cables with a manufactured product compliant according to the standard. |  |  |  | Pending Verification
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method (tape). | No more cables be cut and taped in the facility. | 4 months | Facility has taken corrective action and remove all the lose connection of the cables. Furthermore, factory has maintained checklist to inspect all the loose wiring on monthly basis. |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method (tape). | Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. | 4 months | Facility has taken corrective action and replaced all affected cables like where lose joints are present, appropriate connector has been installed and where cables has to be replaced, we have installed new cables with appropriate length. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Circuit breakers | Block C on level(s) L01 - First. - The Breaker installed does not provide connected cable protection. - 6mm2 connected to a 60A breaker. - It was also noted during a review of the as built SLD that other cables are not protected by the breakers installed. | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes. | 3 months | Facility will consult a third party engineer to review the entire installation of connections and cable wires with in the given timeline. |  |  |  | Pending Verification
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Circuit breakers | In several locations in the facility breakers installed do not provide connected cables protection eg. 32A breaker connected to a 4mm2 cable. | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes. | 3 months | Facility will consult a third party engineer to review the entire installation of connections and cable wires with in the given timeline. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Hot Spots | Block A on level(s) L00 - Ground. The temperature with the bank of light switches was slightly elevated to the other switches, this could be because of loose connections within the switch. | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 01 month | Facility will inspect all electrical panel to analyse the root cause of abnormal temperatures within the given timeline. |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Hot Spots | In Block A the internal of the breakers is showing an elevated temperature. | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 6 months | Facility will inspect all electrical panel to analyse the root cause of abnormal temperatures within the given timeline. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Cabling & Wiring | Cable size | The electrical single line diagram (SLD) was checked for cable sizing. It was noted that some breakers installed do not provide the connected cable protection. The SLD isn't printed at a size that is legible. | Replace cables with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 3 months | Facility has taken corrective action and change the cable as per recommended size. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Cabling & Wiring | Cable size | The electrical single line diagram (SLD) was checked for cable sizing. It was noted that some breakers installed do not provide the connected cable protection. The SLD isn't printed at a size that is legible. | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes. | 3 months | Factory has taken corrective action and has corrected all combination of cables and breaker sizes. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Cabling & Wiring | Cable size | Block B on level(s) L00 - Ground. The Breaker installed does not provide connected cable protection. The cable in question shows an elevated temperature. | Replace cables with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 3 months | Factory has taken corrective action and has corrected the size of cable by replacing it. |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Cabling & Wiring | Cable size | Block B on level(s) L00 - Ground. The Breaker installed does not provide connected cable protection. The cable in question shows an elevated temperature. | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes. | 3 months | Factory has taken corrective action and has corrected all combination of cables and breaker sizes. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Cabling & Wiring | Cables support and protection | In several locations throughout the facility electrical panels openings are not correctly sealed. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 3 months | Factory has taken corrective action and conducted internal audit electrical panel of all over factory and sealed it with plates/glands to prevents from dust & dirt. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Cabling & Wiring | Cables support and protection | Block C on level(s) L00 - Ground. Electrical equipment is not installed correctly | Install equipment / faceplate correctly. | 3 months | Factory has taken corrective action and has install equipment/faceplate correctly. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Cabling & Wiring | Cables support and protection | At the panel supplying the fire pumps there are cables that are not correctly fixed in place to prevent movement. Protection isn't provided to prevent mechanical damage to cables. | Correctly terminate all cabling in and out of the panel. Secure all cables to a method of cable containment (for example using a cable gland). | 3 months | Factory has taken corrective action and conducted internal audit of all electrical panel to check out the non conformities. Furthermore factory also have installed cable gland where needed. |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Cabling & Wiring | Cables support and protection | External Area on level(s) L00 - Ground. - Cables are not correctly fixed in place to prevent movement. - Protection isn't provided to prevent mechanical damage to cables | Provide protection to prevent cables being walked on that could cause damage to the cables. | 3 months | Factory has taken corrective action and provided protection to prevent cables being walked on that could cause damage to cables. |  |  |  | Pending Verification
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | DBs & Elec Protection Systems | Circuit breakers | It was observed that breakers were being used as switching devices (turning equipment on/off) in the generator room. Breakers are designed to be installed within electrical panels; some breakers are installed on walls. Outside panels, breakers have exposed electrical connections. | The device is to be changed for a suitable switching device i.e., fused switched isolator. | 3 months | Factory has taken immediately corrective action and changed the switching device with the suitable one. |  |  |  | Pending Verification
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Generator, Transformer & Sub-Station Room | Room separation | Block A on level(s) L01 - First. - UPS and batteries are in a shared location with the office kitchen. | Provide a separate space or enclosure for the electrical equipment that will prevent workers coming into contact with the equipment | 3 months | Factory has taken corrective action and made the separate space for the electrical equipment to prevent the worker coming into contact with the electrical equipment. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Cabling & Wiring | Cable trench and channel cleanliness | It was noted in several locations that the cleanliness was not being maintained within the electrical cable containment. | Initiate a regular maintenance and cleaning schedule for all electrical panels and containment. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. Seal all openings, covers and lids in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 2 months | Factory has taken corrective action and conducted internal audit of all electrical equipments, their cleaning, dust, fluff and dirt. Furthermore factory has also made checklist for inspection in order to prevent any hazard. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Diagrams & Drawings | Electrical layout drawing | An electrical load balance document was not available during the inspection. | Create an Electrical Load Balance Document: Engage a certified electrical engineer to conduct a thorough assessment of the electrical loads in the factory. This should include all equipment, machinery, lighting, and any other systems that use electricity. | 8 months | Factory has taken corrective action and hired a certified electrical engineer to conduct a thorough assessment of the electrical loads in the factory including all equipment, machinery, lighting, and any other systems that use electricity. Factory will Submit documentation to Accord for review. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Diagrams & Drawings | Electrical layout drawing | The absence of an electrical load balance document during an inspection indicates that there might not be a record of the distribution of electrical loads in the factory. This document is crucial as it helps prevent issues like overheating, power-quality problems, and energy loss that can occur with unbalanced loads. | Keep the electrical load balance document updated and readily available for future inspections. This will ensure that the document can be easily accessed and reviewed during inspections. | 8 months | Factory has taken corrective action and keep the electrical load balance document updated and readily available for future inspections. It will ensure that the document can be easily accessed and reviewed during inspections. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Emergency Lighting | Independent power source | Emergency lighting throughout all buildings. - Emergency lighting is powered from the same source that supplies the normal lighting | Emergency Lighting to be powered from a source independent of supplying the normal lighting in accordance with BCP Ch 10.14.1.1 and NFPA 101, on failure of normal lighting supply | 6 months | Factory will powered all the emergency lights with independent source within the given timeline. |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Emergency Lighting | Provided but insufficient | This relates to emergency lighting throughout all buildings. - Manual on-off switch is provided for emergency lighting units. | Provide emergency lighting that automatically turns on within 1s of the failure of the normal lighting supply. | 3 months | Factory will correct all system of emergency lightning to be turn on within the 1s of the normal light supply within the given timeline. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Emergency Lighting | Provided but insufficient | This relates to emergency lighting throughout all buildings. - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs | Provide additional emergency fixtures to supply adequate illumination along the means of egress. | 3 months | Factory has taken corrective action and updated the checklist of emergency lights in order to cross check the adequate supply. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. Some of the related issues include: Incomplete coverage of fire alarm devices in all/some areas, e.g., - Cargo EMR at roof level - Level 2 of building B back structural bay - Entrance area to Building B on Ground lvl - Exterior rooms north of Building B - Detectors not installed top of stairs - Sounders inaudible due to low volume or high ambient noise in prayer room on Level 1 and in fire alarm room on Ground Level - Audible signals for fire alarm notification are not distinctive from audible signals used for other purposes. | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Factory will submit design documentation for a FADS system to Pakistan Accord to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E32 +1 month | Factory will submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E33 + 4 month | Factory will submit documentation to Pakistan Accord demonstrating that all materials for installation of the FADS are inhoused |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E34 + 5 month | Factory will submit full "as-built" documentation of the system to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E35 +3 months | Factory will advise Pakistan Accord when SUPS installation fully completed and fully functional for verification inspection |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E36 + 3 months | Factory will arrange verification of their FADS by Accord Pakistan within the given timeline. |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 148 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 149 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 151 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 152 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
28-Oct-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Fashion Knit Industries, Plot No. F-240 S.I.T.E., Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2023-10-28
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed at numerous locations. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | Factory will change all non -compliant locking features with the compliant one in accordance with accord pakistan. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed at numerous locations. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Factory will change all non -compliant locking features with the compliant one in accordance with accord pakistan. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Doors on all escape routes, including those leading to outside or away from the building, must swing in the direction of travel to an emergency exit. Doors on escape routes were observed to be swinging in the wrong direction (inwards) across all buildings. | Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard | 3 months | Factory will change all non -compliant door swinging with the compliant one in accordance with accord pakistan. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Sliding exit doors observed in several locations throughout the three buildings where only swinging doors provide an acceptable level of risk. | Replace sliding door(s) with side hung swinging door(s) which swing in the direction of egress travel | 4 months | Factory will take corrective action, conduct internal audit all over the facility to inspect & replace sliding doors with side hung swinging door. |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to all inspected buildings: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors - Exit stairway exposed to unprotected openings - Penetrations into/through exit stair protective enclosure - Automatic door closers are not installed/functioning in several locations | Install, or repair, automatic closing mechanisms, as needed. | 3 months | Factory will conduct visit of all over the factory in order to inspect the exit doors and will install Automatic Door Closer at exit doors of all departments. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. - Automatic door closers are not installed/functioning in several locations | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs; - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | Factory will submit the proper diagram showing the fire door, fire equipments and fire rated walls and roof for all stairways within the given timeline. Documentation for fire door assemblies listing, fire rating and door opening mechanisms will be provided to Accord for review |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | F7 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. . | F6 + 4 months | Factory fire rated construction for separation of the stairs, and install fire doors will install door with automatic closer mechanism at all stairs to comply with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | [10 empty] | F8 | Means of Escape | Protection of stairs | Two cargo lift shafts in Building B which are not protected by fire and smoke resistant construction and are open into the nearby escape stair between Buildings B and C. Options to address this issue include providing a fire-rated lift lobby around lift openings on each floor, provide opening protective assemblies for each lift opening into the stair with 2-hr fire-rated construction and 1.5-hr opening protective assemblies e.g., a fire curtain, or other solution proposed by the factory and approved by Pakistan Accord. | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory will submit drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | Two cargo lift shafts in Building B which are not protected by fire and smoke resistant construction and are open into the nearby escape stair between Buildings B and C. | Provide fire-rated separation between staircase enclosure and lift in accordance with the Pakistan Accord Building Standard, implementing the previously reviewed design proposal. | F8 + 4 months | Provide 2-hour fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit discharge | Obstructions along means of egress which reduce exit capacity. Two observations were made of temporary obstructions that reduced the exit capacity of the exterior exit discharge pathway on the east side of the building | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments | 1 months | Factory will clear all the obstacles from all pathways. Furthermore factory has also maintained checklist to inspect all pathways of the factory. |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit discharge | Obstructions along means of egress which reduce exit capacity. Two observations were made of temporary obstructions that reduced the exit capacity of the exterior exit discharge pathway on the east side of the building | Remove obstruction, rearrange means of egress, or provide an additional means of egress to provide sufficient exit capacity | 3 months | Factory will clear all the obstacles from all pathways. Furthermore factory has also maintained checklist to inspect all pathways of the factory. |  |  |  | Pending Verification
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit access | This relates to exit access from the canteen on Level 2 through the adjacent storage area, a higher risk intervening space | Prepare drawings showing how access to the exit will be arranged so that it is not necessary to pass through a higher risk area | 4 months | Factory will prepare drawings showing how it will provide a path to the exit without passing through a higher risk area |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit access | This relates to exit access from the canteen on Level 2 through the adjacent storage area, a higher risk intervening space | Exit access shall be arranged so that it is not necessary to pass through any hazardous areas and to avoid travel through | F12+ 4 months | Factory will provide an alternative route or protected path to the exit according to the layout and documents reviewed by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Final exit discharge at ground level which is not protected and therefore not providing safe passage away from the building to a public way. - The exterior exit discharge pathways on the east and west sides of the buildings, as well as in those in middle of the buildings (between buildings A, B, C) on Ground Level, are exposed directly to unprotected openings - The exterior exit discharge pathway on the west side of Buildings C passes directly by the exterior fire pump | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes | 4 months | Factory will prepare drawings showing how it will provide protected routes from the buildings exits between buildings A, B and C, and submit to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit discharge | Final exit discharge at ground level which is not protected and therefore not providing safe passage away from the building to a public way | Ensure external exit discharge routes are adequately fire separated from the rest of the building | F14 + 4 months | Factory will provide protective routes according to Pakistan Accord Building Standard and as per proposal reviewed by Accord. |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit signage | Exit signage. It was observed that: - There is insufficient exit signage | Provide exit signage so access to exits are marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | Factory will rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standards and BCP 10.15.1, 10.15.2 and 10.15.3 |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit signage | Exit signage. It was observed that: - There is misleading or partial exit signage | Remove any misleading exit signage and/or floor markings and provide exit signage so access to exits are marked by approved readily visible signs along full length of the escape route | 3 months | Factory has taken corrective action immediately and removed misleading signages and paste exit signages at all location where needed. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Suppression | Standpipe system | Standpipe system for firefighting operations. - These buildings do not have a Class I standpipe system but require one because the buildings are not separated, are not sprinklered, are more than 2 storeys, and have a collective floor area greater than 2,325 m2 - Insufficient number of risers - Insufficient number of standpipe hose connections | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24 | 4 months | Factory will submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 25 |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Suppression | Standpipe system | These buildings do not have a Class I standpipe system | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F18 + 1 month | Factory will submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Suppression | Standpipe system | These buildings do not have a Class I standpipe system | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F19 + 4 months | Factory will submit documentation to Pakistan Accord demonstrating that all materials for installation of the SUPS are inhoused |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Suppression | Standpipe system | These buildings do not have a Class I standpipe system | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F20 + 3 months | Factory will submit full "as-built" documentation of the system to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Standpipe system | These buildings do not have a Class I standpipe system | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F21 + 3 months | Factory will advise Pakistan Accord when SUPS installation fully completed and fully functional for verification inspection |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Standpipe system | These buildings do not have a Class I standpipe system | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F22+ 3 months | Factory will provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Fire pumps | Fire pump and water supply which currently support the hydrant / standpipe system. - No electric fire pump - Fire pump and fire pump control equipment not listed - Arrangement of water supply and fire pump means the fire pump is in negative suction; did not confirm adequate water supply | Provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Accord for review | 4 months | Factory will provide design for electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Fire pumps | Fire pump and water supply which currently support the hydrant / standpipe system. - No electric fire pump - Fire pump and fire pump control equipment not listed - Arrangement of water supply and fire pump means the fire pump is in negative suction; did not confirm adequate water supply | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system | 18 months | Factory will provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Water supply | Fire pump and water supply which currently support the hydrant / standpipe system. - Arrangement of water supply and fire pump means the fire pump is in negative suction; did not confirm adequate water supply | Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system | 18 months | Factory will provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Separation of shafts | This relates to openings in floors where fire rated separations are required. Observations relate to the two cargo lifts open to building B having lift shafts connecting all floors not separated by fire and smoke resisting construction and opening protection | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will prepare drawings showing the proposed fire separation details of vertical shafts and submit to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Rated Construction | Separation of shafts | This relates to openings in floors where fire rated separations are required. Observations relate to the two cargo lifts open to building B having lift shafts connecting all floors not separated by fire and smoke resisting construction and opening protection | Provide 2-hour fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord. | F27 + 4 months | Factory will provide fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Storage | In process storage in non-storage occupancies, where - Miscellaneous (in process) storage areas exceed 10% of the floor area, meaning it is not accessory to the other occupancy type - Miscellaneous (in process) storage areas exceed 23m² (250ft²) in one area (non-sprinklered buildings) - Miscellaneous (in process) storage areas are not separated from other storage areas by at least 3m (10ft). This is not always achieved, examples of non-compliances include (list not exhaustive): - Lack of fire separation between storage area and production area at 1st, 2nd and 3rd floor level | Prepare drawings showings proposed fire separation details of vertical shafts according to Building Code of Pakistan Table 8.6.3.1. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors enclosing the shafts - Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Factory will identify all designated storage areas and provide a drawing showing areas that can be provided to meet in-process storage limitations and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, the drawing will present the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works.. |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Storage | Storage does not always meet in-process storage requirements and needs to be separated from non-storage occupancies | Provide 2-hour fire rated construction, including 90-minute fire rated doors assemblies to lift shafts according to the layout and documents reviewed by Pakistan Accord. | F29 + 4 months | Factory will provide 2-hour fire rated construction, including 90-minute fire rated doors assemblies to separate storage areas according to the layout and documents reviewed by Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Electrical room not separated by fire and smoke resisting construction, including LT room on Ground Level of Building B and electrical panel area on Ground Level of Building A | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | 4 months | Facility will made fire rated walls around LT room and electric room within the given timeline. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Fire pumps not separated by fire and smoke resisting construction that could be negatively affected during a fire incident Generator room not separated by fire and smoke resisting construction | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | F31 + 4 months | Factory will made fire rated wall and roof around Fire Pump area with Listed Fire Door. |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Separate generator room by 2-hr fire rated construction | Separate electrical rooms by 2-hr fire rated construction. | 4 months | Factory will made fire rated wall and roof around Generator room with Listed Fire Door. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Hazardous Materials | Chemicals storage | Storage, handling, and use of flammable and combustible liquids and/or solids including diesel storage in generator room and fire pump area and machine oil storage in accessory building north of building B. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. | 3 months | Factory will located all required MSDS MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements, and submit to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Hazardous Materials | Chemicals storage | Storage, handling, and use of flammable and combustible liquids and/or solids including diesel storage in generator room and fire pump area and machine oil storage in accessory building north of building B. | Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms | 3 months | Factory will prepare drawings showing the proposed fire separation of chemical storage areas and submit to Accord for review. |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Hazardous Materials | Chemicals storage | Storage, handling, and use of flammable and combustible liquids and/or solids including diesel storage in generator room and fire pump area and machine oil storage in accessory building north of building B. | Implement the plan for protection of chemical storage areas on site. All chemical storage areas to be compliant with Accord Standard | F25+ 3 months | Factory will Implement the plan for protection of chemical storage areas on site so that all chemical storage areas comply with Accord Standard |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Hazardous Materials | Diesel storage | Storage, handling, and use of flammable and combustible liquids and/or solids including diesel storage in generator room and fire pump area and machine oil storage in accessory building north of building B. | Interior diesel storage (maximum 1265 litres on ground level) is permitted if it is fire separated from other areas by 1-hr fire rated construction and stored in accordance with other requirements of NFPA 30. Diesel storage is permitted within generator rooms and fire pump rooms if adequately stored and that room is separated from adjacent occupancies. | 3 months | Facility will made separate fire rated walls and roof for diesel storage within the given timeline and according to requirements of NFPA 30. |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2023-10-28
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Fashion Knit Industries, Plot No. F-240 S.I.T.E., Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2023-10-28
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Potentially insufficient vertical reinforcement in the Building B RC columns at Ground and first floor levels. Ferroscan at the Ground floor level indicates 1no. vertical reinforcement at mid-face over each side of column. This reduces the strength of columns in bending and shear. Design calculations of Building B columns indicate a requirement of minimum 1% vertical reinforcement. Provided reinforcement is circa 0.45%. | Building Engineer to determine the in-situ numbers & size of vertical reinforcement installed in the columns of Building B. Submit the findings to the Pakistan Accord for review. | 2 months | Detailed ferro scanning was performed for columns of Building-B at Ground Floor and First Floor Columns. Factory will submit details to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Potentially insufficient vertical reinforcement in the Building B RC columns at Ground and first floor levels. Ferroscan at the Ground floor level indicates 1no. vertical reinforcement at mid-face over each side of column. This reduces the strength of columns in bending and shear. Design calculations of Building B columns indicate a requirement of minimum 1% vertical reinforcement. Provided reinforcement is circa 0.45%. | Building Engineer to carry out the structural assessment of Building B columns for the gravity and lateral loads in accordance with the insitu reinforcement located in the columns. | 3 months | Factory will appoint building engineer to carry out a structural assessment and submit to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Potentially insufficient vertical reinforcement in the Building B RC columns at Ground and first floor levels. Ferroscan at the Ground floor level indicates 1no. vertical reinforcement at mid-face over each side of column. This reduces the strength of columns in bending and shear. Design calculations of Building B columns indicate a requirement of minimum 1% vertical reinforcement. Provided reinforcement is circa 0.45%. | Complete the remedial works if required. Continue to implement safe load plans. | S2 + 3 months | Factory will submit details of building engineer assessment to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Structural System | Vertical load path | Column drop panels are missing at the 1st floor level of Building A along grid line H | Building Engineer to complete an assessment of Building A 1st floor slab for punching shear check as column drop panels do not exist along GL-H. Note: from a visual inspection, it appears to be that there is an RC beam along GL-H, Building Engineer to verify its existence from some site opening up works, confirm the reinforcement and capacity to support the slab loads. Submit the findings to Pakistan Accord for review. | 6 months | It was a drafting error to show the drop panels there. In actual drop panels are not present at site, instead there is a peripheral beam. The above corrections are made in drawings. Factory will submit corrected drawings to Accord for review |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Structural System | Lateral stability system | Diagonal cracks in the non-structural brickwork walls are observed in Building A | Building Engineer to carry out a stability analysis of Building A against the lateral loads and propose additional stability system if required. Submit the proposed remedial works to the Pakistan Accord for review. | 3 months | Factory has taken corrective action and will resolve the issues within the given timeline. Factory will submit the proposed remedial works to the Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural System | Lateral stability system | Diagonal cracks in the non-structural brickwork walls are observed in Building A | Carry out remediation works. | S5+ 4 months | Factory has taken corrective action and will resolve the issues within the given timeline. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural System | Lateral stability system | Cracks at the RC column and beam joints at the roof level of Building C are observed which are perhaps due to the in-sufficient capacity of joints to resist forces due to lateral loads. | Building Engineer to carry out a stability analysis of Buildings B & C against the lateral loads and propose additional stability system if necessary. Submit the proposed remedial works to the Pakistan Accord for review. Once agreed, complete the remediation works. | 7 months | Factory will submit the structural stability assessment and proposed remedial works, if needed, to the Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Cracking | Beams | This relates to the buildings B and C. Consistent and repeated beam cracking on the primary beams of Buildings B & C at the 2nd floor. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, in such cases, Building Engineer to investigate the cause of beams cracking and identify appropriate remediation. The investigation shall include confirmation of reinforcement in the beams and a design assessment based on the as-constructed building and loading. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Cracking | Beams | This relates to the buildings B and C. Consistent and repeated beam cracking on the primary beams of Buildings B & C at the 2nd floor. | Carry out remediation works if required. | S8 + 4 months | Factory will take corrective action and implement the proposed works if needed based on proposals reviewed by Accord. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Loading | Uncontrolled loading | This relates to the buildings B & C. Un-controlled fabric storage and dense fabric piles were observed at some floor areas | Building Engineer to review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. Loading to be actively managed by Factory Management. | 6 months | Floor load plans had already placed at each floor of all three buildings |  |  |  | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Cracking | Slabs | This relates to the buildings A roof slab | Building Engineer to investigate the cause of slab cracks. Investigate if cracks are only in the render. If cracks are within RC slab, in such case, Building Engineer to propose the remedial works, and once reviewed by Accord, implement the remedial works. | 6 months | Factory will take corrective action, submit assessment to Accord and will resolve the issues within the given timeline. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Structural Design | Drawings differ from as-built | - Column drop panels are missing at the 1st floor level along grid line H of the Building A. - Steel shed is constructed over the Building B roof but it is not shown on the as-built structural drawings. - As-built structural drawings of Building B show square column at grid line C/2 while 550mm dia RC circular column was observed on site. - As-built structural drawings of Building B are missing back extension along GL-1. | Building Engineer to collect information and produce accurate and complete as-built documentation. | 6 months | Factory has taken corrective action and It was due to drafting error to show the drop panels there. In actual drop panels are not present at site, instead there is a peripheral beam. The above corrections are made in drawings. Factory will submit revised drawings to Accord for review |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Cracking | Non structural | Cracking was observed in the non-structural parapet walls of building A. | Sections of plaster finish to wall to be removed and extent of crack to be reviewed by Building Engineer. Propose the remedial works, and once reviewed by Accord, implement the remedial works. | 6 months | Factory has taken corrective action and will resolve the issues within the given timeline. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 124 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 125 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 126 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 127 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 128 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 129 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 130 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 131 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 132 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 133 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 134 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 135 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 136 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 137 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 138 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 139 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 140 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 141 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 142 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 143 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 144 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 145 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 146 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 147 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 148 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 149 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 151 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 152 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1