## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
2024-07-04
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | MAK Garments (Pvt) Ltd.-Plot # 46, Sector 7-A Sector 7 A Korangi Industrial Area, Karachi, Sindh, Pakistan.
[9 empty] | Date of Initial Inspection | [12 empty] | 2024-07-04
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | During the inspection, it was found that substation room layout drawing was not available in the facility. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but were outdated. | Upgrade comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory has electrical layout drawings - including power layouts, lighting layouts, fire alarm layouts and containment layouts but the layout drawings were outdated and missing necessary details. | Upgrade comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | It was found that at different locations such as Building-2 ground floor, first floor production area and Building-3 washing area the circuit breakers were installed without breaker boxes and fixing supports. | Cover all circuit breakers that are openly installed throughout the facility with concealed metallic boxes to ensure safety and compliance in accordance with BS 7671:2018 , 18th Edition, Regulation 421.1.201. | 1 month | Facility will be install breakers covers in all circuits breakers |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E5 | DBs & Elec Protection Systems | Circuit breakers | At Building-2 first floor distribution board, faulty and brunt signs circuit breaker was identified. The brunt condition of the circuit breaker significantly increases the risk of an electrical fire due to potential overheating. | Faulty/Burnt sign circuit breakers should be replaced with appropriately rated breakers conforming to BS EN 60898 or BS EN 60947. | E4 + 1 month | Facility will be replace faulty/burnt breakers |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | It was also found that the multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. -Observed at building-3 ground floor area (50 Ampere breaker with 1.5Sqmm Cable and rooftop area distribution board 100 Ampere breaker with undersized cable). | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. | 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | E7 | DBs & Elec Protection Systems | Hot Spots | During the inspection, hot spots were found in the following electrical panels at a cable termination point. -Observed at the Building-3 ground floor distribution board, Building-2 first floor distribution board, Building-1 LT room panels, and Building-2 ground floor distribution board. | Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring the safe and reliable operation of the electrical systems. | 1 month | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | [10 empty] | E8 | DBs & Elec Protection Systems | Hot Spots | It was also found that the Thermographic report was not available at the site. | Carry out an independent thermographic survey on the entire electrical system periodically once in every 6 months. Submit the test report to the Pakistan Accord for review. | E7 + 6 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Earthing system | It was found at Building-1 ground floor that no visual earth pits were identified. | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | [10 empty] | E10 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations, and many electrical machines did not have earth wires. Observed at Building-2 ground floor distribution board, Building-2 first floor stitching area distribution board, Building-3 ground floor distribution board, Building-3 ground floor power plug, and Building-2 mezzanine floor distribution board. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. Submit the design to Pakistan Accord for review prior to completing the installation of the earthing system. | E9 + 2 months | Facility will be ensure that proper earthing system will installed |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | It was also found that the Earth testing record was not available at the site. | Develop and submit the earth testing record to the Pakistan Accord for review. | E10 + 1 month | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was observed at Building-3's ground floor outdoor area that the electrical distribution board (Non-IP Rated) was not suitable for the environmental conditions in which it was installed. | Identify and replace electrical panels, that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 2 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was found at the Building-2 first floor and the Building-3 washing area inside the distribution boards that there was loose wiring and insufficient working space inside the distribution boards for operation and maintenance. | Install wire ducts to organize and route wires neatly, remove loose cables, and ensure that no cables are attached to the bus bars, panel body. This may mean the addition of new distribution boards with proper accessibility for cables incoming and outgoing, bus-bar alignment. | 1 month | Facility will install wire ducts as per requirements |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was also found that the front gate and enclosures of electrical distribution boards were found damaged in various locations, including the Building-3 rooftop area, Building-1 generator room, and Building-3 washing machine panel. | Repair or replace broken panels to restore proper enclosure integrity in accordance with BS 7671 (18th Edition) regulation 416.2.1. | 1 month | Facility will be replace /repair all damaged panels |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | [10 empty] | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was found that at the Building-3 outdoor area the electric panel was covered with plywood, Plywood is a flammable material. | Remove the plywood cover and replace it with a metal or non-combustible enclosure that is designed for outdoor use. | 1 month | Facility will be replace this electrical panels |  |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | [10 empty] | E16 | DBs & Elec Protection Systems | Loop Connection | During the inspection loop connections were identified within Building-1 ground floor generator room distribution board, Building-3 rooftop elevator distribution board, Building-1 LT room main changeover panel and Building-3 ground floor distribution board. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilized to provide each circuit with the required live, neutral, and earth connections. | 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed in a number of electrical distribution boards and power plugs across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. -Observed at Building-1 ground floor generator room distribution board, Building-3 ground floor distribution board, and Building-3 ground floor power plugs. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022) | 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | [10 empty] | E18 | DBs & Elec Protection Systems | Openings | During the inspection, it was found that many distribution boards and cable trays have openings that may cause potential hazards due to environmental factors. -Observed at Building-1 ground floor LT panel, Building-2 ground floor cable trays not covered, Building-3 ground floor distribution board, and Building-3 machines panel openings. | Examine the entire facility panels to identify all openings, holes, and gaps that need to be sealed. Seal the openings/holes of panels, cable trays and trenches with metallic enclosures, fire-resistant sealants, gaskets. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Adequate Accessibility | At multiple locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components. -Observed at Building-1 ground floor generator room panel blocked by water pumps, Building-1 lt room changeover panel inadequate accessibility and Building-3 ground floor machines panel inadequate accessibility blocked by machines. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 1 month | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | [10 empty] | E20 | DBs & Elec Protection Systems | Adequate Accessibility | It was found that a significant accumulation of lint and dust in multiple distribution boards. -Observed at Building-1 ground floor fire hydrant distribution board, Building-3 ground floor distribution board, Building-1 LT room panels and Building-3 rooftop distribution board. | All electrical distribution boards and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | E19+ 1 month | Facility will be clean all distribution board. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was found that No Lightning Protection System was installed throughout the facility also any assessment was not available. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. Submit the risk assessment to the Pakistan Accord for review before installation. If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). | 6 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. The system throughout the building is a addressable but not listed, however, it has deficiencies, some of which observed are (non-exhaustive): -Malfunctioning of fire alarm panel (Panel was on silent mode during inspection) - Lack of fire rated cables at many locations throughout the system. - Non-Listed equipment’s/products - Inadequate coverage of detectors (absent in Building-2 office blocks, warehouses, production floor areas (finishing and stitching), and Building-3 washing and dyeing areas) - Incorrectly installed detectors (e.g. Close to ceiling fan) -Insufficient fire alarm audibility in the ground floor finishing area, building-3 washing area and building-2 first floor stitching area. | (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E22 + 1 month | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Detectors | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E23 + 4 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | fire Alarm & Detection System (FADS) | Fire Alarm Panel | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E24 + 5 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Manual Call Points | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E25 + 5 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Fire Alarm & Detection System (FADS) | Alarm Sounders | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E26 + 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E28 | Fire Alarm & Detection System (FADS) | Maintenance records | During the inspection, it was found that no Inspection, testing and maintenance (ITM) record for the fire detection and alarm system in accordance with NFPA 72. | Inspect, test and maintain the fire detection and alarm system and keep written records on-site, in accordance with NFPA 72. | 1 month | Facility will be done ITM record |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Emergency Lighting | Provided but insufficient | It was found that the emergency lights provided in the facility were insufficient to cover the entire facility. The emergency lighting did not provide adequate illumination levels, leading to dark or poorly lit areas during power outages. -Observed at Building 2 mezzanine floor, Building 2 ground floor stairs, Building 3 washing area, Building 3 rooftop spot area and Building 2 rooftop elevator room. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. Submit the emergency lights design to Pakistan Accord for information. | 6 months | Facility will be install emergency light |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Emergency Lighting | Provided but non-functional | During the inspection, it was observed at the Building-2 ground floor finishing area that the emergency lighting was not functional when tested. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant listed emergency lighting fixtures to ensure they provide adequate illumination. | 2 months | Facility will be install emergency light |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Emergency Lighting | Independent power source | During the inspection, it was observed that the emergency lighting within the Building-2 ground floor finishing area was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Emergency Lighting | General Lighting | It was observed at multiple locations such as Building external areas, stairs, Washing area, rooftops, and walkways were identified as lacking sufficient general lighting. | Conduct a thorough assessment of lighting throughout the facility to find areas with insufficient illumination. Install additional lighting fixtures in these spots to ensure adequate brightness. Ensure the new lighting design meets safety and efficiency guidelines to provide clear visibility for all tasks and emergency situations. | 3 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Generator, Transformer & Sub-Station Room | Battery | It was observed at the ground floor generator room that battery terminals were exposed, corroded and not properly insulated. | Replace and insulate exposed, corroded battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 1 month | Facility has replace the battery terminals . |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Cabling & Wiring | Cables support and protection | It was found that the cables were running without cable containment and laid directly over the floor. Inadequate cable containment and support results in sagging or stress on cables, which can lead to damage or failure. -Observed at Building-3 RO plant, Building-2 mezzanine floor IT office room, Building-2 ground floor sucking machine area, Building-1 ground floor generator room, Building-1 LT room, Building-3 ground floor compressor area. | Secure cables with appropriate supports or containments to prevent sagging, stress, and potential hazards, in accordance with BS 7671 18th Edition + A2 (2022) Regulation 522.8.5. | 3 months | Facility will be install PVC duct channel to ensure that no open wire. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Cabling & Wiring | Cables support and protection | It was also found at the Building-1 office block area that the electrical connections were open and exposed. | Insulate any open and exposed connections to ensure proper termination and avoid electrical hazards, in accordance with BS 7671 18th Edition + A2 (2022) Regulation 526.5. | E34 + 1 month | Facility will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E36 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, It was found that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. -Observed at Building-2 first floor stitching area channel and Building-2 ground floor finishing area channels. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 2 months | Facility will be clean all trunking system and also add this practice on monthly schedule to ensure that two time in the month the must clean |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Cabling & Wiring | Splicing of cables | It was found that the cable terminations within the Building-2 ground floor distribution boards were made without cable lugs. | Install cable lugs on all improperly terminated cables within the distribution board to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022) | 2 months | Facility will be installed cable lugs |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Cabling & Wiring | Splicing of cables | PVC tape joints were found at Building-3 ground floor washing area. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 2 months | Facility will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E39 | Cabling & Wiring | Splicing of cables | It was also found that at Building-2 first floor stitching area fan wires were inserted directly into power receptacles without a power plug. This practice is highly dangerous. | Replace the directly inserted power wires with proper power plugs to ensure safe and secure connections. | 1 month | Facility will install power plugs at all locations where wires are directly inserted to ensure safe and secure connections |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Cabling & Wiring | Colour coding | During the inspection of multiple distribution boards, deviations from standard cable colour coding practices were identified. -Observed at Building-3 ground floor washing area distribution board & Building-2 first floor stitching area distribution board. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors | 2 months | After hiring of consultant we will be fixed this issue |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Cabling & Wiring | Fixtures | At multiple locations loose and broken power receptacles were found. -Observed at Building-2 ground floor office block & Building-2 ground floor finishing area. | Implement a regular inspection and secure all power receptacles, ensuring they remain safely and correctly installed. Replace any broken and burnt sign power receptacles to ensure safe and reliable electrical connections | 1 month | Facility replace any damaged or burnt-out power receptacles immediately to maintain safe and reliable electrical connections. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Cabling & Wiring | Fixtures | It was found at Building-2 first floor stitching area that the power receptacle with burnt signs identified. | Implement a regular inspection and secure all power receptacles, ensuring they remain safely and correctly installed. Replace any broken and burnt sign power receptacles to ensure safe and reliable electrical connections | 1 month | The Facility will conduct regular inspection |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Cabling & Wiring | Fixtures | It was also found at Building-2 ground floor finishing area and first-floor stitching area that combustible materials stored near power receptacles, including paper, fabrics, and other flammable items. | Remove all combustible materials near the power receptacle. | 1 month | Facility will be removed all combustible materials |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Cabling & Wiring | Fixtures | At Building-1 and Building-3 ground floor the power receptacles were found to be installed in a wooden box, Which poses a significant fire hazard. | Replace the wooden box with an appropriate non-combustible enclosure. | 3 months | facility will be replace |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
2024-07-04
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [12 empty] | M.A.K Garments (Pvt) Ltd Plot # 46, Sector 7A, Korangi Industrial Area Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 2024-07-04
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F1 | Means of Escape | Protection of stairs | Unprotected openings into stair S3 in Building-1. Fire doors propped open in Building-1. - Doors not fire door in Building-1. - Door self-closers are missing in Building 1 (1st floor) | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self- closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Protection of stairs | Unprotected openings into stair S3 in Building-1. - Fire doors propped open in Building-1. - Doors not fire door in Building-1. - Door self-closers are missing in Building 1 (1st) floor | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F1 + 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Escape doors are lockable in most of the doors in Building 1 & Building 3. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | The facility will remove all locking devices from doors on all egress routes to ensure they can open freely |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Escape doors are lockable in most of the doors in Building 1 & Building 3. | - Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 4 months | The facility will change the escape doors as per Accord standards |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Escape doors | Escape doors are lockable in most of the doors in Building 1 & Building 3. | Monitor escape doors to ensure there are no locking devices installed that prevent easy access to emergency exits. | F4+ 4 months | The facility will remove all locking devices from doors on all egress routes to ensure they can open freely |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Exit access | Escape passing through increased risk area on way to exit in Building 2 & in passage b/w Building 1 & 2. - Obstructions on escape route at 1st floor, Building -1. - Unprotected stair S2 discharges inside the building at a distance from building exit. | Remove obstructions on escape routes and keep them clear for escape. | 2 weeks | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F7 | Means of Escape | Exit access | Escape passing through increased risk area on way to exit in Building 2 & in passage b/w Building 1 & 2. - Obstructions on escape route at 1st floor - Building -1. - Unprotected stair S2 discharges inside the building at a distance from building exit. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge routes. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F8 | Means of Escape | Exit access | Escape passing through increased risk area on way to exit in Building 2 & in passage b/w Building 1 & 2. - Obstructions on escape route at 1st floor - Building -1. - Unprotected stair S2 discharges inside the building at a distance from building exit. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Accord Building Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into exit discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F7 + 4 months | We are currently in the process of hiring a consultant, and once we finalize the details with them, we will provide you with the exact date and time. We are working to confirm everything as soon as possible and will update you shortly |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit discharge | Exit discharge routes from Stair S1 is not fire separated in Building 1. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes Provide additional exits from site. | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit discharge | Exit discharge routes from Stair S1 is not fire separated in Building 1. | Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high-risk areas | F9 + 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | F11 | Means of Escape | Exit signage | Missing exit signs at entry into stairs in Building-1. - Missing exit signs at roof of Building-1. - Electrically powered exit signs are not a tested and listed system in whole factory. | Rectify signs and provide new signage to comply with Accord Standard. | 3 months | Facility has installed required Signs as per accord standard |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F12 | Means of Escape | Exit signage | Missing exit signs at entry into stairs in Building-1. - Missing exit signs at roof of Building-1. - Electrically powered exit signs are not a tested and listed system in whole factory. | Ensure that all exit signage is checked periodically and in good working condition. | F11 + 3 months | Facility has installed required Signs as per accord standard |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F13 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the Building 1. - Generator room is not fire separated from the rest of the Building 1 & Building 2. - Boiler area is not fire separated from rest of the Building 2. - Gas steam generator is not fire separated from Building 2 & Building 3 | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F14 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the Building 1. - Generator room is not fire separated from the rest of the Building 1 & Building 2. - Boiler area is not fire separated from rest of the Building 2. - Gas steam generator is not fire separated from Building 2 & Building 4 | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F13+ 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F15 | Fire Rated Construction | Separation of occupancies | Large office areas not fire separated from the finishing area in Building 1. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors). | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F16 | Fire Rated Construction | Separation of occupancies | Large office areas not fire separated from the finishing area in Building 1. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F15 + 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F17 | Fire Rated Construction | Separation of shafts | Lift shafts is not fire separated in Building 1. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | [10 empty] | F18 | Fire Rated Construction | Separation of shafts | Lift shafts is not fire separated in Building 1. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F17 + 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F19 | Fire Rated Construction | Storage | Storage areas are not fire separated from the finishing department-ground floor-Building 1. -Store room not separated from Stitching area at first floor- Building 1. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F20 | Fire Rated Construction | Storage | Storage areas are not fire separated from the finishing department-ground floor-Building 1. -Store room not separated from Stitching area at first floor- Building 1. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F19 + 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F21 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs in Building -1 while it requires since Building 1 has 3 number of floors with area greater than 2325 m2 (i-e building has 2362 m2 area). | (1) Submit design documentation for standpipes system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F22 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs in Building -1 while it requires since Building 1 has 3 number of floors with area greater than 2325 m2 (i-e building has 2362 m2 area). | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F21+ 1 month | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F23 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs in Building -1 while it requires since Building 1 has 3 number of floors with area greater than 2325 m2 (i-e building has 2362 m2 area). | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F22 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | [10 empty] | F24 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs in Building -1 while it requires since Building 1 has 3 number of floors with area greater than 2325 m2 (i-e building has 2362 m2 area). | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F23 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | [10 empty] | F25 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs in Building -1 while it requires since Building 1 has 3 number of floors with area greater than 2325 m2 (i-e building has 2362 m2 area). | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F24+ 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | [10 empty] | F26 | Fire Suppression | Standpipe system | Missing standpipe outlets in stairs in Building -1 while it requires since Building 1 has 3 number of floors with area greater than 2325 m2 (i-e building has 2362 m2 area). | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F25+ 4 months = 18 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | [10 empty] | F27 | Fire Suppression | Fire pumps | Fire pump set is not listed. - There is no diesel pump. - Fire pumps are not in a fire separated room. - Fire pumps are exposed to the weather conditions. - Fire pumps do not start automatically. | Provide design for electric duty pump, diesel backup fire pumps and jockey pumps, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and submit to Accord for review following 6 steps mentioned above. | 18 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | [10 empty] | F28 | Fire Suppression | Water supply | Fire tank capacity is not sufficient. | Develop a rectification plan to provide adequate fire water supplies. The plan should demonstrate compliance with NFPA 24. Submit the plan to Accord for review and approval prior to implementation on site. Prepare design and drawings for a new dedicated fire water tank (or combined tank with dedicated fire water section). The design shall comply with Building Code of Pakistan and NFPA 24. These should be submitted Accord for review. | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | [10 empty] | F29 | Fire Suppression | Water supply | Fire tank capacity is not sufficient. | Implement the plan agreed with Accord. | F28 + 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | [10 empty] | F30 | Fire Safety Management | Fire drills | No regular fire drills - No evidence of fire drills | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | Facility has planned fire drill training as per requirements |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | [10 empty] | F31 | Fire Safety Management | Fire drills | No regular fire drills - No evidence of fire drills | Ensure fire drills are performed a minimum 2 times per year. | F30+ 2 months | Facility has planned fire drill training as per requirements |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | [10 empty] | F32 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels in Building-1. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | Facility will be update all evacuation plans |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F33 | Fire Safety Management | Emergency Action Plan | Escape diagrams are missing on some levels in Building-1. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F32+ 2 months | Facility will be update all evacuation plans |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Doors. Inadequate records of fire pumps maintenance | Prepare maintenance schedule for all life safety systems. | 3 months | facility will be update maintenance schedule |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Doors. Inadequate records of fire pumps maintenance | - Prepare a schedule of proposed system maintenance. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | facility will be update maintenance schedule |  |  |  | In Progress
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Fire Doors. Inadequate records of fire pumps maintenance | - Ensure all systems are being maintained as per the schedule agreed with Accord . - Keep maintenance records. | F35+ 3 months | facility will be update maintenance schedule |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire pumps. Inadequate records of testing of Fire Doors. | Prepare testing schedule for all life safety systems. | 3 months | facility will be update maintenance schedule |  |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire pumps. Inadequate records of testing of Fire Doors. | Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | Facility will be tested all fire doors and fire pumps with authorized party. |  |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire pumps. Inadequate records of testing of Fire Doors. | Ensure all systems are being tested as per the schedule agreed with Accord. - Keep testing records. | F38+ 3 months | Facility will be tested all fire doors and fire pumps with authorized party. |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2024-07-04
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [12 empty] | M.A.K Garments (Pvt) Ltd Plot # 46, Sector 7A, Korangi Industrial Area Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 04-Jul-24
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns of Building-1 at the Ground floor level appear to be overstressed against the observed load. | Factory to share the column cube testing reports of building-1 at the time of construction if any with Accord to recheck the column calculation. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns of Building-1 at the Ground floor level appear to be overstressed against the observed load. | Cut a piece of the reinforcing bar extruding from column above the roof floor and test the rebar for the steel tensile and yielding strength. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns of Building-1 at the Ground floor level appear to be overstressed against the observed load. | Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the columns identified in red. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns of Building-1 at the Ground floor level appear to be overstressed against the observed load. | Submit concrete and steel test results to Accord for review . | S3 + 1 month | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns of Building-1 at the Ground floor level appear to be overstressed against the observed load. | Factory Engineer to review design, loads and columns stresses in area identified in the report. | S4 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal columns of Building-1 at the Ground floor level appear to be overstressed against the observed load. | Produce and actively manage a loading plan for all floor plates within the factory considering floor capacity and column capacity. Share All the safe load plans with Pakistan accord for review and approval | S5 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | [10 empty] | S7 | Cracking | Column | A crack was observed on one column at ground floor level of Building-2, upon further inspection of the building and after ferro scanning it was observed that all to columns of building 2 were jacketed. We requested the factory to chip of the render of one column and it was observed that wire mesh was used to jacket the column at ground floor level. The crack observed in the jacketed area of the column, potential cause of the crack can be that the bond between old and new concrete was not made properly or overstressing of the column. | Factory Engineer to review design, loads and columns stresses in the building 2 columns at ground floor. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | [10 empty] | S8 | Cracking | Column | A crack was observed on one column at ground floor level of Building-2, upon further inspection of the building and after ferro scanning it was observed that all to columns of building 2 were jacketed. | Submit details of the assessment, with proposals for remedial works if needed, to Accord for review before implementing remedial measures | S7 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S9 | Cracking | Column | A crack was observed on one column at ground floor level of Building-2, upon further inspection of the building and after ferro scanning it was observed that all to columns of building 2 were jacketed. | Factory to implement Remedial work after review by Accord. | S8 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Structural System | Lateral stability system | The stability system of Building 1 is changing from floor to floor, Ground floor consists of flat slab and Moment resisting frame whereas the first floor is moment resisting frame. | Building Engineer to review the design and check for the lateral stability of Building-1. Propose any remedial measures as required and submit to Accord for review | 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Structural System | Lateral stability system | The stability system of Building 1 is changing from floor to floor, Ground floor consists of flat slab and Moment resisting frame whereas the first floor is moment resisting frame. | Implement remedial measures as necessary in accordance with proposal reviewed by Accord | S10 + 4 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Other Damage/Defects | Corrosion of reinforcement | On the first-floor level of building 1 the beams are cracked due to water seepage; the source of moisture ingress is seepage from the expansion joint in the building | Building Engineer to inspect the area and propose waterproofing measures to prevent further damage occurring as well as beam repair/remedial works. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Other Damage/Defects | Corrosion of reinforcement | On the first-floor level of building 1 the beams are cracked due to water seepage; the source of moisture ingress is seepage from the expansion joint in the building | Factory to implement Remedial work. | S12 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Other Damage/Defects | Corrosion of reinforcement | On the first-floor level of building 1 the beams are cracked due to water seepage; the source of moisture ingress is seepage from the expansion joint in the building | Monitor the area for future signs of water ingress | S13 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Other Damage/Defects | Spalling concrete | The concrete of first floor slab of building 1 was spalling at multiple locations due to lack of waterproofing on the roof. | Building Engineer to inspect the area and propose waterproofing measures to prevent further damage occurring as well as beam repair/remedial works. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S16 | Other Damage/Defects | Spalling concrete | The concrete of first floor slab of building 1 was spalling at multiple locations due to lack of waterproofing on the roof. | Factory to implement Remedial work. | S15 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S17 | Other Damage/Defects | Spalling concrete | The concrete of first floor slab of building 1 was spalling at multiple locations due to lack of waterproofing on the roof. | Monitor the area for future signs of water ingress | S16 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S18 | Other Damage/Defects | Spalling concrete | The concrete of roof of building 2 is spalling at multiple locations due to lack of waterproofing on the roof. | Building Engineer to inspect the area and propose waterproofing measures to prevent further damage occurring as well as beam repair/remedial works. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S19 | Other Damage/Defects | Spalling concrete | The concrete of roof of building 2 is spalling at multiple locations due to lack of waterproofing on the roof. | Factory to implement Remedial work. | S18 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S20 | Other Damage/Defects | Spalling concrete | The concrete of roof of building 2 is spalling at multiple locations due to lack of waterproofing on the roof. | Monitor the area for future signs of water ingress | S19 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S21 | Other Damage/Defects | Moisture ingress | The concrete of the OHWT on roof of building 1 is damaged at multiple locations due to moisture ingress. | Building Engineer to inspect the area and propose waterproofing measures to prevent further damage occurring as well as repair/remedial works. | 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S22 | Other Damage/Defects | Moisture ingress | The concrete of the OHWT on roof of building 1 is damaged at multiple locations due to moisture ingress. | Implement remedial works. | S21 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S23 | Other Damage/Defects | Moisture ingress | The concrete of the OHWT on roof of building 1 is damaged at multiple locations due to moisture ingress. | Monitor the area for future signs of water damage. | S23 + 3 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S24 | Structural Documentation | Undocumented modification | There is an additional steel structure and OHWT is constructed on roof of Building 1 and Building 2 which needs to be updated on the architectural drawings, the Mezzanine floor in Building 1 is also not marked in the available architecture drawings. The part of corridor between building 1 and Building 2 is covered with steel shed as well. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S25 | Structural Documentation | Documentation unavailable | The following drawings are not available and needs to be prepared/updated. • Structural drawings of Building 1, Building 2 and Building 3. • The architectural drawings of Building 1, Building 2 and Building 3. • The location of staircase also need to be updated on the drawings. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S26 | Structural Documentation | Lack of safe load plans | No safe load plans posted in the factory. | Building Structural Engineer to produce loading plans for all floors within the factory considering floor capacity and column capacity. Loading to be actively managed by Factory Management. Display all the produced safe load plans on each floor . | 6 months | We are in the process of hiring a consultant to assist us in completing this task. we will be done the hiring process maximum one month, and we will share the details once hiring has done end of March-2025. |  |  |  | In Progress

## E Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Fixtures
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## F Categories
Categories | Means of Escape | Fire Rated Construction | Hazardous Materials | Fire Suppression | Fire Safety Management
Means of Escape | Protection of stairs | Structural fire rating | Chemicals handling | Standpipe system | Fire drills
Fire Rated Construction | Number of exits | Extensive voids | Chemicals storage | Fire extinguishers | Records of systems maintenance
Fire Suppression | Travel distance | Separation of high-risk areas | Diesel storage | Fire pumps | Records of system testing
Hazardous Materials | Exit capacity | Separation of shafts | Gas storage | Sprinkler system | Staff training
Fire Safety Management | Exit access | Separation of occupancies |  | Water supply | Emergency Action Plan
| Escape stair condition | Floor openings |  | Exterior hydrants | Fire vehicle access
| Exit discharge | Storage
| Escape doors | Atrium
Exit signage
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## S Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Leaking Pipes
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type