## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
13-Dec-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Apparel Manufacturers Pvt Ltd (Unit 2), 36/6, Sector-15, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 13-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | Single Line Diagrams were not provided for the facility | Consult a qualified engineer to create all Single Line Diagrams and rectify design issues. | 6 months | Single Line Diagrams will be provided once we hire an electrical engineering team |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | Thermographic & Insulation Test Reports were not provided. | Thermographic & Insulation Testing report shall be prepared for the whole facility. | E1 + 6 month | Thermographic & Insulation Testing report will be provided by the team |  |  | Does not comply for approval. Equipment details missing. Further resistance values not provided in insulation test report. | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | Maintenance record was provided for the facility | Maintenance records shall be maintained periodically. | 3 months | Maintenance records will be maintained periodically. |  |  | Insufficient to comply for approval. | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | Diagrams & Drawings | Electrical layout drawing | Earth testing reports were not available on site. | Provide Earth Testing Report and maintain an inspection and reporting regime | 6 months | Earth Testing Report will be provided along inspection report |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | Diagrams & Drawings | Electrical layout drawing | This relates to the whole facility. - As-built Layout drawings were not provided. | Consult a Qualified Engineer complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. | E4 + 3 months | As built Layout drawings will be provided |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the whole facility: Roof was found to have some solar panel fabrication works in execution, but there was no Lightning protection system installed in the facility. Any document related to LPS assessment was not presented. | A proper risk assessment report needs to be conducted by a qualified consultant to establish whether an LPS is required or not. Submit assessment report to Pakistan Accord for review. | 2 months | A proper risk assessment report will be provided |  |  | Submitted as per NFPA 780 however as per British Standards (BS) but is required as per Pakistan Accord. | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the whole facility: Roof was found to have some solar panel fabrication works in execution, but there was no Lightning protection system installed in the facility. Any document related to LPS assessment was not presented. | If applicable, design and implement the LPS system as per BS 7671 standard and documentation reviewed by Pakistan Accord. | E6 + 6 months | If Applicable then LPS system will be installed |  |  | Not in compliance with BS Standards | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | Abnormal Temperature found within the electrical panel at cable termination points, resulting in abnormal temperatures on below positions (non-exhaustive): - Panel Distribution Board Ground Floor: Red Phase at 52 ℃ - Kitting 1st Floor Distribution Board: Main CB at 45 ℃ - Multiple Locations: Power sockets were found overloaded | Rectification of distress on red phase at ground floor distribution board is required to be done immediately. | 1 month | Rectification has already done the following points -Panel Distribution Board Ground Floor -Kitting 1st Floor Distribution Board Survey will conducted related overloaded sockets |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Hot Spots | Abnormal Temperature found within the electrical panel at cable termination points, resulting in abnormal temperatures on below positions (non-exhaustive): - Panel Distribution Board Ground Floor: Red Phase at 52 ℃ - Kitting 1st Floor Distribution Board: Main CB at 45 ℃ - Multiple Locations: Power sockets were found overloaded | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | E8 + 1 months | After rectification, again survey will be provided related these issues |  |  | Report lacks testing equipment details further few images show breaker in off state. | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Hot Spots | Abnormal Temperature found within the electrical panel at cable termination points, resulting in abnormal temperatures on below positions (non-exhaustive): - Panel Distribution Board Ground Floor: Red Phase at 52 ℃ - Kitting 1st Floor Distribution Board: Main CB at 45 ℃ - Multiple Locations: Power sockets were found overloaded | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 6 months. Carry out independent thermographic survey. | E9 + 6 months | Thermographic tests and survey will be conducted after every six months |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection, it was observed that the switches and sockets were damaged at various locations. Additionally, the positions of these switches are inadequate; some are located near combustible materials, while others are in areas where frequent operations take place, such as the main gate, child's room, kitchen, knit office on the first floor, and near knit machines on the first floor. Operating these switch sockets in the current condition poses a high risk of sparking, electrocution, and fire hazards. | Replace damage power socket outlet suitable for the equipment's electrical requirements. Securely terminate and connect the equipment wires to the newly installed socket outlet. | 3 months | Detailed survey will be conducted and after actions will be taken |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Earthing system | This relates to the whole facility. In most of the areas, bonding of cable tray, metal structures, Distribution Board doors were found missing. Few areas are listed below: - Distribution Board at Ground Floor Below stairs - First Floor Knitting Main Distribution Board - Machines 1st Floor | Connect all metal bodies of Electric panels to the earth terminal within electric panels. | 6 months | Survey will be conducted and report will be provided |  |  | Layout drawings required. | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Earthing system | This relates to the whole facility. In most of the areas, bonding of cable tray, metal structures, Distribution Board doors were found missing. Few areas are listed below: - Distribution Board at Ground Floor Below stairs - First Floor Knitting Main Distribution Board - Machines 1st Floor | Ensure all metallic parts of a critical risk. the electrical installation are suitably bonded in accordance with BS7671:2018 + A2 2022 | 6 months | After survey report approved actions will be taken |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Earthing system | This relates to the whole facility. No Earth cables were found for the Motor at placed in LT Room Ground Floor, also on the 3rd floor stitching area. Implement 3-wire system for single phase & earth factory-wide instead of 2-wire system. | All earth connections must be connected to earth pits via their respective distribution boards | 3 months | Earthing will be provided in LT Room Ground Floor, also on the 3rd floor stitching area. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Cabling & Wiring | Cables support and protection | This relates to the whole facility: It was noted in several locations that the cleanliness was not being maintained within the electrical panels and trunking system. The cable trunking system was found filled with a high quantity of fluff and dust that is at high risk of fire. | All Trunking systems must be cleaned and maintained. | 3 months | All electric panels and trunking system have cleaned |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Cabling & Wiring | Cable trench and channel cleanliness | This relates to the whole facility: It was noted in several locations that the cleanliness was not being maintained within the electrical panels and trunking system. The cable trunking system was found filled with a high quantity of fluff and dust that is at high risk of fire. | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. | 2 months | Cleaning and maintenance schedule checklist will be provided |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Lint & dust inside panel board | This relates to the whole facility: It was noted in several locations that the cleanliness was not being maintained within the electrical panels and trunking system. The cable trunking system was found filled with a high quantity of fluff and dust that is at high risk of fire. | Develop a periodic maintenance record of Distribution Boards and cable trays. | 1 months | Checklist will be maintained monthly |  |  | does not comply for approval, Three previous record required | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Cabling & Wiring | Splicing of cables | This relates to the whole facility: PVC Tapping joints found in different Distribution Boards; Some of them are given below for reference. - AC Outers at Ground Floor - Small Distribution Board in Ground Floor LT - Distribution Board below Stairs Ground Floor - Cutting Office - Cutting MC Ground Floor - At Fridge Ground Floor Offices - FF Main Distribution Board - Neutral/Earth 1st Floor Knitting MC - In store area. | Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. | 4 months | PVS taping joints survey will be conducted. And appropriate connectors will be provided |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the whole facility: Distribution Boards installed in the external environment must be weather/rain proof such as Distribution Board Supply Pump Ground Floor Having Too-sensitive electronics inside also the Distribution Board at the roof for the compressor are not weather proofed. | All external electrical distribution boards must be IP rated for protection against environmental factors. | 3 months | will be installed |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Multiple Connections | This relates to the whole facility: There is cross-circuiting (Looping, Bunching at Moulded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. In some Distribution Boards, multi looping was found on circuit breakers at various locations, example Panel Distribution Board below ground floor stairs, rest of the Distribution Boards like small Distribution Board LT room, Supply Pump Distribution Board Ground Floor, and Knitting Machine incoming . | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new DBs adjacent to existing panel. | 3 months | A detailed survey will be conducted. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Main Building on level(s) L01- 1st Floor: The rating of the cable was less than the rating of the breaker therefore the breaker would not provide adequate protection to the cables. - 4mm cable on 60A CB No Earthing - 16mm Cable on 100A CB No Earthing | Consult a qualified engineer to review the entire installation and advise the correct combination of cable and breaker sizes | 3 months | Electrical Engineer will conduct survey and generate capacity report |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Circuit breakers | This relates to the Main Building on level(s) L01- 1st Floor: The rating of the cable was less than the rating of the breaker therefore the breaker would not provide adequate protection to the cables. - 4mm cable on 60A CB No Earthing - 16mm Cable on 100A CB No Earthing | Replace breakers or cable with correct cable sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 3 months | Breakers will be replaced after Electrical Engineer's survey report |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Main Building on level(s) L01-Ground Floor. During electrical inspection, significant issues were identified with the distribution board (Distribution Board) situated below the stairs on the ground floor. These issues encompass the absence of the red phase Busbar, inadequate Earthing and Bonding, presence of idle cables, unfit dressing of cables, and sharp openings. Moreover, a notable deficiency observed is the lack of earth connections, which is also apparent in other Distribution Boards such as the one situated below the stairs on the ground floor and the main Distribution Board on the first floor in the knitting area. | Develop a regular inspection and maintenance program for all electrical panels. | 3 months | Maintenance programme checklist will be developed |  |  | Not provided for all panels further data is not valid | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Main Building on level(s) L01-Ground Floor. During electrical inspection, significant issues were identified with the distribution board (Distribution Board) situated below the stairs on the ground floor. | Consult a qualified engineer to access, design and procure appropriate LT panel for the application. | 4 months | Alternate programme for LT panel will be provided. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Main Building on level(s) L01-Ground Floor: Many of the Distribution Boards are equipped with poorly maintained Obsolete-type circuit breakers, having distress on cables and burnout connectors | Investigate the reason of distress and burnout connectors, develop a regular inspection and maintenance program for all distribution boards. | 3 months | Detailed survey will be conducted and after actions will be taken |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L01-Ground Floor: During our inspections, we visited the ground floor LT room. In the electrical panel room, we observed inadequate conditions regarding the cables and conduits. Specifically, there were issues with proper clipping, cleanliness, containment, and the mesh of wirings. | Installation of cable support required to be done for exposed cables. Replacement of rusted containment required to be done. | 3 months | LT room will be properly maintained with earthing, cleaning, containment etc |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | DBs & Elec Protection Systems | Openings | This relates to the Main Building on level(s) L01-Ground Floor: Unsealed openings of Distribution Boards having Sharp Edges which can damage insulation of the cables. Unsealed opening could provide a passage for dust and dirt. However, it also provides passage for rodents to enter which could lead to a potential hazard for short circuit. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 3 months | Seal of opening will be installed in every panel |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | DBs & Elec Protection Systems | Openings | This relates to the Main Building on level(s) L01-Ground Floor: Unsealed openings of Distribution Boards having Sharp Edges which can damage insulation of the cables. Unsealed opening could provide a passage for dust and dirt. However, it also provides passage for rodents to enter which could lead to a potential hazard for short circuit. | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. | 3 months | Checklist will be generated maintained monthly |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L01-Ground Floor: Cables termination installed without cable lugs, which results in breaking strands of the cables and gets heated. Circuit breakers incomings found lug less such as: - Ground Floor Distribution Board Pumps - First Floor Distribution Board Incoming Circuit Breaker | All stranded cables terminations shall be installed with proper cable lugs. | 3 months | Lugs will be installed in all panel breakers including - Ground Floor Distribution Board Pumps - First Floor Distribution Board Incoming Circuit Breaker |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Cables support and protection | Loose wiring and idle connections were found, these need to be dressed properly in conduits for example at AC Outers at Ground Floor, Fan in Child Room, Near Washrooms, and Cutting area Wiring Seems Loose. Open Electrical Earth wire at the Ground floor and 1st Floor near knitting machines can cause trip and fall hazards. | Reroute cables and secure all cables to a method of cable containment | 3 months | Detailed survey will be conducted and after actions will be taken |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L01-Ground Floor: Main distribution board at Distribution Board Below Ground Floor found with a mesh of electrical wires which are not dressed properly. In some Distribution Boards, idle or dismantled cables were found, which could pose a potential hazard and ignite a fire. | Cable dressing needs to be done along with removal of Idle cables (if any). | 3 months | Idle Cables will be removed. And proper dressing and connectors will be used |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L01-Ground Floor: Main distribution board at Distribution Board Below Ground Floor found with a mesh of electrical wires which are not dressed properly. In some Distribution Boards, idle or dismantled cables were found, which could pose a potential hazard and ignite a fire. | Schedule a proper maintenance records to monitor, control and rectify weak electrification works. | 3 months | Maintenance checklist will be developed. |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Cabling & Wiring | Cables support and protection | The factory was found to have PVC conduit for all power, lighting, and fire applications, leading to potential safety and compliance issues. | Lighting-Power and Fire cables circuits must be distinguished in their relevant conduits. | 3 months | All relevant conduits will be replaced |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L01-Ground Floor: - An unidentified blue wire observed in LT Room ground floor in idle condition. - An unused or idle changeover is observed below the stairs of Ground Floor, claimed to be non-operational. | Cable needs to be removed it immediate from both source end and LT room. Idle changeover which is non-operational, has to be removed from the location with complete disconnection. | 3 months | A detailed survey will be conducted and submitted |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L02- 2nd Floor: Lights were found hung on metallic wire fixed to both ends of wall having no strong support. | Fix lights and cables in an appropriate and compliant ceiling/hanging arrangement for these lights | 3 months | Fix lights and cables will properly installed |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Emergency Lighting | No emergency lighting | This relates to inadequate emergency lighting throughout the building at all levels: Lack of adequate emergency lighting in and around the building. This presents a risk to occupants escaping especially in the event of an Emergency evacuation after daylight hours. | All fire wardens to be provided with portable torches to assist in evacuation after hours when there is insufficient natural light. Replace batteries where necessary to ensure that emergency lights achieve the required period of protection as required by the Building Code of Pakistan. | 3 months | New Portable lights will be provided to fire wardens and security guards |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Emergency Lighting | Provided but insufficient | This relates to inadequate emergency lighting throughout the building at all levels: Lack of adequate emergency lighting in and around the building. | Provide emergency lighting along all escape routes according to Pakistan Accord Building Standard & BCP 10.14.1 & 10.14.2, including outside the building, so that building occupants can escape safely from the building. Test the system to ensure all escape routes are adequately illuminated comply with BCP 10.14.2.5. | E36 + 3 month | Survey will be conducted and report will be provided |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Emergency Lighting | No emergency lighting | This relates to inadequate emergency lighting throughout the building at all levels: Lack of adequate emergency lighting in and around the building. | Maintain the all emergency lights in good condition at all times. | E37 + 3 months | After survey lights will be replace where needed. |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system generally throughout the building. In some areas the installed detection and alarm system found to be non-functioning e.g. at 3rd Floor Sampling, R&D and Storage area, 2nd Floor Stitching and Finishing and Storage areas. | Existing alarm and detection system should be made 100% operational without any fault. | 3 months | Existing fire alarm system will be 100% operational |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. There is an automatic fire detection and alarm system in the building, however the system has numerous deficiencies .i.e.: - Lack of fire rated cables. - Non Listed equipment /products are used in the system, including fire alarm panel. - Inadequate number of detectors and sounders and placement issues at all levels. | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | After survey design will be made which includes technical data sheet and FADS Factory will submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E40+ 1 months | Documentation will be submitted |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E41 + 4 months | Material list and its availability with installation procedure will be provided |  |  |  | In Progress
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E42 + 5 months | As built drawing will be provided |  |  |  | In Progress
3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E43 + 3 months | Verification inspection from ACCORD will be held |  |  |  | In Progress
3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E45 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E44 + 3 months | Full testing and commissioning certification will be provided. |  |  |  | In Progress
3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
13-Dec-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Apparel Manufacturer Pvt Ltd Unit 2 Plot 36/6, Sector 15 Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 13-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors along egress routes at exit discharge points at 1st, 2nd and 3rd Floors. Doors on escape routes, particularly those leading off the floor or to outside must not have locking devices; they must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. | Locking Mechanism from all escape routes doors should be removed on permanent basis. | 1 month | All door locks will be removed. |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors along egress routes at exit discharge points at 1st, 2nd and 3rd Floors. | Install opening mechanisms on all doors on escape routes comply with Pakistan Accord Standard Art. 1.4 & 1.5. | 3 months | Opening mechanism will be installed. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F3 | Means of Escape | Escape doors | Lockable mechanisms on doors along egress routes at exit discharge points at 1st, 2nd and 3rd Floors. | Maintain door easy opening mechanisms, self-closing and hold open devices in good working order. | 4 months | self-closing and hold open devices will be installed. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F4 | Means of Escape | Escape doors | The two main exits gates for exit away from the building (from the premises), are not provided with non-lockable opening mechanisms that are easily openable from inside, they do not open in the direction of escape, which could prevent occupants from escaping away from the building. Doors on escape routes leading to outside or away from the building do not need to be fire rated, but must not be lockable and must swing in the direction of exit. These gates must also be of a width that allows free flow of the full building occupant load to move through them without an undue queuing time in the event of an emergency. Where there are security concerns special door locking features complying with NFPA 101 can be used, that do not allow opening from outside but cannot be lockable from inside, and must meet other door requirements as per the Pakistan Building Code. | Remove all non-compliant locking features from doors on emergency escape routes. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | 1 month | Opening mechanism will be installed. |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F5 | Means of Escape | Escape doors | The main exits gates to outside the property at Ground Floor level: The two main exits gates for exit away from the building (from the premises), are not provided with non-lockable opening mechanisms that are easily openable from inside, they do not open in the direction of escape. | Provide opening mechanism on doors in the direction of travel and minimum leaf width complying with BCP 10.9.1.4 and reconfigure if not adequate to cater for all occupants of the building. | 3 months | One door is already opening outward mechanism and about second door, its wicket door will be open outside and its width will be increase after breaking the outward stairs. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F6 | Means of Escape | Escape doors | The main exits gates to outside the property at Ground Floor level: The two main exits gates for exit away from the building (from the premises), are not provided with non-lockable opening mechanisms that are easily openable from inside, they do not open in the direction of escape. | Maintain door easy opening mechanisms, self-closing and hold open devices in good working order. | 4 months | Easy Opening mechanism will be installed after Structural engineer Survey. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Exit discharge | Exit discharge from the Cutting area at Ground Floor to outside the building, which leads to a narrow escape route that is not protected. If the exit out of the back of the cutting area is not used then the means of egress is not sufficient to meet travel distance limits from that space. The exit leads to a route where temporary and permanent obstructions and unprotected hazardous areas along the route mean that an adequate egress path is not available. | Clear obstruction of escape paths immediately and continuously maintain them free of all obstructions or impediments. | 1 month | Alternate route will be provided. |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit discharge | Exit discharge from the Cutting area at Ground Floor to outside the building, which leads to a narrow escape route that is not protected. | Design escape route with minimum width requirement at the back of the building leading to out of the premises in accordance with Pakistan Accord standard & BCP 10.10.5.3 and ensure separation of high-risk areas from discharge route with fire rated construction in accordance with Pakistan Accord Building Standard & BCP Table 10.9.1.8.13. Document proposal for meeting requirements, including technical details and certifications, and present to the Pakistan Accord for review before commencement of the works. | 4 months | We will show it to the structural engineer and find out the best solution, and submit proposal to meet requirements. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Exit discharge | Exit discharge from the Cutting area at Ground Floor to outside the building, which leads to a narrow escape route that is not protected. | Implement the design of the discharge route that addresses the egress width and protection issues as per documentation presented to Pakistan Accord for review and maintain protected and free of obstacles at all times | F8 + 4 months | Implement the new Design. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Protection of stairs | Protection of internal escape stairs at all levels: The main internal emergency stairway is not protected from production floors, office areas and other openings. Some of the issues that were observed were (non-exhaustive): - obstructions st escape stairs Ground level - Non-fire rated doors opening into the staircase - Offices opening directly into the staircase on 1st and Ground Floor levels. - Lift shaft opening into the staircase at Ground & 3rd Floor levels. - Electrical panels, water cooler and store in the staircase at Ground level. | Remove all temporary obstructions and stored combustible materials from the emergency staircase. | 1 month | Alternate plans will be provided after discussing with the fire safety team. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Protection of stairs | Protection of internal escape stairs at all levels: The main internal emergency stairway is not protected from production floors, office areas and other openings. | Prepare proposed design documentation and submit to Pakistan Accord for review that demonstrate compliance with Pakistan Accord Building Standards and BCP Table 10.9.1.8.13 , including: - documentation of 2-hour fire rated construction of the protective enclosure, with 90-minute fire rated doors for any accommodation opening, - fire rated enclosure for the Lift shaft openings in the staircase, - removal of electrical DBs from the staircase. Submit proposed design for the remedial works before upgrading works begin. | 4 months | -Lift shifts will be closed with bricks/blocks. -Alternate Plan for D.B will be provided. -Fire rated doors purchase plan will be shared. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Protection of stairs | Protection of internal escape stairs at all levels: The main internal emergency stairway is not protected from production floors, office areas and other openings. | Implement upgrading works to provide protection to the emergency stairs according to the design submitted and reviewed by Pakistan Accord. | F11+ 4 months | Implementation programme will be settled. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Protection of stairs | The external steel emergency stairway in the SE corner of the building serving the 3rd to 1st Floors, with final exit discharge at ground level, is not protected from the interior accommodation or from high-risk areas at discharge level and therefore may not provide safe passage away from the upper floors. Observations included (non-exhaustive): - Combustible materials observed on the stair landing, - Exits stairways not protected by opening protective assemblies, i.e. fire doors at 1st and 2nd Floors. - Non-fire rated separating materials (glass) at openings - No separation from Diesel Generator under stair discharge area | Remove combustible material/temporary obstructions from stairs and stair landings. | 1 month | -Combustible material will be removed permanently. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Protection of stairs | The exterior steel emergency stairway serving the 3rd to 1st Floors, with final exit discharge at ground level, is not protected from the interior accommodation or from high-risk areas at discharge level and therefore may not provide safe passage away from the upper floors. | Propose alterations to provide 2-hour fire rated protection to the external steel stairway to allow safe evacuation from the upper floors using this stair, including listed fire rated doors/protective assemblies at openings in accordance with requirements of the Pakistan Accord Standard and PBC Table 8.6.3.1. Proposed design to be submitted to Pakistan Accord for review, including documentation of fire rated assemblies proposed for the remedial works before the upgrading works begin. | 4 months | Alternate plan will be provided, including: -Fire rated doors will be planned. -Glass windows will be blocked with bricks/blocks. -Alternate plan for replace diesel Generator will be provided. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Protection of stairs | Protection of the steel external escape stairs on the SE corner of the building at all levels. The exterior steel emergency stairway serving the 3rd to 1st Floors, with final exit discharge at ground level, is not protected from the interior accommodation or from high-risk areas at discharge level and therefore may not provide safe passage away from the upper floors. | Implement the design as per documentation approved by Accord and using approved and certified materials or components. | F14 + 4 months | Implement the design as per documentation approved by Accord and using approved and certified materials or components. |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit signage | Insufficient Exit signage at floor exits and misleading escape route floor markings which is not consistent with exit signage. Directional exit signage was also found insufficient at all levels where the continuation of the egress path is not obvious. | Remove any misleading exit signage and floor marking which are not consistent with exit signage and evacuation plan. | 1 month | Exit signs will be again rechecked and will leading to Exits. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit signage | Exit and directional signage throughout the building. Insufficient Exit signage at floor exits and misleading escape route floor markings which is not consistent with exit signage. Directional exit signage was also found insufficient at all levels where the continuation of the egress path is not obvious. | Provide exit signage so that access to exits are indicated by approved, readily visible signs from all areas of the floor and clearly visible at exits and that comply with Pakistan Accord Standards and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | Exit Signs will be increased and illuminated. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit signage | Exit and directional signage throughout the building. Insufficient Exit signage at floor exits and misleading escape route floor markings which is not consistent with exit signage. Directional exit signage was also found insufficient at all levels where the continuation of the egress path is not obvious. | Maintain the all the exit doors and change of direction signage in good working order at all times. | 4 months | Exit signs survey will be procured and Signs will be increased. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Separation of shafts | Lift shaft connecting floors is not separated from the production floor accommodation by fire and smoke resisting construction and opening protection at 1st and 2nd Floor. Although the lift was non-operational at the time of the inspection, it provides a path for fire and smoke spread vertically between floors and the protected stairway. | Provide design with proposal to provide 2-hour fire resistant enclosure to the unprotected lift shaft openings into the accommodation at 1st and 2nd Floors and present to the Pakistan Accord for review, before commencement of the works. | 4 months | Lift is not operational so it's opening shafts will be closed with bricks/walls. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Separation of shafts | Unprotected openings of the Lift shaft at 1st and 2nd Floors: Lift shaft connecting floors is not separated from the production floors by fire and smoke resisting construction and opening protection at 1st and 2nd Floors. | Provide fire rated protection to the lift shafts openings in accordance with documentation submitted and reviewed by Pakistan Accord. | F19 + 4 months | Lift is not operational so it's opening shafts will be closed with bricks/walls. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Separation of high-risk areas | Lack of separation of high risk areas from different occupancies at Ground, 2nd and 3rd Floors. Areas observed include (non-exhaustive): - Lack of fire separation between electrical rooms, Steam Generator, Compressor, Diesel Generator, Storage from other areas | Remove diesel containers besides the generator and store in a safe place. | 1 month | -Steam generator and Compressors will be covered with Bricks Wall. -Alternate plan for removal of generator with diesel containers will be provided. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Separation of high-risk areas | Lack of separation of high risk areas from different occupancies at Ground, 2nd and 3rd Floors. Areas observed include (non-exhaustive): - Lack of fire separation between electrical rooms, Steam Generator, Compressor, Diesel Generator, Storage from other areas | Submit plans and documentation for complying with Pakistan Accord Standard and BCP Table 8.2.7 for separation of different occupancies for review, including documentation of fire rated assemblies proposed for the remedial works, before upgrading works begin. | 4 month | -Steam generator and Compressors will be covered with Bricks Wall. -Alternate plan for removal of generator with diesel containers will be provided. |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Separation of high-risk areas | Lack of separation of high risk areas from different occupancies at Ground, 2nd and 3rd Floors. | Provide the required Fire Separation as per documentation submitted to and reviewed by Pakistan Accord. | F22 + 4 months |  |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
13-Dec-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Apparel Manufacturers Pvt Ltd (Unit 2), 36/6, Sector-15, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 13-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal column indicated, which supports the water tank on the Roof, is potentially overstressed subject under the applied load at Ground floor level. This column also supports a heavy floor build-up around the toilet area at the 3rd floor level. | Building Structural Engineer to review design, loads and columns stresses in area identified. Verify in-situ concrete strengths either by 100mm diameter cores or existing cylinder strength data for the identified columns, or Propose plans for removal the floor build-up & blockwork walls around the column at the 3rd floor level to reduce the load on this column. Make proposal for reducing column stress to an adequate level and submit to Pakistan Accord for review | 3 months | We are hiring Civil Engineer and he will review and report it. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, the internal column indicated, which supports the water tank on the Roof, is potentially overstressed subject under the applied load at Ground floor level. This column also supports a heavy floor build-up around the toilet area at the 3rd floor level. | Implement remedial measures as per proposal reviewed earlier that demonstrate compliance with the requirements of the Pakistan Accord Building Standard | S1 + 3 months | We will Implement this matter |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Loading | Uncontrolled loading | It was observed that the 1st floor slab was supporting heavy loads that appeared excessive where fabric storage was observed adjacent to the staircase, as well as on other areas on this floor. | Building Structural Engineer to review design load of floors and produce safe loading plans for all floors within the factory giving consideration to types of materials to be stored and actual floor and column capacity | 3 months | We are hiring Civil Engineer and he will review and report it. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Loading | Uncontrolled loading | It was observed that the 1st floor slab was supporting heavy loads that appeared excessive where fabric storage was observed adjacent to the staircase, as well as on other areas on this floor. | Load plans to be displayed in storage areas and loading actively managed by Factory Management. | 6 months | We are hiring Civil Engineer and he will review and report it. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Structural System | Lateral stability system | Vertical and horizontal bracings missing in the roof steelwork which is a structural risk for the steel frame with high wind loads. The new steel frame to support PV panels which is under construction also appears to be missing vertical and horizontal roof bracings. | Building Structural Engineer to assess the as-built steelwork structure and propose additions to the lateral stability system as required. Submit proposed alteration works to Pakistan Accord for review. | 3 months | We are hiring Civil Engineer and he will review and report it. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural System | Lateral stability system | Vertical and horizontal bracings missing in the roof steelwork which is a structural risk for the steel frame with high wind loads. The new steel frame to support PV panels which is under construction also appears to be missing vertical and horizontal roof bracings. | Complete the installation of the lateral stability system as per the revised proposal where necessary. | S5 + 4 months | We will Implement the horizontal bracing. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural Design | Drawings differ from as-built | Structural drawings do not match with current arrangement of the structure | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. Submit drawings once completed to Pakistan Accord for review | 6 months | Factory will hire Civil Engineer to produce accurate and complete as-built documentation |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Cracking | Column | A vertical crack in the RC column was observed at front entrance at Ground Floor level. No heavy storage at superstructural levels was identified as the cause of the cracking at this location. | Sections of plaster finish to columns to be removed to investigate if cracks penetrate the building structure. | 2 months | We are hiring Civil Engineer and he will review and report it. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Cracking | Column | A vertical crack in the RC column was observed at front entrance at Ground Floor level. | Building Structural Engineer to determine the cause of cracking and design appropriate remedial measures if needed. Submit proposals for remedial works to Pakistan Accord for review. | 2 months | After Building Structural Engineer report It will be decided for further work. If RC beam will filled then one more month will be required |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Cracking | Column | A vertical crack in the RC column was observed at front entrance at Ground Floor level. | Implement proposals as per review and develop safe load plans for all floors to suit. Factory management to implement load plans | S9 + 4 months | After Building Structural Engineer report It will be decided for further work. If RC beam will filled then one more month will be required |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Structural System | Connection details | It appears to be that there is no bolted/welded connection between the roof steel beams and similarly, there is no fixity between the roof tubular steel purlins and the steel beams. | Building Structural Engineer to investigate if a welded connection is provided between steel beams and if necessary, provide bolted/welded connection to Engineer’s design & details. | 3 months | All roof tubular steel purlins and the steel beams will be checked and welded/ bolted if required. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5
3 | 8 |  | 122 | 421 | 6 | 5
3 | 8 |  | 123 | 421 | 6 | 5
3 | 8 |  | 124 | 421 | 6 | 5
3 | 8 |  | 125 | 421 | 6 | 5
3 | 8 |  | 126 | 421 | 6 | 5
3 | 8 |  | 127 | 421 | 6 | 5
3 | 8 |  | 128 | 421 | 6 | 5
3 | 8 |  | 129 | 421 | 6 | 5
3 | 8 |  | 130 | 421 | 6 | 5
3 | 8 |  | 131 | 421 | 6 | 5
3 | 8 |  | 132 | 421 | 6 | 5
3 | 8 |  | 133 | 421 | 6 | 5
3 | 8 |  | 134 | 421 | 6 | 5
3 | 8 |  | 135 | 421 | 6 | 5
3 | 8 |  | 136 | 421 | 6 | 5
3 | 8 |  | 137 | 421 | 6 | 5
3 | 8 |  | 138 | 421 | 6 | 5
3 | 8 |  | 139 | 421 | 6 | 5
3 | 8 |  | 140 | 421 | 6 | 5
3 | 8 |  | 141 | 421 | 6 | 5
3 | 8 |  | 142 | 421 | 6 | 5
3 | 8 |  | 143 | 421 | 6 | 5
3 | 8 |  | 144 | 421 | 6 | 5
3 | 8 |  | 145 | 421 | 6 | 5
3 | 8 |  | 146 | 421 | 6 | 5
3 | 8 |  | 147 | 421 | 6 | 5
3 | 8 |  | 148 | 421 | 6 | 5
3 | 8 |  | 149 | 421 | 6 | 5
3 | 8 |  | 150 | 421 | 6 | 5
3 | 8 |  | 151 | 421 | 6 | 5
3 | 8 |  | 152 | 421 | 6 | 5
3 | 8 |  | 153 | 421 | 6 | 5
3 | 8 |  | 154 | 421 | 6 | 5
3 | 8 |  | 155 | 421 | 6 | 5
3 | 8 |  | 156 | 421 | 6 | 5
3 | 8 |  | 157 | 421 | 6 | 5
3 | 8 |  | 158 | 421 | 6 | 5
3 | 8 |  | 159 | 421 | 6 | 5
3 | 8 |  | 160 | 421 | 6 | 5
3 | 8 |  | 161 | 421 | 6 | 5
3 | 8 |  | 162 | 421 | 6 | 5
3 | 8 |  | 163 | 421 | 6 | 5
3 | 8 |  | 164 | 421 | 6 | 5
3 | 8 |  | 165 | 421 | 6 | 5
3 | 8 |  | 166 | 421 | 6 | 5
3 | 8 |  | 167 | 421 | 6 | 5
3 | 8 |  | 168 | 421 | 6 | 5
3 | 8 |  | 169 | 421 | 6 | 5
3 | 8 |  | 170 | 421 | 6 | 5
3 | 8 |  | 171 | 421 | 6 | 5
3 | 8 |  | 172 | 421 | 6 | 5
3 | 8 |  | 173 | 421 | 6 | 5
3 | 8 |  | 174 | 421 | 6 | 5
3 | 8 |  | 175 | 421 | 6 | 5
3 | 8 |  | 176 | 421 | 6 | 5
3 | 8 |  | 177 | 421 | 6 | 5
3 | 8 |  | 314 | 421 | 6 | 5
3 | 8 |  | 315 | 421 | 6 | 5
3 | 8 |  | 346 | 421 | 6 | 5
3 | 8 |  | 349 | 421 | 6 | 5
3 | 8 |  | 350 | 421 | 6 | 5
3 | 8 |  | 351 | 421 | 6 | 5
3 | 8 |  | 352 | 421 | 6 | 5
3 | 8 |  | 353 | 421 | 6 | 5
3 | 8 |  | 354 | 421 | 6 | 5
3 | 8 |  | 355 | 421 | 6 | 5
3 | 8 |  | 356 | 421 | 6 | 5
3 | 8 |  | 357 | 421 | 6 | 5
3 | 8 |  | 358 | 421 | 6 | 5
3 | 8 |  | 359 | 421 | 6 | 5
3 | 8 |  | 360 | 421 | 6 | 5
3 | 8 |  | 361 | 421 | 6 | 5
3 | 8 |  | 362 | 421 | 6 | 5
3 | 8 |  | 363 | 421 | 6 | 5
3 | 8 |  | 364 | 421 | 6 | 5
3 | 8 |  | 365 | 421 | 6 | 5
3 | 8 |  | 366 | 421 | 6 | 5
3 | 8 |  | 367 | 421 | 6 | 5
3 | 8 |  | 368 | 421 | 6 | 5
3 | 8 |  | 369 | 421 | 6 | 5
3 | 8 |  | 370 | 421 | 6 | 5
3 | 8 |  | 371 | 421 | 6 | 5
3 | 8 |  | 372 | 421 | 6 | 5
3 | 8 |  | 373 | 421 | 6 | 5
3 | 8 |  | 374 | 421 | 6 | 5
3 | 8 |  | 375 | 421 | 6 | 5
3 | 8 |  | 376 | 421 | 6 | 5
3 | 8 |  | 377 | 421 | 6 | 5
3 | 8 |  | 378 | 421 | 6 | 5
3 | 8 |  | 379 | 421 | 6 | 5
3 | 8 |  | 380 | 421 | 6 | 5
3 | 8 |  | 381 | 421 | 6 | 5
3 | 8 |  | 382 | 421 | 6 | 5
3 | 8 |  | 383 | 421 | 6 | 5
3 | 8 |  | 384 | 421 | 6 | 5
3 | 8 |  | 385 | 421 | 6 | 5
3 | 8 |  | 416 | 421 | 6 | 5
3 | 8 |  | 417 | 421 | 6 | 5
3 | 8 |  | 418 | 421 | 6 | 5
3 | 8 |  | 419 | 421 | 6 | 5
3 | 8 |  | 420 | 421 | 6 | 5
3 | 8 |  | 421 | 421 | 6 | 5
3 | 8 |  | 422 | 421 | 6 | 5
3 | 8 |  | 423 | 421 | 6 | 5
3 | 8 |  | 424 | 421 | 6 | 5
3 | 8 |  | 425 | 421 | 6 | 5
3 | 8 |  | 426 | 421 | 6 | 5
3 | 8 |  | 427 | 421 | 6 | 5
3 | 8 |  | 428 | 421 | 6 | 5
3 | 8 |  | 429 | 421 | 6 | 5
3 | 8 |  | 430 | 421 | 6 | 5
3 | 8 |  | 431 | 421 | 6 | 5
3 | 8 |  | 432 | 421 | 6 | 5
3 | 8 |  | 433 | 421 | 6 | 5
3 | 8 |  | 434 | 421 | 6 | 5
3 | 8 |  | 435 | 421 | 6 | 5
3 | 8 |  | 436 | 421 | 6 | 5
3 | 8 |  | 437 | 421 | 6 | 5
3 | 8 |  | 438 | 421 | 6 | 5
3 | 8 |  | 439 | 421 | 6 | 5
3 | 8 |  | 440 | 421 | 6 | 5
3 | 8 |  | 502 | 421 | 6 | 5
3 | 8 |  | 503 | 421 | 6 | 5
3 | 8 |  | 504 | 421 | 6 | 5
3 | 8 |  | 505 | 421 | 6 | 5
3 | 8 |  | 506 | 421 | 6 | 5
3 | 8 |  | 507 | 421 | 6 | 5
3 | 8 |  | 508 | 421 | 6 | 5
3 | 8 |  | 509 | 421 | 6 | 5
3 | 8 |  | 510 | 421 | 6 | 5
3 | 8 |  | 511 | 421 | 6 | 5
3 | 8 |  | 512 | 421 | 6 | 5
3 | 8 |  | 513 | 421 | 6 | 5
3 | 8 |  | 514 | 421 | 6 | 5
3 | 8 |  | 515 | 421 | 6 | 5
3 | 8 |  | 516 | 421 | 6 | 5

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
| Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
| Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
| Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixture
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1