## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
13-Dec-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Klash Private Ltd. (Unit 1), Plot # 28 117 JB Near Paharange Drainage Millat Road Dhanola Faisalabad
[8 empty] | Date of Initial Inspection | [12 empty] | 18-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | During the inspection, it was found that Substation room layout drawings were not available in the facility. | Consult a qualified electrical engineer to complete Sub-Station room layout drawing. These drawings should accurately reflect the current electrical infrastructure in the facility. Submit the Substation room layout design to Pakistan Accord for review. | 3 months | 1. We will hire & consult a qualified electrical engineer to complete Sub-Station room layout drawings which will be reflect accurately with the current electrical infrastructure of the facility. 2. Once drawings will be finalized will share layout with Pakistan Accord for review. |  |  | 13-12-24: Not prepared yet. | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | Single Line Diagrams were provided but were not updated and had some design flaws which need to be rectified. | Consult a qualified electrical engineer to complete/upgrade Single Line Diagrams that clearly depict the existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. Submit the Single Line Diagrams to Pakistan Accord for review. | 6 months | 1. We will hire & consult a qualified electrical engineer to complete Sub-Station room layout drawings which will be reflect accurately with the current electrical infrastructure of the facility. 2. Once drawings will be finalized will share layout with Pakistan Accord for review. |  |  | 13-12-24: Submitted to Accord for review. | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | Electrical layout drawings were provided but were not updated and had some design flaws which need to be rectified. | Consult a qualified electrical engineer to complete/upgrade electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match the existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing, consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. Submit the As-Built layout drawings design to Pakistan Accord for review. | 8 months | 1. We will hire & consult a qualified electrical engineer to complete Sub-Station room layout drawings which will be reflect accurately with the current electrical infrastructure of the facility. Further we will design with separate diagrams & will ensure that each panel are clearly visible & up to date as per current electrical installation system. 2. Once drawings will be finalized will share layout with Pakistan Accord for review. |  |  | 13-12-24: Submitted to Accord for review. | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Hot Spots | During the inspection, hot spots were found in the following electrical panels at a cable termination point, where there were signs of overloading resulting in abnormal temperatures: - Building-1 Ground Floor DB-1, DB-2, Cutting Area DB - Building-1 First Floor Sample Room DB - Building-2 First Floor Stitching Unit 2 DB, Stitching Area DB - Building-2 Second Floor Stitching Area DB | Inspect the electrical panels to identify the source of abnormal temperatures, which may be caused by loose connections, Overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 1 month | 1. We will inspect all panels to identify the source of abnormal temperatures. Further we will check loose connections, overloaded circuits & other issues which can be cause of abnormal temperature. We will repair all these types of issues if found in electrical panels. |  |  | 13-12-24: No hotspot found. | Corrected
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | It was found that there was no Thermographic test report available at the site, so that faults such as overheating components or loose connections may go unnoticed and increases the risk of fire. Early detection through thermography can prevent fire incidents. | Carry out thermographic an independent thermographic survey on the entire electrical system. Submit the test report to Pakistan Accord for review. | E4 + 6 months | 1. We will arrange thermographic survey independently after internal inspection of all panels. 2. Once thermographic survey is done, will share test result with Pakistan Accord for review. |  |  | 13-12-24: Some pictorial evidence were provided at site but need be provided in standard report format. | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | It was found that there was no Thermographic test report available at the site | Create a schedule to have a thermographic survey carried out by a qualified surveyor on the entire electrical system at intervals of no less than 6 months. | E5 + 6 months | 1. We will create schedule to arrange thermographic survey carried out by a qualified surveyor for the entire electrical system bi-annually. Once schedule will be done, will share with Pakistan Accord as well. |  |  | 13-12-24: Not prepared yet. | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Circuit breakers | It was found in many distribution boards that the sizing of circuit breakers and cables was not as per actual load capacity. | Review the entire combination of cable and breaker sizes throughout the facility. Replace breakers or cables with the correct cable sizes or breaker sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 4 months | We will replace all old breakers or cables which size will be less than according to actual running load |  |  | Provided evidence insufficient , required for all instances | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Circuit breakers | In Building-2 Second Floor distribution board only an Earth Leakage Circuit Breaker was installed as a main protection. The Earth Leakage Circuit Breaker only protects the circuit during an earth fault and will not protect under overload and short circuit condition which potentially lead to a fire risk during overload and short circuit. | Install main MCCB breaker in Building-2 second floor distribution board for overload and short circuit protection. | 3 months | We have installed main MCCB breaker in distribution board for the protection of overload and short circuit protection in Building-2 second floor. Documental evidence will be submitted to Accord for review |  |  | 13-12-24: Rectified. | Corrected
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Earthing system | During the inspection, it was found that many distribution boards have no earth distributions. This was observed in (non-exhaustive): - Main Building-1 on level L01 First Floor - Building-2 level L00-Ground Floor | Install earth distribution within each distribution board. | 3 months | 1. We will hire & consult qualified electrical engineer to design the earthing layout. Once layout will be finalized, will share with Pakistan Accord for review. 2. We will install earth distribution within each distribution board in the facility once layout will be approved from Pakistan Accord. |  |  | Provided evidence insufficient , required for all instances | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | Many Earth pit for the facility were not visually found. | Make all earth pit visible, so that if there is ever any variation in the earthing values or future modification in earthing works then maintenance can be performed on the pit accordingly. | 3 months | 1. We will hire & consult qualified electrical engineer to design the earthing layout. Once layout will be finalized, will share with Pakistan Accord for review. 2. We will install earth distribution within each distribution board in the facility once layout will be approved from Pakistan Accord. |  |  | Provided evidence insufficient , required for all instances | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | It was also found that the earthing distribution system layout was not available. | Consult a qualified electrical engineer to design the earthing layouts. Submit the design to Pakistan Accord for review prior to completing the installation of the earthing system. | 4 months | 1. We will hire & consult qualified electrical engineer to design the earthing layout. Once layout will be finalized, will share with Pakistan Accord for review. 2. We will install earth distribution within each distribution board in the facility once layout will be approved from Pakistan Accord. |  |  | Resubmission required ,report lac compliance for approval. | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was found that loose wiring, cables have joints that are in contact with bus-bars and panel bodies inside the distribution boards, which could be a potential cause of electric shock or a short circuit. | Inside the distribution board ensure correct panel wiring, install cable ducts with covers, remove loose cables, remove cable joints, and ensure that no cables are attached to the bus bars. Also Maintain periodical inspection checklist for each distribution board. | 4 months | We will check distribution boards to ensure correct panel wiring, install cable ducts with covers etc. And will remove loose wiring cables, joist & also will ensure no cables should be attached to the bus bars in distribution boards. |  |  | Closed | Corrected
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | The water cooler and solar power distribution board placed on the roof of Building-2 were non-IP-rated panels which may cause any potential hazards due to environmental factors. | All external electrical distribution boards must be IP rated for protection against environmental factors. | 4 months | We will replace electrical distribution boards with IP rated for protection regarding environmental factors. |  |  | Closed | Corrected
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | Surge protection devices were not installed in any distribution boards. If a surge occurs without the device, it can be the cause of an accident or any equipment damage. This was observed in: - Building-1 and Building 3 DBs | Provide surge protective devices with each main distribution board throughout the facility | 6 months | For Installation of surge protection in each DB required a huge cost & time to complete this, we will install surge protection in all DB's of Building 1 and Building 3 asap. |  |  | Closed | Corrected
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Panel/cabling/busbar | PVC Tape joints were found in different distribution boards including - Building-1 cable trays Ground Floor Sample area - Building-2 First floor stitching department No more flexible cables shall be cut and taped in the facility. | Replace the taped/cut cables with continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or use joint boxes and appropriate connectors to joint cables. Also Maintain periodical inspection checklist for each distribution board. | 6 months | We have replaced taped/cut cables with continuous of appropriate length in 1. Building-1 Sample area 2. Building-2 First floor stitching department etc. Documental evidence will be submitted to Accord for review |  |  | Closed | Corrected
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Adequate accessibility | During the inspection, many power boards were installed in an inappropriate location such as under the steam line and many were fixed with cable ties. This was observed in: - Building-1 Level L01-First Floor - Building-2 L02-Second Floor - Building-2 First Floor Stitching Area - Building-2 Second Floor Stitching Area Without adequate working space, maintenance and troubleshooting tasks become challenging, increasing the likelihood of errors and safety incidents. | Relocate the power board to a compliant location. Remove cable ties and install proper support to power boards. | 6 months | 1. We will relocate the power board to a compliant location. 2. Further will remove cable ties and will install proper support to power boards. |  |  | Provided evidence insufficient , required for all instances | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Multiple Connections | There is cross-circuiting (Multiple, Bunching at Moulded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the distribution panels in the following places: - Building-1 First Floor Cutting Area - Building-2 Ground Floor Clothing House - Utility Building Sub-Station Room | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels. | 6 months | We will check & modify installation of circuits that will not be share breakers. |  |  | Closed | Corrected
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the Building 1, 2 and 3 Rooftops. It was found that Lightning Arrestors were installed with each Building but their assessment was not available. | Consult with a qualified electrical engineer to assess and update the design as needed of the Lightning Protection System for Buildings 1 , 2 and 3. Submit the design to Pakistan Accord for review. | 2 months | 1. We will hire & consult a qualified electrical engineer to assess and update the design as needed of the LPS for Building 1,2 & 3. 2. Once design finalize, will share with Pakistan Accord for review. |  |  | Risk assessment resubmission required. | In Progress
[8 empty] | Initial | [10 empty] | E19 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the Building 1 Rooftops. It was found that Lightning Arrestors were installed with each Building but their assessment was not available. | Implement the design as per documentation previously reviewed by Accord for Building 1 | E18 + 2 months | Factory will make changes to LPS as required by approved design on Building 1 |  |  | Resubmission required ,report lack compliance for approval. | In Progress
[8 empty] | Initial | [10 empty] | E20 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the Building 2 Rooftops. It was found that Lightning Arrestors were installed with each Building but their assessment was not available. | Implement the design as per documentation previously reviewed by Accord for Building 2 | E19 + 4 months | Factory will make changes to LPS as required by approved design on Building 2 |  |  | Resubmission required | In Progress
[8 empty] | Initial | [10 empty] | E21 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the Building 3 Rooftops. It was found that Lightning Arrestors were installed with each Building but their assessment was not available. | Implement the design as per documentation previously reviewed by Accord for Building 3 | E20 + 6 months | Factory will make changes to LPS as required by approved design on Building 3 |  |  | Resubmission required | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards.The system throughout the building is a conventional type, however it has deficiencies, some of which observed are (non-exhaustive): - Lack of fire rated cables at MCPs. - Non-Listed equipment/products. - Inadequate coverage of detectors (absent in office areas of Building-1, 2 and 3, Utility rooms, kitchens, canteen and prayer areas) - Incorrectly installed detectors (eg. under deep beams) - detectors did not activate sounders (eg. Building-3 sample area) | (1) Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 for Buildings 1, 2 and 3 | 3 months | 1. We will hire & consult qualified 3rd party regarding installation of new FSDS (fire detection & alarm system) as per NFPA 72 standards. 2. After consultation & hiring of 3rd party, working will be started on design upgrading layout. 3. Once design is finalized, It will be shared with Pakistan Accord for review. |  |  | Resubmission required after incorporating the comments | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E22 + 1 month | Factory will submit L/C documentation to Accord for any components of the FADS system that need to be imported to complete the system proposed by the design |  |  | 13-12-24: At design and development stage. | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E23 + 4 months | Factory will submit documentation to Accord verifying that all system components have been procured and on site ready for installation of the complete FADS system as proposed in the approved design |  |  | 13-12-24: At design and development stage. | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review for Building 1 | E24 + 5 months | Once installation of the FADS system is complete, factory will submit full "as-built" documentation of the system to Pakistan Accord for review for Building 1 |  |  | 13-12-24: At design and development stage. | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation for Buildings 1, 2 and 3 | E25 + 3 months | Factory will advise Pakistan Accord when FADS installation fully completed and ready for on-site verification for Buildings 1, 2 and 3 |  |  | 13-12-24: At design and development stage. | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site for Buildings 1, 2 and 3.. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E28 + 3 months | Factory will provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site for Buildings 1, 2 and 3. |  |  | 13-12-24: At design and development stage. | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Emergency Lighting | Provided but insufficient | This relates to the whole facility. During the inspection, it was noted that an emergency system was present but not fully functional. Some defects observed were (non-exhaustive): - emergency lights were absent on the walkway and stairs (eg, Building 2, Building 3, 2nd Floor cutting area)) - some emergency lights were not operational - inadequate illumination levels (eg. Building-1 First Floor Ladies Token Area, Building 2 Second Floor Stitching Area, Office Area, Utility Building Generator Rm) | Repair or replace Emergency Lights and batteries with devices located in accordance with NFPA 101. Replace batteries where necessary to ensure that emergency lights operate continuously for the duration required by the Building Code of Pakistan. Ensure that current system is fully operational | 3 months | Factory will provide evidence of how it has repaired & replaced emergency lights including batteries with listed devices as per Standards. |  |  | 13-12-24: This issue persist in the factory. | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Emergency Lighting | Provided but insufficient | This relates to the whole facility. During the inspection, it was noted that an emergency system was present but not fully functional. | Provide fully functional emergency lighting system covering all internal and external escape routes according to Pakistan Accord Building Standard & BCP 10.14.1 & 10.14.2, | E31 + 3 month | Factory will ensure that it has a fully functional emergency lighting system covering all internal and external escape routes for Buildings 1. 2 & 3, and in accordance with Pakistan Accord Building Standard & BCP 10.14.1 & 10.14.2, |  |  | 07/09/2024 - Factory reported this as Done 13-12-24: - When tested many of them did not have sufficient battery backup in building 1, 2 and 3. | Pending Verification
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Cabling & Wiring | Cables support and protection | During the inspection, it was found that: - Power cables at roof level in PVC trunking and not adequately protected from environment | Replace PVC trunking at roof level with a fixed cable tray or in a cable trench to ensure power cables are concealed. | 3 months | We will replace all PVC trunking at roof level with fixed cable to ensure power cables are concealed. |  |  | 13-12-24: - Rectified | Corrected
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Cabling & Wiring | Cables support and protection | During the inspection, it was observed that cable insulation was damaged due to lack of support in: - Building-1 Ground Floor sampling area, cutting area - Cable trays with inadequate support (eg. Building-2 Ground Floor Stitching Area | Replace all insulation damaged cables in the cutting area. Protect and install support for all cables which are open and loose. | 3 months | Factory will provide evidence to show how 1. It has replaced all insulation damaged cables in the cutting area. 2. Further it has installed support for all cables which were opened & loose. |  |  | 07/09/2024 - Factory reported this as Done 13-12-24: - Rectified | Corrected
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Cabling & Wiring | Cables support and protection | During the inspection, it was observed that there was cable insulation damage due to sharp edges/openings in cable trays at: - Building-2 Second Floor Stitching Area | Seal any openings in cable trays and ensure that no sharp openings are created in the future. | 3 months | Factory will provide evidence to show how it has sealed openings in cable trays and ensured that no sharp openings are created in future. |  |  | 07/09/2024 - Factory reported this as Done 13-12-24: - Rectified | Corrected
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Cabling & Wiring | Cables support and protection | During the inspection, it was observed that some cable trays had inadequate support in: - Building-2 Ground Floor Stitching Area | Add required supports with cable trays. | 3 months | Factory will provide evidence to show how it has provided required supports with cable tray in Building-2 Ground floor Stitching Area. |  |  | 07/09/2024 - Factory reported this as Done 13-12-24: - Rectified | Corrected
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Cabling & Wiring | Cable trench and channel cleanliness | This relates to the whole facility. It was noted in several locations that the cleanliness of the trunking system was not being maintained. The cable trunking system was filled with a dust and fluff, posing a high fire risk. Some areas where this was observed are (non-exhaustive): - Building-1 Ground Floor Cutting Area - Building-2 First Floor Stitching Area | Ensure that electrical trunkings are cleaned, inspected, and free from dust and dirt. Develop a periodic cleaning record for each cable tray and cable trench. | 2 months | Factory will provide evidence to show how it has cleaned electrical trunkings located in Building-1 Ground Floor Cutting Area & Building 2 First Floor Stitching Area. Factory will develop a periodic cleaning record for each cable tray and cable trench. |  |  | 13-12-24: - To be rectified. | Pending Verification
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Cabling & Wiring | Splicing of cables | This relates to the whole facility. Cables terminations installed without cable lugs, which results in breaking strands, loose connection and burn signs observed in: - Building-1 First Floor DB - Building 2 Ground Floor DB | Carry out modifications necessary to ensure that all stranded cable terminations are installed with proper cable lugs. | 4 months | We will check & will do necessary modification to ensure that all stranded cable terminations are installed with proper cable lugs. |  |  | 13-12-24: - Rectified | Corrected
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Cabling & Wiring | Colour coding | This relates to the whole facility. In many distribution boards across all three buildings, deviations from cable color coding standards were found, posing a risk of misinterpretation and potential accidents. This was observed in DBs in (non-exhaustive): - Building-1 Ground and First Floors - Building 2 Ground and Second Floors | Where necessary replace wiring with correct colour codes to avoid any hazards arising from confusion over role of each wire. | 2 months | We will check all distribution boards & will replace wiring with correct colour codes to avoid any hazards within the facility. |  |  | 13-12-24: - Rectified | Corrected
3 | 8 |  | 143 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | DBs & Elec Protection Systems |  | This was found on Director office DB building 1. In these loop connections, one circuit breaker is energised by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilised to provide each circuit with the required live, neutral, and earth connections. | 3 months |  |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Follow Up | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Generator, Transformer & Substation room |  | In generator room, Several battery terminals were exposed and not properly insulated, increasing the risk of electrical shock or short circuits. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 1 months |  |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
13-Dec-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Klash Private Ltd. (Unit 1) Plot # 28 117 JB Near Paharange Drainage Millat Road Dhanola Faisalabad
[8 empty] | Date of Initial Inspection | [12 empty] | 18-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point | Remove all locking devices from doors on all egress routes that could prevent opening from inside | 1 month | Factory will remove all locking devices from doors along escape routes where doors could be locked preventing opening from the inside |  |  | 13-12-24: Locking mechanism again observed at site in Building 3 with wire lock provision in escape doors. | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 for Building 1 | 3 months | Factory will source a mechanism that allows for easy opening from inside, but lockable from outside where required. Will submit documentation of proposed mechanism to Accord for review before installing new locks in Building 1 |  |  | 13-12-24: Factory has installed a mechanism on one of the escape door in Building 3 that allows for easy opening from inside, but lockable from outside and will continue to install the same on all doors where required. | In Progress
[8 empty] | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 for building 2 | 3 months | Klash will source a mechanism that allows for easy opening from inside, but lockable from outside where required. Will submit documentation of proposed mechanism to Accord for review before installing new locks in Building 2 |  |  | 13-12-24: Factory has installed a mechanism on one of the escape door in Building 3 that allows for easy opening from inside, but lockable from outside and will continue to install the same on all doors where required. | In Progress
[8 empty] | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 for Building 3 | 3 months | Klash will source a mechanism that allows for easy opening from inside, but lockable from outside where required. Will submit documentation of proposed mechanism to Accord for review before installing new locks in Building 3 |  |  | 13-12-24: Factory has installed a mechanism on one of the escape door in Building 3 that allows for easy opening from inside, but lockable from outside and will continue to install the same on all doors where required. | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Escape doors | Doors on escape routes are swinging in the wrong direction (inwards): - Building 1, 3rd Floor Canteen Emergency Stair door swinging in the opposite direction of emergency travel - Building 1, 3rd Floor sample room emergency staircase - Building 1, 2rd Floor cutting area and staircase - Building 3 level 2 technologist department | Escape doors to be side hung doors that swing in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | Factory will change the direction of escape doors to swing outwards and will provide opening mechanisms as per Accord Building Standard Section 1 Clauses 1.4 and 1.5 in Building 1, 2 & 3 |  |  | 13-12-24: 1. Factory to remedy the issue in Building 1. Not completed 2. Factory to remedy the issue in Building 1. Not completed 3. Factory has done the remedy of the issue. Issue resolved 4. Office door now swinging outwards. Issue resolved. | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Escape doors | Doors on escape routes that swing in both directions | Ensure that doors can swing in the direction of escape and are easily opening in compliance with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | We will ensure opening the direction of escape for all escape doors and will provide opening mechanisms as per Accord Building Standard Section 1 Clauses 1.4 and 1.5 in Buildings 1, 2 & 3 |  |  | 13-12-24: Factory will replace the doors with side hung that swing in the direction of escape and Accord will review the provisions on upcoming Follow Up Inspection. | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F7 | Means of Escape | Escape doors | Sliding exit doors observed on Klash Unit 1 in the following areas (non-exhaustive): - Building 1 production area, canteen, offices, exit stairways. | Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors, that are side swinging and open in the direction of travel to an exit. | 3 months | We will replace all non-compliant sliding doors with Swinging doors which will open in direction of escape. |  |  | 13-12-24: Drawings of the proposed solution to this issue will be submitted to Accord for review. | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F8 | Means of Escape | Number of exits | Per Pakistan Accord Standard there should be a minimum 2 exits from every occupied floor. - Building 1 stitching area 2nd floor has only one emergency staircase S-3, and the route to staircase S1 converges on the space next to S-3 so does not provide an alternative | Develop plan and drawings to provide additional exit where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | We have developed Plan regarding additional exit & will share with Accord for approval. |  |  | 13-12-24: Factory will re submit the plan to rectify the issue. | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Number of exits | Per Pakistan Accord Standard there should be a minimum 2 exits from every occupied floor. | Implement the above plan as agreed with Pakistan Accord. Number of exits from all floors and parts of the building should comply with Pakistan Accord Building Standard. | F8 + 4 months | Once Plan will be approved from Pakistan Accord team's side, work will be implemented. |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Travel distance | Excessive Travel Distance were observed in: Building 1 - Ground and 1st Floors, from office areas - 2nd Floor from offices and stitching areas | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | We have developed Plan regarding excessive travel distance regarding alternative escape route. We will send to Pakistan Accord as pdf file for review. |  |  | 13-12-24: Factory has submitted the design documents for review by Accord. | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Travel distance | Excessive Travel Distance were observed in: Building 1 - Ground and 1st Floors, from office areas - 2nd Floor from offices and stitching areas | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F10 + 4 months | Once Plan is approved from Accord team, factory will implement the remedial work. |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Protection of stairs | Per Pakistan Accord Building Standard, exit stairs should be adequately protected. This is not always achieved, as observed (list not exhaustive): - unprotected openings into stairs S-1, S-3, S-4, S-7 and S-8 etc. - no fire doors on S-3 and S-4. - fire load in stairs S-3 and S-7. - services passing through stairs S-15 | Remove fire load and any other obstructions due to stored items from stairs | 2 weeks | We have removed fire load & other obstruction near stairs. We will submit evidence to Accord and monitor this issue on daily basis. |  |  | 13-12-24: Fire load still observed in S7, factory to resubmit the design and evidence to Accord for review. | Pending Verification
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Protection of stairs | Per Pakistan Accord Building Standard, exit stairs should be adequately protected. This is not always achieved, as observed (list not exhaustive): - unprotected openings into stairs S-1, S-3, S-4, S-7 and S-8 etc. - no fire doors on S-3 and S-4. -fire load in stairs S-3 and S-7. - Services passing through stairs S-15 | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | We have discussed this with our structural engineer, he will finalized & provide drawings. Once drawing will be received, will share with Accord team for approval. |  |  | 13-12-24: Factory has submitted the design to Accord and once reviewed factory will start remediation work. | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Protection of stairs | Per Pakistan Accord Building Standard, exit stairs should be adequately protected. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. Note that the final exit door from a stair to outside the building does not need to be fire rated. - All penetrations through stairs need to be fire stopped. Unprotected openings (e.g. holes or window/louver openings) are not permitted. - Where stairs discharge within a building, a fire separated corridor shall be provided that leads outside building. | F13 + 4 months | Once drawing is finalized & approved from Accord side, we will implement the agreed solution. |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit access | Corridor from basement area is not fire separated from the rest of the building to protect the exit route from Building 3 basement production hall. | For protected corridors leading to floor or building exits, prepare drawings showing the proposed fire separating construction to discharge routes to the building exit. These shall be submitted to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | Drawing with proposal for protecting the corridor will be submitted to Accord for review. |  |  | 13-12-24: Factory will re submit the plan to rectify the issue. | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit access | Corridor from basement area is not fire separated from the rest of the building to protect the exit route from Building 3 basement production hall. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90 minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Building Standard. Some of the key requirements include: - All doors into protected corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into exit discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge routes need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F15 + 4 months | Once design and drawings has been approved from Accord, we will carry out the remedial work accordingly. |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm. This was observed in: - Building 1 – emergency staircase S4 from roof to the 3rd floor of 1,880 mm was observed | Fix headroom height safety signage and other measures required to ensure safe passage where head height is less than 2.05 m on the escape route | 1 month | We have fixed headroom height safety by taking some immediate corrective action on all floors. Safety signs posted, padding also done to protect head injury. Evidence will be submitted to Accord for review |  |  | 13-12-24: Factory has installed padding on the passage and head room issue is resolved. | Corrected
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm. This was observed in: - Building 1 – emergency staircase S-4 from roof to the 3rd floor of 1,880 mm was observed | Implement measures to ensure adequate clear height along all escape routes or provide alternative escape route as required after Pakistan Accord review. | F17 + 4 months | As per discussed with our structural team, we are unable to make any modification with current beam structure. We have taken some safety measure regarding headroom height safety.Modifications will be made if necessary once reviewed by Accord and feedback received |  |  | 13-12-24: Measures Implemented by factory are reasonable and issue is resolved. | Corrected
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit signage | Exits routes must be clearly marked by approved exit signage. The following deficiencies have been observed in all buildings, (list not exhaustive): - Missing exit signs at stair discharge routes - Missing exit signs in corridors and circulation areas - Missing exit signs in production areas - Electrically powered exit signs are not a tested and listed system. - Misleading escape signages e.g. Building 3 storage area | Remove misleading direction arrows from the means of egress. | 1 month | We have removed misleading direction arrows from the means of egress. We will submit evidence of how it was addressed to Accord |  |  | 13-12-24: Misleading signage issue is resolved by the factory. | Corrected
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Exit signage | Exits routes must be clearly marked by approved exit signage. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standards And BCP 10.15.1, 10.15.2 and 10.15.3 | F19 + 2 months | Pakistan Accord Building Standardand BCP 10.15.1, 10.15.2 and 10.15.3, We will submit marked up plans showing exit signs at stairs, corridors, circulation and in Production areas as well. |  |  | 13-12-24: Factory will submit details of the signage to the Accord for review and will resolve the issue in 2 months. | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Means of Escape | Exit signage | Exits routes must be clearly marked by approved exit signage. | Ensure that all exit signage is checked periodically and in good working condition. | 3 months | We will install exit signs at stairs, corridors, circulation and in Production areas as well. We have marked all exit routes with clear signage & electrical staff is doing inspection monthly basis. Inspection record is available for review. |  |  | 13-12-24: Factory will make the schedule of the signage inspection and implement it after review by Accord. | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Standpipe system | Per Pakistan Accord Building Standard a Class-I standpipe systems is required in the building. The system should be designed and installed in accordance with NFPA 14. The following deficiencies have been observed on site, including (list not exhaustive): - Location of standpipe outlets not compliant - Missing standpipe outlets in stairs - Insufficient number of risers and hose connections in all buildings. | (1) Submit design documentation for a standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24 | 4 months | Factory wil submit full documentation with the design proposal for the standpipe system demonstrating compliance with all relevant standards. |  |  | 13-12-24: Factory will submit design documents to Accord for review in 2 months. | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F22 + 1 month | We will discuss with fire safety, electrical expert team. After their recommendation will prepare reference drawings & will share with Pakistan Accord for review. Once it will be approved, then work will be started accordingly. |  |  | 13-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS | F23 + 4 months | After discussed with technical experts, work will be implemented accordingly. |  |  | 13-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F24 + 3 months | After discussed with technical experts, factory will submit the as built documentation |  |  | 13-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F25 + 3 months | Factory will advise Pakistan Accord that SUPS installation fully completed and fully functionally. |  |  | 13-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Suppression | Standpipe system | Class-I standpipe systems is required in the building designed and installed in accordance with NFPA 14. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F26 + 3 months | Factory will provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team |  |  | 13-12-24: At design and development stage (step 1) | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Suppression | Fire pumps | A complete fire pump set is required when a standpipe is required, designed and installed in accordance with NFPA 20 and comprising of a) Electric pump (Main), b) Diesel Pump (Back-Up), and c) Jockey Pump. The following deficiency was observed on site: - All pumps and controllers are non-listed. | Provide full pump set complying with NFPA 20 as part of the supporting infrastructure for the SUPS system | 18 months | Pumps will be installed as part of the SUPS infrastructure as above. |  |  | 13-12-24: Factory will submit design documents to Accord for review in 2 months. | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Separation of shafts | Shafts should be enclosed in fire resisting construction to maintain compartmentation between floors. The following deficiencies have been observed (list not exhaustive): - Building 2, all floors - Lift shafts not separated with fire rated construction from Production / Storage areas | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Drawing with proposal for separation of the shafts will be submitted to Accord for review |  |  | 13-12-24: 1. Assessed the lift shafts per Accord guidelines and no fire separation of lift shaft is required as the shafts are not in exit routes and the steel doors are auto closing when lift is moving. Factory to submit the egress layouts of Building 2 highlighting the lift shafts not in use of exit passage. | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Separation of shafts | Building 2, all floors - Lift shafts not separated with fire rated construction from Production / Storage areas | Provide 2-hour fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord. | F29 + 4 months | Once drawing is has been reviewed and approved from Accord, we will implement the work accordingly. |  |  | 13-12-24 Issue will be mark completed once the design is reviewed by Accord and found as per description in F29. | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Floor openings | Each floor should be fire separated using 2 hours fire resisting construction with 90 minutes fire rated door/shutter assemblies sealing penetrations. The following deficiencies were observed on site (list not exhaustive): - Non-fire-rated cable penetrations (e.g. electric cables passing between floors in Building 3 | Maintain fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory to submit documentation with proposals for sealing penetrations |  |  | 13-12-24: Factory will submit the plan on how to do the fire stop on the floor openings. | Pending Verification
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Floor openings | Non-fire-rated cable penetrations (e.g. electric cables passing between floors in Building 3 | Separate floors by fire-rated floor/ceiling assemblies in accordance with the Pakistan Accord Building Standard | F31 + 4 months | We have discussed with electrical team, they will complete the work regarding fire rated cable penetration which are passing between floors in Building 3. |  |  | 13-12-24: Factory will commence the werk once the plan is reviewed by Accord. | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Separation of occupancies | Different occupancy types are required to be fire separated from each other: The following deficiencies have been observed (list not exhaustive): - Building 1, Office and Production areas not separated from Process Storage. - Building 2, Offices are not separated from IT room. - Building 2 ground floor office block not fire separated from exit enclosure - Building 3, Separation required between Mosque & Cutting Department | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors) | 4 months | Drawing with factory proposal for the fire rated separation complying with Pakistan Accord will be submitted to Accord for review |  |  | 13-12-24: 1. Factory will submit design to Pakistan Accord for review. 2. Factory has proposed plan to relocate the IT room and will submit the design to Accord for review. 3. Factory will submit the updated design to Accord for review. 3. Factory has provided fire separation between mosque and Cutting department. | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Separation of occupancies | - Building 1, Office and Production areas not separated from Process Storage. - Building 2, Offices are not separated from IT room. - Building 3, Separation required between Mosque & Cutting Department | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord | F33 + 4 months | Once proposal has been reviewed by Accord factory will implement the work regarding fire rated separation between occupancies in accordance with Pakistan Accord Building Standards. |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Storage | Storage occupancies need to be fire separated using fire resisting walls with fire rated doors. Miscellaneous (in process) storage can be accommodated in the production floor where it meets the following limitations: - Storage areas do not exceed 10 percent of the floor area - Storage areas do not exceed 2.45m in height - Storage areas do not exceed 23m² in one area - Storage areas are separated from other storage areas by at least 3m. The following was observed where storage was not separated from other occupancies by fire rated construction, (list not exhaustive): - Building 1 Ground floor, 1st floor. - Building 2 Ground floor production area. - Building 3 packing area to Prayer area. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Storage areas will be identified, and proposals submitted to Accord on a drawing showing where in-process storage will be located and which areas need to be fire separated as dedicated storage spaces |  |  | 13-12-24: 1. Storage not fire separated from production in Building 1, Factory will resubmit the design to Accord for review. 2. Storage in the Building 2 ground floor is being removed, once completed the factory will submit the details of the actions that they have done in remediation of this storage separation. 3. Factory will submit updated design with storage areas highlighted and the planned separation of storage from other occupancies to Accord for review by 31st Jan 2024. | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Storage | Storage occupancies need to be fire separated using fire resisting walls with fire rated doors. Miscellaneous (in process) storage can be accommodated in the production floor where it meets the limitations | Identify in-process storage areas on site by floor markings complying with dimensional limitations. Ensure that the above plan is implemented for fire rated separation of storage following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F35 + 4 months | Once drawing has been reviewed and agreed by Accord, the factory will implement the layout previously submitted to Pakistan Accord. |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Fire Rated Construction | Separation of high-risk areas | High fire risk areas require to be fire separated from the rest of the building with 2 hour fire resisting construction with 90 minutes fire doors. The following deficiencies were observed (list not exhaustive): - Building 3, Separation required between Finished goods warehouse & LT cabinet 1000A - All floors – All Buildings have High Voltage Panels not separated from working Stations - Gas line is not fire separated. - Building 3, Electric room is not fire Separated | Prepare drawings showing the proposed fire separation details of high fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | Fire Pump room not included in K-1 Building, it is included in K-2, Only electrical and gas line drawing to Unit 1 will be submitted to Accord for review |  |  | 13-12-24: 1. Electrical room in Building 3 is fire separated and the factory will provide the details of Fire Doors to the Accord for verification. 2. Reassessed the risk of the panels, no fire separation is required and the only requirements regarding these panels is to ensure the fire load remain at a safe distance from these panels. 3. Reassessed the fire risk of these gas lines and there is no fire separation required as the occupants has alternative exit discharge routes from all buildings. 4. Reassessed the fire risk of this electrical room and there is no fire separation required as the occupants has alternative exit discharge routes from all buildings. | Pending Verification
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Rated Construction | Separation of high-risk areas | The following deficiencies were observed (list not exhaustive): - Electrical rooms are not fire separated, - Gas line is not fire separated. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord | F37 + 4 months | Fire Pump room not included in K-1 Building, it is included in K-2., Once drawings have been reviewed by Accord electrical and gas lines will be separated as agreed |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Hazardous Materials | Chemicals storage | Chemical storage areas should be fire separated from the rest of building, with adequate ventilation. The following deficiencies were observed (list not exhaustive): - Chemicals in Generator room, Boiler room at Building 2 Ground floor without containment | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms | 4 months | MSDS sheets are displayed and chemical drawing sheet will be submitted to Accord for review |  |  | 13-12-24: Building 2 level ground chemical spillage containment not proper Factory has submitted the drawings of fire separation of chemical storage room from building. | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Hazardous Materials | Chemicals storage | Chemicals in Generator room, Boiler room at Building 2 Ground floor without containment | Implement the above plan reviewed earlier by Pakistan Accord. All chemical storage areas to be compliant with Pakistan Accord Building Standard | F39 + 4 months | All Chemicals will be removed from boiler and generator area and relocated to a designated area. |  |  | 13-12-24: Factory will implement after plan review by Accord | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Fire Safety Management | Records of systems maintenance | Fire safety systems should be adequately maintained to ensure they will operate effectively in and event of and emergency. Maintenance records for the following were not available or inadequate (list not exhaustive): - Fire Pumps - Standpipes - Emergency lighting - Fire Extinguishers - Fire Doors | Prepare maintenance schedule for all life safety systems | 3 months | Factory will prepare a maintenance schedule for all life safety system & will share with Pakistan Accord. |  |  | 13-12-24: Factory has submitted maintenance schedule for life safety systems to Accord for review. | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Fire Safety Management | Records of systems maintenance | Maintenance records for all life safety systems were not available or inadequate | Prepare a schedule of proposed system maintenance. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | Factory will prepare a maintenance schedule for all life safety system & will share with Pakistan Accord. |  |  | 13-12-24: Factory will proceed with the maintenance documents and record keeping as per the review by Accord. | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F43 | Fire Safety Management | Records of systems maintenance | Maintenance records for all life safety systems were not available or inadequate | Ensure all systems are being maintained as per the schedule agreed with Accord. Keep maintenance records | F42 + 3 months | Our fire safety Team is responsible for all life safety equipments & they will prepare and keep maintenance records for all life safety systems |  |  | 13-12-24: Factory will proceed with the maintenance documents and record keeping as per the review by Accord. | In Progress
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F44 | Fire Safety Management | Records of system testing | Fire safety systems should be adequately tested to ensure they will operate effectively in and event of and emergency. Records of testing for the following were not available or inadequate (list not exhaustive): - Fire Pumps - Standpipes - Emergency lighting - Fire Extinguishers - Fire Doors | Prepare testing schedule for all life safety systems | 3 months | Factory will prepare testing schedules for all life safety system & will share with Pakistan Accord. |  |  | 13-12-24: Factory has submitted testing schedule for life safety systems to Accord for review. | In Progress
3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F45 | Fire Safety Management | Records of system testing | Maintenance records for all life safety systems were not available or inadequate | Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | Factory will prepare testing schedules for all life safety system & will share with Pakistan Accord. |  |  | 13-12-24: Factory will proceed with the testing documents and record keeping as per the review by Accord. | In Progress
3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F46 | Fire Safety Management | Records of system testing | Maintenance records for all life safety systems were not available or inadequate | Ensure all systems are being tested as per the schedule agreed with Accord . Keep test records | F45 + 3 months | Our fire safety Team is responsible for all life safety equipments & they will prepare and keep testing records for all life safety systems |  |  | 13-12-24: Factory will proceed with the testing documents and record keeping as per the review by Accord. | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
13-Dec-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Klash Private Ltd. (Unit 1), Plot # 28 117 JB Near Paharange Drainage Millat Road Dhanola Faisalabad
[8 empty] | Date of Initial Inspection | [12 empty] | 18-Mar-2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floor appears to be overstressed. The drawing show 16T25s in columns whereas we scanned 6T25s, 2 on each face. The internal and external columns at the Ground floor level of building 1 and building 2 appear to be highly stressed. We noted floor finishes of 180mm contributing to high superimposed dead load. | Appoint a qualified and experienced structural engineer immediately to remove the concrete cover of 2 sample columns to expose the reinforcement as a check on number and diameter of the reinforcing bars in the column and submit results to Pakistan Accord for review and further instruction. This can be done on columns at first floor of buildings 1 and 2. | 3 months | 1. Factory have appointed qualified structural engineer and had meeting with him on each point. 2. Factory have taken sample of core testing in yellow highlighted columns of building-1 and building-2 to expose the reinforcement as a check on number and diameter of the reinforcing bars in the column and send for testing. 2. Received test result of core testing. Factory will share documentation giving results of these tests to Accord for review |  |  | 13/12/24: 1) Factory appointed the structural engineer. 2) Factory shared the core test results and also shared the reinforcement data after column chipped Results. 3) Factory submitted the core test report and pictorial evidence of reinforcement in column. Based on provided core test results from column stress analysis we obtained factor of safety in amber zone. | Corrected
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | Structural engineer to carry out Ferroscan of the columns in which reinforcement has been exposed as well as all columns at Ground Floor level in the yellow shaded area in Figure 21 of the report. | 3 months | 1. Factory have appointed qualified structural engineer and had meeting with him on each point. 2. Factory have carried out Ferroscan of the columns in which reinforcement has been exposed as well as all columns at Ground Floor level in the yellow shaded area. 2. Received test result of core testing. Factory will share documentation giving results of these tests to Accord for review |  |  | 13/12/24: 1) Factory appointed the structural engineer. 2) Factory shared the ferroscan test results. 3) Factory submitted the ferroscan test report. Provided results matched with initial inspection conducted by Accord. | Corrected
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | (1) Appoint qualified and competent Structural Engineer to carry out DEA on the full building ( buildings 1 and 2), in accordance with the DEA scope and minimum requirements set out in the Initial Inspection report. | 1 months | 1. Factory have appointed qualified structural engineer and had meeting with him on each point. 2. Structural engineer will provide carried our DEA scope of building 1 and building 2. |  |  | 13/12/24: 1) Factory appointed the structural engineer. 2) Factory committed to provide DEA on 28/12/24 for building-2 only. 3) Factory decided to dismantle building-1. | Corrected
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | (2) Submit accurate As-built Drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied, to Pakistan Accord for review | S3+ 3 months | Factory will submit the as-built drawings showing structure, loading, elements, dimensions, levels, foundations and framing on Plan, Section and Elevation drawings and a report on Engineering tests carried out to justify material strengths and reinforcement content in all key elements studied. |  |  | 13/12/24: Factory committed to provide as-built detailed architectural and structural drawings on 28/12/24 for both building-1 and building-2. | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | (3) Submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan | S4+ 4 months | Factory will submit structural engineering assessment with supporting calculations based on the as-built drawing and material strengths reviewed previously using a model-based design that justifies the safety and serviceability of the building against loading as set out in Building Code of Pakistan |  |  | 13/12/24: 1)Factory committed to submit 3D model with supporting calculations on 28/12/24 for building-2. 2)Factory decided to dismantle building-1. | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | (4) Submit proposals for any retrofitting works that may be needed to demonstrate the adequacy of the structure to Pakistan Accord for review | S5 + 4 months | As we have conducted core testing and ferro scanning (see attached) if any retrofitting required then we will submit proposals. |  |  | 13/12/24: 1) Factory committed to submit the detailed proposal of retrofitting with supporting calculations on 20/12/24 for building-2 only. 2) Factory decided to dismantle building-1. | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord on Building 1 | S6+ 6 months | As we have conducted core testing and ferro scanning (see attached) if any retrofitting required then we will submit proposals. |  |  | 13/12/24: 1) Factory decided to dismantle building-1. 05/06/2025: 1) The Factory has not dismantled building 1 yet and need to submit the timeline when the factory plans to proceed with dismantling | In Progress
[8 empty] | Initial | [10 empty] | S8 |  |  | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | (5) Carry out all retrofitting works if needed as proposed and previously reviewed by Pakistan Accord on Building 2 | S6+ 6 months | As we have conducted core testing and ferro scanning (see attached) if any retrofitting required then we will submit proposals. |  |  | 13/12/24: 1) Factory committed to submit the detailed proposal of retrofitting with supporting calculations on 20/12/24 for building-2. | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Potential Overstress | Highly stressed columns | Based on an initial assessment the columns on the ground floors of buildings 1 and 2 appear to be overstressed. | (6) Factory to advise Pakistan Accord when all retrofitting works are complete and make provision for a verification inspection attended by the factory Structural Engineer. Once Pakistani Accord has verified retrofitting works in accordance with previously reviewed proposals, then this item will be complete | S8+ 1 month | Based on the remarks of structural engineer assessment accord will advise us retrofitting plan if needed. |  |  | 13/12/24: 1) Factory committed to submit the detailed proposal of retrofitting with supporting calculations on 20/12/24 for building-2 only. 2) Factory going to dismantle building-1. | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Other Damage/Defects | Corrosion of reinforcement | Building-2 boiler area column and beam reinforcement was observed as rusted due to moisture ingress. | Building Engineer to inspect the areas which is experiencing water leakage and propose measures to prevent further damage and carry out repair works. | 6 months | Structural engineer inspected the leakage and rectified as well and also prepared retrofitting measures to prevent further (see attached) |  |  | 13/12/24: Factory repaired the inner side of the building whereas the outer side is still affected from seepage and corrosion. Factory committed to repair after completion of DEA. | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Structural Documentation | Undocumented extension | Following items needs to be updated on as-built structural drawings produced as part of DEA: - Building 2 boiler area extension - Additional rooms and steel shed on roof of building 1 and building 2 - Building 1- 2nd floor roof slab beam framing plan | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | Factory wil update Building 2 boiler area extension Additional rooms and steel shed on roof of building 1 and building 2 , Building 1- 2nd floor roof slab beam framing planin as built drawing. |  |  | 13/12/24: Factory committed to submit the updated structural drawings on 5/1/24, 20/1/25, and 28/2/25 for all buildings. | In Progress

## ECats
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Cable size
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## FCats
Categories | Means of Escape | Fire Rated Construction | Hazardous Materials | Fire Suppression | Fire Safety Management
Means of Escape | Protection of stairs | Structural fire rating | Chemicals handling | Standpipe system | Fire drills
Fire Rated Construction | Number of exits | Extensive voids | Chemicals storage | Fire extinguishers | Records of systems maintenance
Fire Suppression | Travel distance | Separation of high-risk areas | Diesel storage | Fire pumps | Records of system testing
Hazardous Materials | Exit capacity | Separation of shafts | Gas storage | Sprinkler system | Staff training
Fire Safety Management | Exit access | Separation of occupancies | fsdf | Water supply | Emergency Action Plan
| Escape stair condition | Floor openings |  | Exterior hydrants | Fire vehicle access
| Exit discharge | Storage |  | dsfdsf
| Escape doors | Atrium
Exit signage
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## SCats
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1