## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
01-Dec-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Chottani Industries, Plot # 487/A S.I.T.E, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 01-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | This relates to the whole facility: - Single Line Diagrams were not provided. | Consult a qualified engineer to design the entire Single Line Diagrams and rectify design issues. | 3 months | Factory will appoint an electrical consultant to complete an as-built SLD and submit to Accord |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | This relates to the whole facility: - Thermographic & Insulation Test Reports were not provided. - Earth testing report were not available on site. | Thermographic & Insulation Testing, Earth Testing reports shall be prepared and submitted to Pakistan Accord for review. | E1 + 6 months | Factory electrician will carry out the test and provide report to Accord |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | This relates to the whole facility: - Maintenance record was provided. | Maintenance records shall be maintained periodically. | 3 months | Maintenance records will be updated on 6-monthly basis |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | Diagrams & Drawings | Electrical layout drawing | This relates to the whole facility: - As-built Layout drawings were not provided. | Consult a Qualified Engineer complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. Submit completed layout drawings to Pakistan Accord for review | E4 + 6 months | Factory will appoint an electrical consultant to complete an electrical layout drawing and submit to Accord |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | This relates to the whole facility: Lightning protection system is not installed in the facility. Any document related to LPS assessment was not presented. | Risk assessment for Lightning Protection System should be carried out by qualified engineer and submitted to Pakistan Accord for review. | 2 months | Factory will appoint an electrical consultant to carry out an assessment on requirement for LPS and submit report to Accord |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | Lightning protection system is not installed in the facility. Any document related to LPS assessment was not presented | Design system if required and implement accordingly. | E5 + 6 month | If LPS required, factory will install |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. Also noted direct feeding of equipment wires into an electrical outlet without the presence of a proper socket. PVC Tapping joints found in different distribution boards. Some of distribution boards having chattering sound which could be a loose connection or any other issue. Exposed cables seen with Tape Joints ground floor near restrooms, in distribution board first floor, near Boiler, and many more areas. | No more flexible cables be cut and taped in the facility. Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. | 4 months | Cut and taped cables will be replaced |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. Also noted direct feeding of equipment wires into an electrical outlet without the presence of a proper socket. PVC Tapping joints found in different distribution boards. Some of distribution boards having chattering sound which could be a loose connection or any other issue. Exposed cables seen with Tape Joints ground floor near restrooms, in distribution board first floor, near Boiler, and many more areas. | Enclose and protect any exposed wires using conduit, cable trunking, or other appropriate means to prevent contact and minimize the risk of electrical shock. | 2 months | Exposed wires will be enclosed |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility that where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. Also noted direct feeding of equipment wires into an electrical outlet without the presence of a proper socket. PVC Tapping joints found in different distribution boards. | Install a socket outlet suitable for the equipment's electrical requirements. Securely terminate and connect the equipment wires to the newly installed socket outlet. Ensure that wiring is properly insulated, color-coded, and follows standard electrical practices. | 3 months | Suitable socket outlets will be installed and wires securely terminated and connected |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | Cabling & Wiring | Fixture | Loose wiring and inappropriate cable mesh were found throughout the facility, especially in a Telephone distribution board near Ground Floor LT Room. Cables found hanging from cable containments in an inappropriate way, also the industrial sockets were not fix appropriately which could be a potential hazard. | Industrial socket shall be fixed in appropriate manner and all exposed wiring should be rectified. Any kind of exposed wiring shall be avoided in future installation. | 3 months | Industrial sockets will be fixed |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | Cabling & Wiring | Cables support and protection | In various areas throughout the facility there was no cable containment such as the backyard area of ground floor, however, the existing containments have cable dressing issues. | Schedule a proper inspection and maintenance to monitor, control and rectify weak electrification works. | 3 months | Maintenance will be scheduled on 6-monthly basis |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | Cabling & Wiring | Cables support and protection | In various areas throughout the facility there was no cable containment such as the backyard area of ground floor, however, the existing containments have cable dressing issues. | Install appropriate cable containment arrangement for the electrical system. | E11 + 2 months | Appropriate cable containment arrangement will be installed |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Loop Connection | There is cross-circuiting (Looping, Bunching at Moulded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels throughout the facility | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new distribution board adjacent to existing panel. For any future work avoid looping and bunch of cable at MCCB/MCB or bus bar terminal, use individual circuit and overcurrent device for every incoming and outgoing circuit at the distribution boards. | 3 months | Circuits will be modified to avoid breaker sharing |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Lint & dust inside panel board | This relates to the whole facility. It was noted in several locations that the cleanliness was not being maintained within the electrical panels and trunking system | All distribution board to be cleaned and maintained clean. | 1 month | Factory electrician will clean out all electrical panels and trunking |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Lint & dust inside panel board | This relates to the whole facility. It was noted in several locations that the cleanliness was not being maintained within the electrical panels and trunking system | Develop a periodic maintenance record of distribution board and cable trays. Initiate a regular maintenance and cleaning schedule for all electrical panels. | 1 month | Factory already implementing a maintenance schedule, will review schedule for improvements and provide Accord with documented evidence |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Hot Spots | This relates to the Main Building on level(s) L01 - 1st Floor: Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. | Inspect the electrical panel to identify the source of abnormal temperatures, which may be caused by loose connections, Overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, or replacing faulty components. | 1 month | Factory will inspect the panel with a thermal camera and identify cause of hotspots and then implement corrective action to eliminate the problem |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Hot Spots | This relates to the Main Building on level(s) L01 - 1st Floor: Within electrical panels at cable termination points, there are signs of overloading and resulting abnormal temperatures. | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at intervals of no less than 6 months. Carry out independent thermographic survey. | E16 + 6 months | Factory will carry out full thermographic survey and submit report to Accord. Will advise Accord on intended frequency of thermographic surveys |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Main Building on multiple levels: There was too much combustible material storage near a distribution board, also the clearance near distribution board is less than 1.0 m. | Designate regular stacking and storage areas, far from electrical distribution boards. The area near distribution board needs to be clear up to 1.0 m radius. | 2 months | Stacking and storage areas will be designated |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Earthing system | This relates to the whole facility: No earth cables found in many areas such as compressor, finishing distribution board first Floor. Many of the 4 pin connectors of the machines are only supplied by single or three phase wiring with no earthing cables | All earth connections must be connected to earth pits via their respective distribution board. | 6 months | Earth connections will be made via respective DBs |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) B01 - Basement: Many areas were found to have connector issues, unplugged wires, loose connections, unusual wiring and damage IT switches that are near to risk of fire. The CCTV camera adapter found in an unacceptable condition. | Connect all wired connection with rated power sockets. | 3 months | Rated power sockets will be used |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) B01 - Basement: Many areas were found to have connector issues, unplugged wires, loose connections, unusual wiring and damage IT switches that are near to risk of fire. The CCTV camera adapter found in an unacceptable condition. | Install a socket outlet suitable for the equipment's electrical requirements. Enclose and protect any exposed wires using conduit, cable trunking, or other appropriate means to prevent contact and minimize the risk of electrical shock. Securely terminate and connect the equipment wires to the newly installed socket outlet, ensuring waterproofing of external electrical devices/Wiring/Components. | 3 months | Suitable sockets will be installed |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Cabling & Wiring | Cables support and protection | Inappropriate installation of CTs found in cable trays below the distribution board. Any abnormal heating in Current Transformer (CTs) may cause damage to the cables inside the containment. | Remove Current Transformers from cable trays and install a separate metal box arrangement for it adjacent to distribution board. | 3 months | Correct installation of CTs will be made |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | DBs & Elec Protection Systems | Earthing system | This relates to the Main Building on level(s) L00 - Ground Floor: The foundation of the external floor below the electrical panel is metallic and the insolation pad beneath the panel is not suitable for insulation, posing an potential electrical hazard. | Connect whole foundation below the Electric panels to the earth terminal via nearest earth pit. | 6 months | Connections will be made correctly |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | DBs & Elec Protection Systems | Earthing system | This relates to the Main Building on level(s) L00 - Ground Floor: The foundation of the external floor below the electrical panel is metallic and the insolation pad beneath the panel is not suitable for insulation, posing an potential electrical hazard. | Metal that is likely to be live near electrical installation shall be bonded with earth to avoid any hazard. | 6 months | Metal floor will be earthed |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Earthing system | This relates to the Main Building on level(s) B01 - Basement: In most of the areas, earth bonding of cable tray, metal structures, metal tables etc. found missing for example in canteen, basement, and finishing distribution board . | Connect all metal bodies of Electric panels to the earth terminal within electric panels. Metal that is likely to be live near electrical installation shall be bonded with earth to avoid any hazard. | 6 months | All metal bodies will be earthed |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | DBs & Elec Protection Systems | Openings | This relates to the Main Building on level(s) L00 - Ground Floor: LT was in good condition however the safety plates were not removed on inspection day. There is a serious doubt of improper cable dressing, abnormal temperature, sharp edges, dirt and dust also bottom plates were not covered with proper cable glands. | Seal all bottom plates in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 3 months | Bottom plates will be sealed |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Main Building on level(s) L00 - Ground Floor: LT was in good condition however the safety plates were not removed on inspection day. There is a serious doubt of improper cable dressing, abnormal temperature, sharp edges, dirt and dust also bottom plates were not covered with proper cable glands. | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. | 3 months | Maintenance will be scheduled on 6-monthly basis |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | DBs & Elec Protection Systems | Adequate accessibility | This relates to the Main Building on level(s) L01 - 1st Floor. A distribution board found mounted at a very high point. | Need to be relocated at low level for easy access for operation and maintenance | 1 month | DB will be relocated for easy access |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | DBs & Elec Protection Systems | Panel/cabling/busbar | Panels were found in good condition, however, there is a need to have regular maintenance checks along with cable dressing. Some distribution board found to have Idle cables, improper dressing and tape joints | Develop proper maintenance records to monitor, control and rectify weak electrification works. Cable dressing needs to be done along with removal of Idle cables (if any). | 3 months | Cable dressing will be done Maintenance will be scheduled on 6-monthly basis |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Splicing of cables | This relates to the Main Building on level(s) L00 – Ground Floor: Cables termination installed without cable lugs, which results in breaking strands of the cables and gets heated. | All stranded cables terminations shall be installed with proper cable lugs. For any future works avoid terminating stranded cables without lugs. | 4 months | Stranded cables terminations will be installed with proper cable lugs. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | DBs & Elec Protection Systems | Multiple Connections | This relates to the Main Building on level(s) L00 - Ground Floor: During inspection it was found that a distribution board namely Office 2, there were 2 power supplies found connected on bus strips, one was from main circuit breaker and another one was from UPS. Both supplies must be distinguished with their respective distribution board. | Separate both supplies in two distribution board with correct identification and indication of which supply is being operative. Also consult qualified engineer to access and recommend specific size distribution board for the application. | 3 months | Factory will consult with qualified engineer/electrician on DBs and separate supplies |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Cabling & Wiring | Cables support and protection | This relates to the Main Building on level(s) L00 - Ground Floor: Power and Data cables are running in the same PVC conduits, and need to be separated in relevant conduits. | Separate cables so that they have their own containment for each application throughout the facility. | 3 months | Cables will be separated in independent conduits |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | DBs & Elec Protection Systems | Openings | This relates to the Main Building on level(s) L00 - Ground Floor: Unsealed openings of distribution board having Sharp Edges which can damage insulation of the cables. Unsealed opening could provide a passage for dust and dirt. However, it also provides passage for rodents to enter which could lead to a potential hazard for short circuit for example in distribution board 1st and 2nd floor. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 3 months | Openings in electric panels will be sealed |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | DBs & Elec Protection Systems | Adequate accessibility | This relates to the Main Building on level(s) L00 - Ground Floor: Clearance to the electrical panel is currently less than the Pakistan Standard allows. | Hire an Electrical Engineer who can assess and plan the relocation of distribution board accordingly. Also, the distribution board needs to be IP-rated as it is installed in an external area. | 1 month | Relocation of DBs will be planned and implemented |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the Main Building on level(s) L02 - 2nd Floor: Blue cables in Finishing 2 distribution board have a few circuit which are supplied by the Incoming part of CB, this is leading the blue cable to be unprotected. | Cable dressing needs to be done along with removal of Idle cables (if any). | 3 months | Cable dressing will be done |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Cabling & Wiring | Fixture | This relates to the Main Building on level(s) L00 - Ground Floor: Socket block made from wood is inadequate and requires a proper selection, arrangement and mounting on the surface. | All electrical components must be protection against fire risk factors. Replace it with properly designed switchboard mounted on wall surface with no exposed wiring. | 3 months | Switchboard will be mounted on wall with appropriate wiring |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Emergency Lighting | Provided but non-functional | This relates to emergency lighting throughout all buildings. Many areas were observed where emergency lighting was insufficient, including (non-exhaustive); - Emergency lighting provided but did not function in test, e.g., on Levels 1, 2, and 3 stitching walkways. Several lights marked ‘emergency lights’ did not work on power failure. - Insufficient/no battery backup - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs - No emergency lighting in some rooms / areas, e.g., Ground Level near the construction works, cutting room, and along escape routes. | Regularly test the emergency lighting system on each floor | 2 months | Factory will complete initial test on system and correct defects to ensure full operation of current system. Will provide Accord with future testing schedule |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Emergency Lighting | Provided but insufficient | This relates to emergency lighting throughout all buildings. Many areas were observed where emergency lighting was insufficient, including (non-exhaustive); - Emergency lighting provided but did not function in test, e.g., on Level 1, 2, and L3 stitching walkways. Several lights marked ‘emergency lights’ did not work on power failure. - Insufficient/no battery backup - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs - No emergency lighting in some rooms / areas, e.g., Ground Level near the construction works, cutting room, and along escape routes. | Provide emergency lighting in accordance with Pakistan Building Code and NFPA 101. This includes an emergency lighting system that will: - be capable of continuous operation for a minimum duration of 1 h and 30 minutes - provide emergency lighting that automatically turns on within 1s of the failure of the normal lighting supply - provide additional emergency fixtures to supply adequate illumination along all the means of egress. | E27 + 4 months | Factory will appoint electrical consultant to review the entire system, and provide a design to ensure emergency lighting complies fully with Pakistan Accord Building Standard. Submit design to Accord for review before implementing the design |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the fire detection and alarm system not being consistent with acceptable standards. Some of the related issues include the following: - No or incomplete coverage of fire alarm devices in all/some areas, including the inspection area and office on Level 1 and the video call room on Mezzanine Level - Detectors not installed top of stairs - Detectors incorrectly installed which could cause delayed activation, i.e., installed too far from the ceilings, including below structural beams - Wiring with non-fire resisting cables. - Manual fire alarm box(es) not located near exit doorways - Sounders inaudible due to low volume or high ambient noise, e.g., northwest stair to female prayer area, Level 5 | Ensure effective operation of currently installed alarm and detection system in the building. | 3 months | Existing detection and alarm system will be made fully functional |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Factory will appoint a competent engineer to design the system to meet Accord Standard requirements and submit for review |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E40 + 1 months | Factory will submit evidence that L/C has been opened |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E41 + 4 months | Factory will advise Accord when all materials are on site |  |  |  | In Progress
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E42 + 4 months | Factory will submit full "as-built" documentation of the system to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 153 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E43 + 4 months | Factory will advise Pakistan Accord when FADS installation fully completed and ready for review. |  |  |  | In Progress
3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E45 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E44 + 3 months | T&C visit will be arranged |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
01-Dec-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Chottani Industries, Plot # 487/A S.I.T.E, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 01-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | no | no | no
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | There are numerous lockable mechanisms on doors/gates along egress routes and/or at exit discharge points throughout the facility. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | Locking devices will be removed from all doors leading to emergency exits |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | There are numerous lockable mechanisms on doors/gates along egress routes and/or at exit discharge points throughout the facility. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Factory will provide door mechanisms that can be easily opened from the inside where necessary |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Sliding exit doors observed where only swinging doors provide an acceptable level of risk on: - Mezzanine Level (offices) - Level 1 stair access from training area, - Ground Level exit discharge door - Door(s) to administrative/ office area where the population exceeds 10 persons | Replace sliding door(s) with side hung swinging door(s) which swing in the direction of egress travel | 3 months | Sliding doors will be replaced, or pocket doors built into existing sliding doors, with doors that swing in direction of egress travel |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Automatic door closers are not installed in several locations | Remove all materials holding doors open and install, or repair, automatic closing mechanisms, as needed. | 2 months | Closing mechanisms will be repaired/installed and obstructions removed |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Equipment and services (e.g., electrical equipment, ducts) not serving stair inside stair | Provide a fire rated separation between the stair and the conduit, duct, etc., or relocate services so that they no longer penetrate the exit enclosure. Close any gaps with listed products with the appropriate fire rating. Remove equipment and services not serving stairway from stairway or provide construction to separate equipment and service by construction having a fire resistance rating not less than that required for the exit enclosure. | 4 months | Factory will appoint a consultant to prepare drawings showing proposed fire separating construction to protect stairs and submit to Pakistan Accord for review prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors - Lift shafts which are not protected by fire and smoke resistant construction and open into protected escape stairs. - Penetrations into/through exit stair protective enclosure - Equipment and services (e.g., electrical equipment, ducts) not serving stair inside stair - Automatic door closers are not installed in several locations | Install headroom height safety mechanism and signage on underside of lintel where door height is less than 2.05 m on the escape route in the stairway. | 4 months | Safety mechanism and signage will be installed |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors - Lift shafts which are not protected by fire and smoke resistant construction and open into protected escape stairs. - Penetrations into/through exit stair protective enclosure - Equipment and services (e.g., electrical equipment, ducts) not serving stair inside stair - Automatic door closers are not installed in several locations | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. - All doors into stairs need to be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. Note that the final exit door from a stair to outside the building do not need to be fire rated. | F7 + 4 months | Factory will ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction by implementing proposal after review by Pakistan Accord. |  |  |  | Pending Verification
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed on the Mezzanine Level, where exit access is via a kitchen. | Exit access shall be arranged so that it is not necessary to pass through any hazardous areas and to avoid travel through intervening spaces as per Pakistan Accord Building Standard. | 3 months | Factory will make arrangements to provide access to the exit that meets the requirements of the Pakistan Accord Building Standard. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Escape stair condition | Headroom along means of escape being less than 2,050mm, observed in the northeast stair between Level 1 and Ground Level | Install headroom height safety mechanism and signage on underside of lintel where door height is less than 2.05 m on the escape route in the stairway. | 1 months | Safety mechanism and signage will be installed |  |  |  | Pending Verification
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm, observed in two locations, along the northeast stair between Level 1 and Ground Level, as well as from a storage area in the basement. | Propose design modifications to ensure a clear headroom at required locations on the escape route, alternative paths that comply with Pakistan Accord Building Standard and BCP 10.5 or other means of providing safe passageway and present to Pakistan Accord for review. | 4 months | Factory will appoint a consultant to prepare drawings showing proposed modifications and submit to Pakistan Accord for review prior to rectification works |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Headroom along means of escape being less than 2,050mm, observed in two locations, along the northeast stair between Level 1 and Ground Level, as well as from a storage area in the basement. | Implement proposals reviewed by Pakistan Accord to ensure safe passageway on exit access routes | F10 + 4 months | Factory will implement any changes required as per proposals submitted earlier to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit capacity | Insufficient egress capacity in the basement includes the canteen and prayer areas. The occupant load is estimated to be more than 500 occupants, which means 3 exits are required. However, only two exits are provided and they don't appear to be sufficient width and therefore without sufficient capacity. | Propose design modifications to provide sufficient exit capacity for the design population of the canteen and prayer areas as per Pakistan Accord Building Standard and submit to Pakistan Accord for review | 4 months | Factory will appoint a consultant to review exit arrangement and propose modifications as needed and submit to Pakistan Accord for review prior to rectification works |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit capacity | Insufficient egress capacity in the basement includes the canteen and prayer areas. The occupant load is estimated to be more than 500 occupants, which means 3 exits are required. However, only two exits are provided and they don't appear to be sufficient width and therefore without sufficient capacity. | Implement design modifications as per previously reviewed documentation to comply with exit requirements required by Pakistan Accord Building Standard | F12 + 4 months | Factory will implement plan as per proposals submitted earlier to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways between the exits and the public way are exposed to electrical panels, unprotected openings from the basement, and a compressor. | Propose means of protecting external escape routes from the effects of fire anywhere in the building and submit to Pakistan Accord for review. | 4 months | Factory will appoint a consultant to propose means of protecting external escape routes and submit to Pakistan Accord for review prior to rectification works |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways between the exits and the public way are exposed to electrical panels, unprotected openings from the basement, and a compressor. | Protect exit route at exterior of the building from unprotected openings to allow a safe, free and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standard. | F14 + 4 months | Factory will protect external escape routes as per proposal submitted earlier to Accord |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit discharge | Tripping and/or falling hazard at the doors at Ground Level exit discharge which is too steep | Provide stairs or ramps compliant with requirements of the Pakistan Building Code to traverse vertical changes in elevation on an emergency egress route between the building level and ground. | 4 months | Factory will address falling hazards |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Escape stair condition | Handrails not being provided or being defective on one or both sides of exit stairs. It was observed in all interior stairways in the building at various locations. | Provide handrails on both sides of the exit stair in accordance with Pakistan Accord Building Standard | 3 months | Handrails will be provided on stairs |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit signage | It was observed that there is insufficient exit signage throughout the facility, and a lack of illuminated exit signage in general. | Remove any misleading exit signage and/or floor markings and provide exit signage so access to exits are marked by approved readily visible signs along full length of the escape route | 1 months | Factory will remove any misleading signage |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit signage | It was observed that there is insufficient exit signage throughout the facility, and a lack of illuminated exit signage in general. | Provide exit signage so access to exits are marked by approved, readily visible signs from all areas of the floor and clearly visible at exits comply with BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | Factory will provide exit signage to comply with BCP 10.15.1, 10.15.2 and 10.15.3 |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Suppression | Sprinkler system | The Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor. - Building does not have an automatic sprinkler system and requires one because of the building height | (1) Submit design documentation for a sprinkler system along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24 | 4 months | Factory will submit design documentation for the sprinkler and standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment, if required for the SUPS. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Suppression | Sprinkler system | The Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F20 + 1 month | If any material needed to be imported Factory will submit documentation to Pakistan Accord showing that an L/C has been opened for import of the components |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Suppression | Sprinkler system | The Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS | F21 + 4 months | Once all necessary material has been inhoused for the SUPS Factory will submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Suppression | Sprinkler system | The Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F22 + 3 months | Factory will provide Pakistan Accord with full 'as-built' documentation once installation complete |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Suppression | Sprinkler system | The Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F23 + 3 months | Factory will advise Pakistan Accord when SUPS installation fully completed and fully functional. |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Suppression | Sprinkler system | The Pakistan Accord Building Standard requirement to provide an automatic sprinkler system where buildings are more than 50 feet in height, measured from level of fire department access to lowest occupiable floor | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F24 + 3 = 18 months | Factory will share full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Suppression | Standpipe system | Standpipe system for firefighting operations: - Building does not have a Class I standpipe system but requires one because the building is more than 50 feet in height measured from level of fire department access to lowest occupiable floor. | Submit design documentation and provide a Class I standpipe system as per NFPA 14 as part of the SUPS system | 18 months | Provide a Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Separation of shafts | Lift shafts, including lift machine rooms, which penetrate floor that are not protected by fire and smoke resistant construction from production floors. Options to address this issue include providing a fire-rated lift lobby around lift openings on each floor, provide opening protective assemblies for each lift opening into the stair with 2-hr fire-rated construction and 1.5-hr opening protective assemblies or other solution proposed by the factory and approved by Pakistan Accord. | Propose how cargo lift openings will be provided with fire rated floor separation by sealing penetrations or protection of the openings and submit to Pakistan Accord for review | 4 months | Facility will prepare drawings showing the proposed fire separation details of vertical shafts and submitted to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Rated Construction | Separation of shafts | Lift shafts, including lift machine rooms, which penetrate floor that are not protected by fire and smoke resistant construction from production floors: Options to address this issue include providing a fire-rated lift lobby around lift openings on each floor, provide opening protective assemblies for each lift opening into the stair with 2-hr fire-rated construction and 1.5-hr opening protective assemblies, or other solution proposed by the factory and approved by Pakistan Accord. | Provide fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure in accordance with documentation reviewed previously by Pakistan Accord | F27 + 4 months | Provide 2-hour fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Floor openings | Openings in floors where fire rated separations are required: The opening for the future stair connecting the Ground Level and Mezzanine Level provides a pathway for fire and smoke to travel between levels. | Maintain 2-hr fire rated floor separation by sealing penetrations or protection of the openings with a fire rated enclosure | 4 months | Facility will prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review prior to the rectification works. The drawings should cover: - Locations of floor openings - Proposed fire separation details (including fire rating of walls and doors) Factory will implement the previously reviewed plan |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies: There is a child care room below the northwest stair in the basement level, open to the canteen and prayer areas. | Propose design and layout showing how different occupancies can be rearranged and/or enclosed with fire rated construction and submit documentation to Pakistan Accord for review. | 4 months | Facility will prepare a plan and drawings showing showing the proposed separation details. These shall be submitted to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors) |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies: There is a child care room below the northwest stair in the basement level, open to the canteen and prayer areas. | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies. | F30 + 4 months | Facility will provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Rated Construction | Storage | Separate storage by fire and smoke resisting construction and opening protective assemblies, where it cannot be considered as miscellaneous (in-process) storage in non-storage occupancies. In-process storage complies with the following: - Miscellaneous (in process) storage areas does not exceed 10 percent of the floor area (accessory to the other occupancy type) - Storage areas exceed or 93m2 (sprinklered buildings) in one area - Individual storage areas separated from other storage areas by at least 3m (10ft) Different occupancies that may not be accessory to each other and are not separated by fire and smoke resisting construction were observed on Levels 1, 2, 4, and 5 (storage and production area). | Manage storage in non-storage occupancies so that each pile is less than 3.05 m (12ft) in height and less than 93m2 in any one area (sprinklered buildings), and each pile is separated by a minimum of 3.0 m (10 ft) from other storage piles, and total area of temporary storage less than 10% floor area. | 1 month | Factory will provide a plan showing how in-process storage will be arranged to meet limitations for storage in non-storage areas |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Rated Construction | Storage | Separate storage by fire and smoke resisting construction and opening protective assemblies, where it cannot be considered as miscellaneous (in-process) storage in non-storage occupancies. | Where not possible to meet requirements for in-process storage, propose design and layout showing how different storage can be separated from other occupancies can be enclosed with fire rated construction and submit documentation to Pakistan Accord for review. | 4 months | Factory will provide drawings with proposal for fire rated separations between storage and other occupancies in accordance with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Rated Construction | Storage | Separate storage by fire and smoke resisting construction and opening protective assemblies, where it cannot be considered as miscellaneous (in-process) storage in non-storage occupancies. | Separate storage areas that do not comply with in-process storage limits by 2-hr fire-rated construction with 1.5-hr opening protective assemblies. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | F33 + 4 months | Factory will implement the plan for separation of storage areas on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Compressor room not separated by fire and smoke resisting construction on Level 5 | Separate electrical room by 2-hr fire rated construction. | 4 months | Facility will prepare drawings showing the proposed fire separation details of high fire hazard areas. These shall be submitted to Accord for review prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F36 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Steam generator room not separated by fire and smoke construction on Level 1 | Separate room with boiler(s) and/or steam generator(s) by 2-hr fire rated construction. | 4 months | Facility will provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F37 | Hazardous Materials | Chemicals storage | Storage, handling, and use of flammable and combustible liquids and/or solids - Bulk storage of flammable and combustible liquids and/or solids on ground level | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements and propose measures to meet these requirements to Pakistan Accord for review. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. | 4 months | Factory will provide the MSDS for all Chemicals stored and classify materials according to the NFPA requirement. Facility will share documentation with Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Hazardous Materials | Chemicals storage | Storage, handling, and use of flammable and combustible liquids and/or solids - Bulk storage of flammable and combustible liquids and/or solids on ground level | Implement measures for labelling and storage of chemicals used in the factory. | F37 + 4 months | Facility will provide measures for labelling and storage of chemicals |  |  |  | Pending Verification
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Hazardous Materials | Gas storage | Presence of a gas cylinder on the south side of the buildings | Ensure fire separation of the gas cylinder from the effects of a fire anywhere inside the building and ensure that the cylinder is not within 3.05m of any part of the escape route or separate with 2-hr fire rated construction. | 3 months | Factory will provide necessary fire separation of gas cylinders |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
01-Dec-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Chottani Industries, Plot # 487/A S.I.T.E, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 01-Dec-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal and edge columns at the Ground floor level appear to be overstressed for the applied load. | Building Structural Engineer to review design, loads and columns stresses in area as identified in the report. Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the identified columns. Submit data for concrete strength to Pakistan Acord for review. | 6 months | Factory will appoint a recognised laboratory to carry out core tests on the building and submit result to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | Based on an initial assessment, internal and edge columns at the Ground floor level appear to be overstressed for the applied load. | Review and update as necessary the safe loading plans for all floor plates within the factory giving consideration to floor capacity and column capacity. | 6 months | Factory will appoint a structural engineer to assess the capacity structure and produce safe loading plans for each floor of the building. |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Beams | Consistent and repeated beam cracking on RC beams at multiple locations of 3rd floor level. Cracking also observed in RC beam at 1st Floor level. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, in such cases, Building Engineer to investigate cause of cracking and identify appropriate remediation. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | Factory will appoint a structural engineer to assess the cause of cracking and submit proposal for remediation works to Accord for review. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Beams | Consistent and repeated beam cracking on RC beams at multiple locations of 3rd floor level. Cracking also observed in RC beam at 1st Floor level. | Carry out remediation works if necessary as per reviewed remedial proposal or repair cracks if shown to be within the plaster only. | S3 + 4 months | Factory will carry out remediation works if needed |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Loading | Uncontrolled loading | No indication of design loading capacity by means of safe load plans anywhere in factory. Uncontrolled loading was observed in various locations: - Fabric storage at 5th floor level appears to be excessive. - Uncontrolled storage at 2nd floor level. | Building Engineer to consider temporary reduction/removal of storage until an assessment on the load capacity of the as-constructed suspended slab is completed. Building Engineer to ensure the structure is not loaded beyond capacity. | 2 months | Factory will appoint a structural engineer to assess the capacity structure and produce safe loading plans, and load on floor will be adjusted to suit |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural Design | Lack of safe load plans | No indication of design loading capacity by means of safe load plans anywhere in factory. | Building Engineer to produce loading plans for all floors within the factory giving consideration to floor capacity and column capacity. Loading plans are to be posted on the walls of each floor level. Loading to be actively managed by Factory Management. | 6 months | Factory will appoint a building engineer to produce loading plans for all floors within the factory |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural Design | Drawings differ from as-built | Discrepancies were observed between the structural drawings and the as-built condition on site. Structural as-built drawings are to be prepared that reflect the actual structure. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months |  |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixture
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan | Fixture
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1