## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
09-Sep-24
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | Al-Ameera Apparel (Pvt) Ltd. - Plot No 27, Sector 23, Korangi Industrial Area, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 09-Sep-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | Yes/No | Yes/No | Yes/No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were available but not up-to-date also there were missing necessary details such as circuit identification, cable/breaker sizes, protective devices, voltage levels, standard legends and distribution board tags. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 3 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | During the survey, it was noted that the factory lacked electrical layout drawings for all units including small power layouts, lighting layouts, and containment layouts. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | During the survey, it was observed that: - Circuit breakers were mounted inappropriately on wooden planks near washing and below chemical storage covered with polythene sheets. - Circuit breakers were mounted in mesh of wires in generator room with some temporary fixing cable ties. | Remove polythene sheets from circuit breaker mounted on wooden plants. Remove wooden plank mounted circuit breaker, cover all circuit breakers that are openly installed throughout the facility with concealed metallic boxes to ensure safety and compliance with standards. | 1 month | The circuit breaker was fixed for temporary working near washing area. This will be removed after the job is done. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E5 | DBs & Elec Protection Systems | Circuit breakers | During the survey ,it was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes at main LT Room. - 1250A breaker terminated 2 x 240 sq.mm. cables in LT Room. - 1600A breaker terminated on 2 x 240 on main LT ACB. | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable ampacity after applying derating factors. | 3 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | During the inspection, we identified numerous hot spots within panels and distribution boards at different locations such as the RCC Building, distribution board of the washing area, PFI panel contractor, and genset changeover in the HT Room. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 1 month | We have will plan to change electrical changeover, and will take a different quotation from Market. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | E7 | DBs & Elec Protection Systems | Hot Spots | During the inspection It was also found that the Thermographic report was not available at the site | A Thermographic Testing report shall be prepared periodically. | 6 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | During the inspection, it was noted that: - The earth pits were inaccessible and unsuitably located behind the vessels near the and chemical store. | Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 6 months | The company have install the earth pit KE checked and approved. However this will be discussed in the Post Inspection CAP Meeting and will take guidelines for installation as per the standard). |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | [10 empty] | E9 | DBs & Elec Protection Systems | Earthing system | During the inspection it was noted that: - The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections such as in RO Plant, Powerhouse Changeovers and dyeing distribution boards. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 6 months | The company have install the earth pit KE checked and approved. However this will be discussed in the Post Inspection CAP Meeting and will take guidelines for installation as per the standard). |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | During the inspection it was noted that: - Equipotential bonding for the cable trays, machines body and metallic panel covers was missing such as in washing area. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | 3 months | Work in progress. |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | During the inspection it was also found that the Earth testing and Earth distribution layout drawings were not available. | Develop the earth distribution layout drawing and testing record and submit them to the Pakistan Accord. | 6 months | Testing report will be submitted to Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was noted that: - In a number of external areas, it was observed that electrical components were not suitable for the environmental conditions in which they were installed near washrooms and workshop. - Several electrical panels exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements such as at pump area near dyeing process. | Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | Job will done within two months. |  |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was noted that: - There were loose wiring, cables had joints, improper bus-bar arrangement, cables touching with bus-bars and panel body inside the distribution boards. Loose wiring and cable joints create high resistance points, leading to excessive heat generation which can cause the insulation to melt and potentially lead to fire such as in the pump panel behind vessels near the dyeing area. | Install wire ducts to organize and route wires neatly, remove loose cables, remove inside panel cable joints, and ensure that no cables are attached to the bus bars. | 3 months | The work was done on 17/05/2025. |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Panel/cabling/busbar | During the inspection it was noted that: - It was found that in many distribution boards lack dedicated neutral connection for outgoing power circuits. Without dedicated neutral wires, multiple circuits may share a single neutral, leading to an accumulation of return current. This can cause the neutral wire to carry more current than it is rated for, potentially leading to overheating and even fires such as in Powerhouse Changeover Room. | Conduct a thorough inspection of the existing wiring to identify circuits sharing a neutral wire. Provide dedicated neutral wires for each circuit, ensuring that each circuit's return path is properly isolated. | 6 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | [10 empty] | E15 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed in a number of electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker such as RO Plant, washing area distribution bards, grey area and knitting power panels. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 3 months | Multiple connections are in the washing area - no need to work on it. |  |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Openings | During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements such as in LT Room, Quality Department and RCC Building cutting machine distribution board. | Corrective actions are required to seal all openings and replace missing panels covers to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). Install cable glands or bushings to provide strain relief and protect cables at entry points in distribution boards. | 3 months | We will arrange. |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | [10 empty] | E17 | DBs & Elec Protection Systems | Adequate accessibility | During the visit, the electrical panels and distribution boards were examined for adequate accessibility. At numerous locations, it was found that the electrical panels do not possess the required space for inspection or easy access to the panels and their components such as in Transformer Room, UPS panel between 1st and 2nd floor RCC Building, HT Room and Washing & Dryer area. | Electrical equipment shall be arranged to provide sufficient space for the initial installation and later replacement of individual items of electrical equipment. Sufficient allowance shall also be made for sufficient space for the initial installation and later replacement of individual items of electrical equipment in accordance with Section 132.12 of BS7671 18th Edition + A2 (2022). | 1 month | will discussed in Post Inspection CAP Meeting |  |  |  | In Progress
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Lint & dust inside panel board | During the inspection, the cleanliness of electrical panels, distribution boards and electrical containment was assessed. The inspection revealed a significant accumulation of lint and dust in most of the distribution boards, panels and trunking systems such as both 1st and 2nd floor stitching area, dyeing and quality department. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). | 1 month | We prepare a schedule and given time line to electrician for cleaning the board. On going process. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 | [12 empty] | E19 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | The following observations were identified with the current lightning protection system: - A surge arrestor system was provided at roof but there was no LPS installed. However, there was no study / risk assessment available to confirm its adequacy. - No test results were provided for the existing lightning protection system, making it difficult to verify its effectiveness and compliance with relevant standards. - It was observed that there were no Surge protection devices (SPD) installed in any distribution boards. If a surge occurs without the device, it can be the cause of an accident or any equipment damage. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). | 6 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection it was noticed that the fire alarm system was non-listed, non-addressable, having inadequate detection coverage issues, non-fire rated cable, faulty sounders, MCP and detectors The following observations were identified with the FADS: - The cabling used to complete the installation of the FADS is not fire rated evident at dyeing process area. - There is insufficient back-up power supply to the FADs verified at main Admin Office. - Fire alarm interfaces are not provided for the FADS to control the building's gas supply, HVAC system (including dampers), elevators, and electronic access control equipment. The following observations were made regarding the detectors within the facility's Fire Alarm and Detection System (FADS): - Inadequate detection coverage was provided in several areas such as Transformer Room, HT Room and Pump Room basement. - Detection devices were not listed throughout the facility. A non-functional/incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. | This related to Building 01: (1) Submit design documentation for new replacement FADS system in all buildings to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | The company has installed a Fire Alarm & Detection system and its functioning properly. (All the fire related observations will discussed in Post Inspection CAP Meeting (E21 to E38). |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E20 + 1 month |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E21 + 4 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E22 + 5 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E23 + 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E24 + 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection it was noticed that the fire alarm system was non-listed, non-addressable, having inadequate detection coverage issues, non-fire rated cable, faulty sounders, MCP and detectors The following observations were identified with the FADS: - The cabling used to complete the installation of the FADS is not fire rated evident at the dyeing process area. - There is insufficient back-up power supply to the FADs verified at main Admin Office. - Fire alarm interfaces are not provided for the FADS to control the building's gas supply, HVAC system (including dampers), elevators, and electronic access control equipment. The following observations were made regarding the detectors within the facility's Fire Alarm and Detection System (FADS): - Inadequate detection coverage was provided in several areas such as Transformer Room, HT Room and Pump Room basement. - Detection devices were not listed throughout the facility. A non-functional/incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. | This related to building 02: (1) Submit design documentation for new replacement FADS system in all buildings to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E26 + 1 month |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E27 + 4 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E28 + 5 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E29 + 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E30 + 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | During the inspection it was noticed that the fire alarm system was non-listed, non-addressable, having inadequate detection coverage issues, non-fire rated cable, faulty sounders, MCP and detectors The following observations were identified with the FADS: - The cabling used to complete the installation of the FADS is not fire rated evident at dyeing process area. - There is insufficient back-up power supply to the FADs verified at main Admin Office. - Fire alarm interfaces are not provided for the FADS to control the building's gas supply, HVAC system (including dampers), elevators, and electronic access control equipment. The following observations were made regarding the detectors within the facility's Fire Alarm and Detection System (FADS): - Inadequate detection coverage was provided in several areas such as Transformer Room, HT Room and Pump Room basement. - Detection devices were not listed throughout the facility. A non-functional/incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. | This related to Building 03: (1) Submit design documentation for new replacement FADS system in all buildings to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (2) Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | E32 + 1 month |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (3) Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E33 + 4 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (4) Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E34 + 5 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (5) Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E35 + 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Non compliant FADS system was installed throughout the facility. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E36 + 3 months |  |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E38 | Fire Alarm & Detection System (FADS) | Maintenance records | The following observations were made with regards to testing and maintenance: - Routine testing of the Fire Alarm and Detection System (FADS)was observed. However, the said recommendations were neither addressed nor implement as observed during FADS testing. - The testing and maintenance of the Fire Alarm and Detection System (FADS) have not been conducted in accordance with the requirements specified in Chapter 14 of NFPA 72. | Conduct regular testing of the Fire Alarm and Detection System (FADS) to verify proper operation under both mains and backup power supply conditions. Ensure any faults indicated on the FADS control panel are promptly diagnosed and rectified. Maintain accurate records of all routine test results to ensure ongoing compliance and system reliability in accordance with Chapter 14 of NFPA 72. | 3 months |  |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Emergency Lighting | Provided but insufficient | During the inspection It was discovered that several areas had no emergency lighting such as: - Several areas possess non-compliant emergency lights and lack sufficient emergency lighting coverage. - Emergency light at 1st Floor RCC Building connecting knitting shed area. - UPS based non-compliant emergency light in Stores at 2nd Floor in RCC Building | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional listed emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 3 months | will conduct a complete survey and do accordingly where necessary. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Emergency Lighting | Provided but insufficient | During the inspection It was discovered that - Multiple emergency luminaires indicate the need for maintenance such as in dyeing area. - In some areas installed emergency lights are too dim to provide adequate illumination such as in power house. | Perform maintenance on all emergency luminaires indicating issues, including cleaning, bulb replacement, and verification of electrical connections. Replace dim emergency lights with higher intensity luminaires that meet the minimum illumination levels specified in the Building Code of Pakistan Fire Safety Provisions 2016. Ensure that all emergency lights provide adequate brightness to facilitate safe evacuation during emergencies. | 6 months | A complete survey will be held and install the emergency lights where necessary |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Emergency Lighting | General Lighting | During the inspection the following observations were noted: - Several locations were identified as lacking sufficient general lighting including building external areas, stairs, walkways and storage area at RCC Building. - At many locations found the general lights' fixtures were rusted and broken hanged with ropes. Fixtures hung with ropes are unstable and may fall, causing injury to personnel or damage to equipment. Rusted and broken fixtures can lead to exposed wiring, increasing the risk of electrical shocks and short circuits such as in generator area and generator control room. | Conduct a thorough assessment of lighting throughout the facility to find areas with insufficient illumination. Install additional lighting fixtures in these spots to ensure adequate brightness. Ensure the new lighting design meets safety and efficiency guidelines to provide clear visibility for all tasks and emergency situations. The factory needs to check regularly the lights and repair or replace the broken and faulty lights. Remove the lights fixed with ropes and properly fix them with a fastener. | 3 months | The company will arrange the complete assessment and do accordingly where necessary and monitor on regular basis. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Generator, Transformer & Sub-Station Room | Working clearance | During the inspection, it was observed that the working clearance was inadequate in generator, transformer and LT Room. Equipment was placed too close to walls and other panels making it difficult for personnel to access for routine maintenance or emergency interventions. | Reorganize the equipment layout to ensure adequate clearance, remove obstructions in pathways, and implement clear floor markings and signage to designate working areas and pathways. Conduct regular workspace audits to maintain clearances, update maintenance protocols to include clearance checks, provide personnel training on maintaining clearances, and consider installing adjustable equipment to accommodate flexible positioning. | 3 months | will discussed in Post Inspection CAP Meeting |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Cabling & Wiring | Cables support and protection | During the inspection the following observations were noted: - Proper supports were not provided for cables, they were laid directly on the ground such as cables in generator room and knitting panel. - were identified, which can generate sparks and potentially cause a fire. It is essential to avoid loose connections such as hanging wires at main gate. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations). Tighten and secure all loose connections immediately to eliminate the risk of sparks and potential fires. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 526.1 for ensuring secure connections). | 3 months | Will done accordingly |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Cabling & Wiring | Cables support and protection | During the inspection the following observations were noted: - It was found that at many locations, the insulation of cables was damaged. Damaged insulation can expose live conductors, posing a risk of electrical shock to anyone who comes into contact with the cables such as RCC Building 1st floor. - It was also found that the Cable Insulation Test Report was available in the facility. Without proper cable insulation testing, we can't ensure the safety of electrical installations. This raises the risk of fires, equipment failures, and harm to people. | Develop insulation testing report and upgrade insulation or replace damaged cables to prevent electrical hazards. | 6 months | A team will be form for survey of whole company, done accordingly where observation noted. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E45 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, it was observed that the cleanliness of the cable trunking system had not been maintained. Numerous trunking systems were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk such as in stitching 1st floor, 2nd floor, LT Room and Power house trenches. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 2 months | The company will arrange a team from maintenance department to do on regular basis and maintenance in charge will verified it. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E46 | Cabling & Wiring | Splicing of cables | During the inspection it was observed that cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections such as in production area 2nd floor and RO Plant. | Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). | 4 months | Lugs installed 12/05/2025. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E47 | Cabling & Wiring | Splicing of cables | During the inspection it was observed that PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together such as cutting and maintenance workshop. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | Maintenance and Admin team will be survey the whole premises and to find out the observation and solve it. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E48 | Cabling & Wiring | Colour coding | During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified at RCC 2nd Floor main power panel at blue phase and basement area. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 2 months | Survey has been carried out of panels, job was done in identified power panels. Done on 16/05/2025. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E49 | Cabling & Wiring | Fixtures | During the inspection Loose power receptacles hung with moving steel wire: This poses a significant risk of equipment damage or electrical incidents due to the instability of the receptacles. Loose connections can lead to electrical arcing, which increases the risk of fire and can cause serious injury or equipment failure such as in storage area at RCC Building. | Secure the loose power receptacles with appropriate fixed supports to prevent movement and ensure stable connections. Implement a regular inspection and maintenance schedule to check and secure all power receptacles, ensuring they remain safely and correctly installed. | 3 months | We will prepare the schedule of maintenance and checking. Maintenance & compliance department will monitor on this on a regular basis. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E50 | Cabling & Wiring | Fixtures | During the inspection Power receptacles installed in inappropriate locations: Receptacles placed in unsuitable locations, such as non-IP rated sockets installed outdoors or exposed to the elements, are at higher risk of moisture ingress and corrosion. This can lead to electrical short circuits or fires, posing a severe safety hazard such as in Power house control room. | Relocate power receptacles from inappropriate locations to more suitable, protected areas to prevent exposure to environmental elements. For external receptacles utilize suitably rated IP fixtures. Develop installation guidelines and training for personnel to ensure future power receptacles are installed in compliant and safe locations. | 3 months | The company fixed the receptacles in different places to eliminate the loose wiring which is used for outdoor jobs such as welding. This will be discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E51 | Cabling & Wiring | Fixtures | During the inspection it was noted that power receptacles were mounted on combustible wooden ply: installing receptacles on combustible materials like wooden ply increases the risk of fire if a short circuit or overheating occurs. Combustible materials can easily ignite, leading to potential fire hazards and endangering life safety in RCC cutting wooden boards. | Replace combustible wooden ply backings with non-combustible materials to reduce fire risk. Establish a facility-wide standard to use only non-combustible materials for mounting electrical components, and conduct regular audits for compliance. | 3 months | The company has fixed the wooden box and industrial plug is used. Will change the location of the power receptacles. |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
09-Sep-24
Corrective Action Plan - Fire
[9 empty] | Factory Name & Address | [12 empty] | Al-Ameera Apparel (Pvt) Ltd. - Plot No 27, Sector 23, Korangi Industrial Area, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 09-Sep-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | Yes/No | Yes/No | Yes/No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Escape doors are lockable: - Building #1– roof. - Locked exit door@plot#133. - Building #1- stair S-1. All floor levels with lockable gates: - 2nd floor -lockable door installed on exit. - Building#1- 2nd floor – Stitching Department – locked emergency exit gate. - Escape doors are sliding Building #1– 2nd floor -Sliding door installed on exit. - Building #1- 2nd floor – concertina door installed on exit. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | Company will closed all doors only at off time and open them at start time. However, this will discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Escape doors are lockable: - Building #1– roof. - Locked exit door@plot#133. - Building #1- stair S-1. All floor levels with lockable gates: - 2nd floor -lockable door installed on exit. - Building#1- 2nd floor – Stitching Department – locked emergency exit gate. - Escape doors are sliding Building #1– 2nd floor -Sliding door installed on exit. - Building #1- 2nd floor – concertina door installed on exit. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Pakistan Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, which are side swinging and open in the direction of travel to an exit. | 3 months | The internal doors are locked only when the is company closed. At the opening factory all gates are opened to avoid any mishaps. (however will discussed in Post Inspection CAP Meeting) |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Escape doors are lockable: - Building #1– roof. - Locked exit door@plot#133. - Building #1- stair S-1. All floor levels with lockable gates: - 2nd floor -lockable door installed on exit. - Building #1- 2nd floor – Stitching Department – locked emergency exit gate. - Escape doors are sliding Building #1– 2nd floor -sliding door installed on exit. - Building #1- 2nd floor – concertina door installed on exit. | Monitor escape doors to ensure there are no locking devices installed that prevent easy access to emergency exits. | F2+3 months | The internal doors are locked only when company closed. At opening, factory gates are opened to avoid any mishaps. -Sliding doors are open in working time. (However will discussed in the Post Inspection CAP Meeting) |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F4 | Means of Escape | Protection of stairs | -Unprotected openings into stairs – Building #1- stair S-1 – All floor levels – unprotected door openings. -Door self-closers are missing – Building #1 – All floor levels. -Fire doors propped open – Building #1 -All floor levels. -Doors are not fire doors – Building #1 – All emergency exit doors. -Building #1- 3rd floor & all floor levels – Lift shafts are not fire separated from production and stairs. -Fire load under stairs - Building #1 – 1st floor - stair S-3, boiler and combustible fire load under stairs. | Remove fire load from stairs. | 2 weeks | This will be discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F5 | Means of Escape | Protection of stairs | -Unprotected openings into stairs – Building #1- stair S-1 – All floor levels – Unprotected door openings. -Door self-closers are missing – Building #1 – All floor levels. -Fire doors propped open – Building #1 -All floor levels. -Doors are not fire doors – Building #1 – All emergency exit doors. -Building #1- 3rd floor & all floor levels – Lift shafts are not fire separated from production and stairs. -Fire load under stairs - Building #1 – 1st floor - stair S-3, boiler and combustible fire load under stairs. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: -Layout showing the location of fire rated walls/doors to protect the stairs. -Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). -Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | All the combustible fire load will be removed and other items will discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F6 | Means of Escape | Protection of stairs | -Unprotected openings into stairs – Building #1- stair S-1 – All floor levels – Unprotected door openings. -Door self-closers are missing – Building #1 – All floor levels. -Fire doors propped open – Building #1 -All floor levels. -Doors are not fire doors – Building #1 – All emergency exit doors. -Building #1- 3rd floor & all floor levels – Lift shafts are not fire separated from production and stairs. -Fire load under stairs - Building #1 – 1st floor - stair S-3, boiler and combustible fire load under stairs. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not always locked). | F5+4 months | All the combustible fire load will be removed and other items will discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F7 | Means of Escape | Exit access | - Exit access is not fire protected - Building #1-stair S-1, all floor levels exit route is not fire protected. - Building #1 – Exit access (ACC#2&3) - Combustible material stored under exit access, Building #1- 1st floor & all floor levels exit access corridor is not fire protected from production and storage area. -Exit access route is not fire protected - Building #1- stair S-2 – 3rd floor exit access route, Building #1-stair S-1. -All floor levels exit discharge route is not fire protected. -Obstructions & tripping hazard and open manhole – Building #1 -3rd floor – Exit steps with 0.363m height. | Remove obstructions on escape routes and keep them clear for escape. | 2 weeks | We will remove all the obstruction on pathways and will monitor regularly. |  |  |  | In Progress
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F8 | Means of Escape | Exit access | - Exit access is not fire protected - Building #1-stair S-1, all floor levels exit route is not fire protected. - Building #1 – Exit access (ACC#2&3) - Combustible material stored under exit access, Building #1- 1st floor & all floor levels exit access corridor is not fire protected from production and storage area. -Exit access route is not fire protected - Building #1- stair S-2 – 3rd floor exit access route, Building #1-stair S-1. -All floor levels exit discharge route is not fire protected. -Obstructions & tripping hazard and open manhole – Building #1 -3rd floor – Exit steps with 0.363m height. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge routes. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: -Layout showing the location of fire rated walls/doors to protect stair discharge routes. -Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | This will be discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F9 | Means of Escape | Exit access | - Exit access is not fire protected - Building #1-stair S-1, all floor levels exit route is not fire protected. - Building #1 – Exit access (ACC#2&3) - Combustible material stored under exit access, Building #1- 1st floor & all floor levels exit access corridor is not fire protected from production and storage area. -Exit access route is not fire protected - Building #1- stair S-2 – 3rd floor exit access route, Building #1-stair S-1. -All floor levels exit discharge route is not fire protected. -Obstructions & tripping hazard and open manhole – Building #1 -3rd floor – Exit steps with 0.363m height. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Pakistan Accord Building Standard. Some of the key requirements include: -All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). - Penetrations through doors are not permitted. - All fire doors require self-closers. - Doors into exit discharge routes should be kept closed (but not always locked). - All penetrations through walls into stair discharge routes need to be fire stopped. - Unprotected openings (e.g. holes or window/ louver openings) are not permitted. - Ensure external escape routes are relocated so that they do not pass via high-risk areas. | F8+4 months | This will discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F10 | Means of Escape | Escape stair condition | There are no handrails- Building #1-stair S-1– 3rd floor. Emergency exit stairs without handrails, Building #1-stair S-2. All floor levels emergency stairs are without handrails. | Provide handrails as per Pakistan Building Code Standard clause 10.18.10. | 3 months | Handrails have been fixed. Done on 20/01/2025. | Done on 20/01/2025 |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | F11 | Means of Escape | Escape stair condition | There are no handrails- Building #1-stair S-1– 3rd floor. Emergency exit stairs without handrails, Building #1-stair S-2. All floor levels emergency stairs are without handrails. | Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. | F10+ 3 months | Handrails have been fixed. Done on 24/01/2025. | Done on 24/01/2025 |  |  | In Progress
[9 empty] | Initial | [10 empty] | F12 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated - Building #1- stair S-1 , -Exit discharge route is not fire separated – Building #1- Final exit discharge route is not fire separated. Stair discharge route is not fire separated from the building – Building #1-stair S-2 / stair S-1– All floor levels & ground floor. Final exit from building is not adequately away to ensure occupant safety – Main assembly point and all main exits of all buildings. | Remove fire load from exit discharge route. | 2 weeks | 2nd floor, 3rd floor and 1st floor escape from packing area to ground floor assembly point will discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F13 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated - Building #1- stair S-1 , -Exit discharge route is not fire separated – Building #1- Final exit discharge route is not fire separated. Stair discharge route is not fire separated from the building – Building #1-stair S-2 / stair S-1– All floor levels & ground floor. Final exit from building is not adequately away to ensure occupant safety – Main assembly point and all main exits of all buildings. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Pakistan Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes Provide additional exits from site. | 4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F14 | Means of Escape | Exit discharge | Exit discharge routes are not fire separated - Building #1- stair S-1 , -Exit discharge route is not fire separated – Building #1- Final exit discharge route is not fire separated. Stair discharge route is not fire separated from the building – Building #1-stair S-2 / stair S-1– All floor levels & ground floor. Final exit from building is not adequately away to ensure occupant safety – Main assembly point and all main exits of all buildings. | Ensure exit discharge routes are adequately fire separated from the rest of the building.. | F 13 + 4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F15 | Means of Escape | Exit signage | Missing exit signs at stair discharge routes – Building #1 – S-2 & S-1 stairs. Missing exit signs in production areas – Building #1 -3rd floor production area. Missing exit signs in offices and back of house areas – Building #1- ground floor. Missing exit signs at roof – Building #1. Electrically powered exit signs are not a tested and listed system – Building #1. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | We will conduct the complete survey of the company, fixed signs where necessary, and monitor this regularly. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F16 | Means of Escape | Exit signage | Missing exit signs at stair discharge routes – Building #1 – S-2 & S-1 stairs. Missing exit signs in production areas – Building #1 -3rd floor production area. Missing exit signs in offices and back of house areas – Building #1- ground floor. Missing exit signs at roof – Building #1. Electrically powered exit signs are not a tested and listed system – Building #1. | Ensure that all exit signage is checked periodically and in good working condition. | F15 + 3 months | will conduct the complete survey of the company, fixed signs where necessary and monitor regularly |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F17 | Fire Rated Construction | Separation of occupancies | Car park areas are not fire separated from the rest of the building – Building #1 - ground floor. Canteen area not fire separated from the Gas Generator Room – Building #1- ground floor. Buildings not separated to prevent spread of fire – Building #1 – ACC#2 & ACC#3 not fire separated from each other, Building #1-basement storage area not fire separated from rest of building. Offices and storage areas are not fire separated - Building #1- mezzanine floor – Office and storage not fire separated . Openings from the production floors to the emergency corridors-Building #1 – All floor levels. Building #1-ACC#3 – 1st floor opening. | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: Different occupancy types in the building. Proposed fire separation details (including fire rating of walls and doors). | 4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | [10 empty] | F18 | Fire Rated Construction | Separation of occupancies | Car park areas are not fire separated from the rest of the building – Building #1 - ground floor. Canteen area not fire separated from the Gas Generator Room – Building #1- ground floor. Buildings not separated to prevent spread of fire – Building #1 – ACC#2 & ACC#3 not fire separated from each other, Building #1-basement storage area not fire separated from rest of building. Offices and storage areas are not fire separated - Building #1- mezzanine floor – Office and storage not fire separated . Openings from the production floors to the emergency corridors-Building #1 – All floor levels. Building #1-ACC#3 – 1st floor opening. | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F17 + 4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F19 | Fire Rated Construction | Storage | Building #1- 3rd floor - Production not fire separated from storage. Building #1- 3rd floor – excess storage in production area. Building #1-1st floor - storage not separated from production. Building #1- ground floor – excess storage in production. | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F20 | Fire Rated Construction | Storage | Building #1- 3rd floor - Production not fire separated from storage. Building #1- 3rd floor – excess storage in production area. Building #1-1st floor - storage not separated from production. Building #1- ground floor – excess storage in production. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F19+4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F21 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building (Main Fire pump)- Main fire pump installed at ground floor. Electrical rooms are not fire separated – Building #1- 2nd floor – Stitching area – High voltage electric panels are not fire separated. Generator Room is not fire separated (Building #1 -Diesel Generators not separated from high voltage panel room). Boiler not separated from production area and ETP plant -Building #1- ground floor. Building #1- 2nd floor- Gas steam generator not separated from production area / fire rated wall not installed. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: -Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.). -Locations of fire rated walls and doors to protect these rooms. -Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F22 | Fire Rated Construction | Separation of high-risk areas | Fire pump room is not fire separated from the rest of the building (Main Fire pump)- Main fire pump installed at ground floor. Electrical rooms are not fire separated – Building #1- 2nd floor – Stitching area – High voltage electric panels are not fire separated. Generator Room is not fire separated (Building #1 -Diesel Generators not separated from high voltage panel room). Boiler not separated from production area and ETP plant -Building #1- ground floor. Building #1- 2nd floor- Gas steam generator not separated from production area / fire rated wall not installed. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F21 + 4 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F23 | Hazardous Materials | Gas storage | Large amounts of gas in production areas- Building #1- ground floor – boiler area, Building #1- ground floor -Gas cylinder stored in generator area. | Prepare drawings showing gas storage areas. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of gas storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms. | 4 months | Fire fighting cylinders are kept in the Generator Room i.e. Co2 etc.---Gas cylinders are kept in boiler area for burnt the pilot of boiler burner. (However this will discussed in Post Inspection CAP Meeting) |  |  |  | In Progress
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | [10 empty] | F24 | Hazardous Materials | Gas storage | Large amounts of gas in production areas- Building #1- ground floor – Boiler area, Building #1- ground floor -gas cylinder stored in generator area. | Implement the above plan on site. All gas storage areas to be compliant with Pakistan Accord Building Standard. | F23 + 4 months | Fire fighting cylinders are kept in Generator Room i.e. Co2 etc.(However will discussed in Post Inspection CAP Meeting) |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | [10 empty] | F25 | Hazardous Materials | Chemicals storage | Large amounts of chemicals in production areas- Building #1- ACC 3 – 1st floor large amount of chemical without proper storage and safety . Building #1- ground floor – improperly stored chemicals. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. | 4 months | The company shall collect the MSDS of all the chemicals and post in the chemical storage area. Other -all the chemicals are store in separate designated area which is away from production area. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | [10 empty] | F26 | Hazardous Materials | Chemicals storage | Large amounts of chemicals in production areas- Building #1- ACC 3 – 1st floor Large amount of chemical without proper storage and safety. Building #1- ground floor – improperly stored chemicals. | Implement the above plan on site. All chemical storage areas to be compliant with the Pakistan Accord Building Standard. | F25 + 4 months | Chemical are kept outside dyeing area near the color kitchen. However, we will arrange as per standards. |  |  |  | In Progress
No | 3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | [10 empty] | F27 | Hazardous Materials | Diesel storage | Large amounts of diesel storage without bunding - Building #1 –ACC#3 ground floor – large quantity of diesel stored improperly in Generator Room- more than 1265 litres of diesel stored on site. | Prepare drawings showing diesel storage areas. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of diesel storage areas. - Locations of fire rated walls and doors to protect these rooms. - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). - Ventilation provisions to each of these rooms. - Bunding details. | 4 months | Right now do not have not sufficient space in the Generator Room, we will work on it and choose best possible way to close the CAP. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | [10 empty] | F28 | Hazardous Materials | Diesel storage | Large amounts of diesel storage without bunding - Building #1 – ACC#3 ground floor – large quantity of diesel stored improperly in Generator Room- more than 1265 litres of diesel stored on site. | Implement the above plan on site. All diesel storage areas to be compliant with the Pakistan Accord Building Standard. | F27+ 4 months | Right now do not have not sufficient space in the Generator Room, we will work on it and choose best possible way to close the CAP. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | [10 empty] | F29 | Fire Suppression | Standpipe system | Standpipe system connections is not provided on emergency exit stair - Building #1-stair S-6 - 2nd floor and all floor levels. | (1) Submit design documentation for standpipes system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24. | 4 months | Company has installed the fire hydrant system throughout the premises, however this will discussed in Post Inspection CAP Meeting for any improvement or suggestions. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | [10 empty] | F30 | Fire Suppression | Standpipe system | Standpipe system connections is not provided on emergency exit stair - Building #1-stair S-6 - 2nd floor and all floor levels. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F29 + 1 months | Company has installed the fire hydrant system throughout the premises, however this will discussed in Post Inspection CAP Meeting for any improvement or suggestions. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | [10 empty] | F31 | Fire Suppression | Standpipe system | Standpipe system connections is not provided on emergency exit stair - Building #1-stair S-6 - 2nd floor and all floor levels | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F30 +3 months | This will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | [10 empty] | F32 | Fire Suppression | Standpipe system | Standpipe system connections is not provided on emergency exit stair - Building #1-stair S-6 - 2nd floor and all floor levels | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F 31+ 3 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | F33 | Fire Suppression | Standpipe system | Standpipe system connections is not provided on emergency exit stair - Building #1-stair S-6 - 2nd floor and all floor levels | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | F 32 + 3 months | Will be discussed in the Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | [10 empty] | F34 | Fire Suppression | Standpipe system | Standpipe system connections is not provided on emergency exit stair - Building #1-stair S-6 - 2nd floor and all floor levels | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete. | F33 + 4 months = 18 months | Pakistan Accord may guide company for testing (will be discussed in Post Inspection CAP Meeting) |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | [10 empty] | F35 | Fire Suppression | Fire pumps | Fire pump set is not listed – Main fire pump Jockey pump is not listed Diesel backup pump is not listed | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and following steps (1) to (6) above. | 18 months | The company has installed NAFFCO hydrant pump.(However this will be discussed in Post Inspection CAP Meeting). |  |  |  | In Progress
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | [10 empty] | F36 | Fire Suppression | Water supply | No separate fire water tank No dedicated portion of shared water tank for fire safety purposes | Review arrangement of water supply and storage requirements to cover fire water supply as part of supporting infrastructure for the SUPS system, in accordance with NFPA 22 & 24, and submit to Pakistan Accord for review. | 4 months | A 30000 gallon water tank is designated for fire. |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | [10 empty] | F37 | Fire Suppression | Water supply | No separate fire water tank No dedicated portion of shared water tank for fire safety purposes | Provide fire water supply and storage that complies with Building Code of Pakistan and NFPA 22 & NFPA 24 as part of the supporting infrastructure to the SUPS system. | 18 months | A 30000 gallon water tank is designated for fire. |  |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F38 | Fire Safety Management | Fire drills | - No evidence of fire drills - Fire drill documentation is of poor standard. - Not all staff are involved in fire drills. - Not all staff know what to do in the event of fire. | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | Fire drill conducted twice a year---- All the factory employees have participated in the drill. The next drill will be conducted in July-2025. |  |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F39 | Fire Safety Management | Fire drills | - No evidence of fire drills - Fire drill documentation is of poor standard. - Not all staff are involved in fire drills. - Not all staff know what to do in the event of fire. | Ensure fire drills are performed a minimum of 2 times per year. | F38+2 months | Fire drill conducted twice a year---- All the factory employees have participated in the drill. The next drill will be conducted in July-2025. |  |  |  | In Progress
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F40 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Standpipe System. Inadequate records of maintenance of Fire Pumps. Inadequate records of maintenance of Fire Extinguishers. | Prepare maintenance schedule for all life safety systems. | 3 months | Will prepare the maintenance schedule of the safety equipment and monitor regularly. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F41 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Standpipe System. Inadequate records of maintenance of Fire Pumps. Inadequate records of maintenance of Fire Extinguishers. | Prepare a schedule of proposed system maintenance. - Identify how systems will be maintained and who is responsible. The schedule to be submitted to Pakistan Accord for review and approval. | 3 months | We will prepare the schedule and assign the responsibility. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F42 | Fire Safety Management | Records of systems maintenance | Inadequate records of maintenance of Standpipe System. Inadequate records of maintenance of Fire Pumps. Inadequate records of maintenance of Fire Extinguishers. | Ensure all systems are being maintained as per the schedule agreed with Pakistan Accord . Keep maintenance records. | F41 + 3 months | We will make proper record of the mentioned equipment. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F43 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps. Inadequate records of testing of Standpipe System. Inadequate records of testing of Fire Extinguishers. | Prepare testing schedule for all life safety systems. | 3 months | Will prepare the maintenance schedule of the safety equipment and monitor regularly. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F44 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps. Inadequate records of testing of Standpipe System. Inadequate records of testing of Fire Extinguishers. | Prepare a schedule of proposed system testing. Identify how systems will be tested and who is responsible. The schedule to be submitted to Pakistan Accord for review and approval. | 3 months | Will prepare the maintenance schedule of the safety equipment and monitor regularly. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F45 | Fire Safety Management | Records of system testing | Inadequate records of testing of Fire Pumps. Inadequate records of testing of Standpipe System. Inadequate records of testing of Fire Extinguishers. | Ensure all systems are being tested as per the schedule agreed with Pakistan Accord. - Keep testing records. | F 44 + 3 months | Will prepare the maintenance schedule of the safety equipment and monitor regularly. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F46 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | We will prepare the proper records and prepare Emergency Action Plan accordingly |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F47 | Fire Safety Management | Emergency Action Plan | There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F46+2 months | We will maintained the Emergency Action Plan. |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2024-09-09
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [12 empty] | Al-Ameera Apparel (Pvt) Ltd. - Plot No 27, Sector 23, Korangi Industrial Area, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 09-Sep-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | Yes/No | Yes/No | Yes/No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Cracking | Column | Based on an initial assessment, several ground-floor columns in the washing and dyeing area of Building 1 have significant cracks with exposed, corroded reinforcement at the ground-floor level in the wet process area. However, the columns in the basement show no signs of cracking. The potential cause of the cracking appears to be concrete degradation due to continuous moisture ingress, which has led to the corrosion of reinforcement. Additionally, the degraded concrete in these columns is further compromised by the impact of trolley movement. | Structural engineer to carry out a detailed assessment of the column to identify the cause of the cracking. Also to understand the condition of concrete and rebar and determine the residual load capacity and submit to Pakistan Accord for review. | 3 months | The ground floor columns has been strengthened with concrete & SS sheets. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Cracking | Column | Based on an initial assessment, several ground-floor columns in the washing and dyeing area of Building 1 have significant cracks with exposed, corroded reinforcement at the ground-floor level in the wet process area. However, the columns in the basement show no signs of cracking. The potential cause of the cracking appears to be concrete degradation due to continuous moisture ingress, which has led to the corrosion of reinforcement. Additionally, the degraded concrete in these columns is further compromised by the impact of trolley movement. | Propose measures to prevent future damage and works to repair the existing damage and submit to Pakistan Accord for review. | 3 months | The ground floor columns has been strengthened with concrete & SS sheets. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Column | Based on an initial assessment, several ground-floor columns in the washing and dyeing area of Building 1 have significant cracks with exposed, corroded reinforcement at the ground-floor level in the wet process area. However, the columns in the basement show no signs of cracking. The potential cause of the cracking appears to be concrete degradation due to continuous moisture ingress, which has led to the corrosion of reinforcement. Additionally, the degraded concrete in these columns is further compromised by the impact of trolley movement. | Carry out the remediation work. | S2+ 3 months | The ground floor columns will reinforced with cement and SS sheets. We will work on the basement columns which have were mentioned in the inspection report. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Column | Based on an initial assessment, several ground-floor columns in the washing and dyeing area of Building 1 have significant cracks with exposed, corroded reinforcement at the ground-floor level in the wet process area. However, the columns in the basement show no signs of cracking. The potential cause of the cracking appears to be concrete degradation due to continuous moisture ingress, which has led to the corrosion of reinforcement. Additionally, the degraded concrete in these columns is further compromised by the impact of trolley movement. | Monitor the building for future signs of water damage. | S3+ 3 months | The ground floor columns will reinforced with cement and SS sheets. We will work on the basement columns which have were mentioned in the inspection report. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Structural System | Lateral stability system | In RCC Building-1, ground floor consists of a flat slab with column capitals, while the upper floors are designed as a moment-resisting frame. This configuration creates uncertainty regarding the overall stability system of the building. | Building structural engineer to review the as-built design for code compliance (vertical and lateral loads) and confirm if the stability system is adequate. | 3 months | Company will contact an Architect to review the built design and confirm the stability of the building. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Structural System | Lateral stability system | In RCC Building-1, ground floor consists of a flat slab with column capitals, while the upper floors are designed as a moment-resisting frame. This configuration creates uncertainty regarding the overall stability system of the building. | Building engineer to carry out a stability analysis of the building and propose additional stability system if it is necessary and submit to Pakistan Accord for review. | 3 months | This will be discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | [10 empty] | S7 | Structural System | Lateral stability system | In RCC Building-1, ground floor consists of a flat slab with column capitals, while the upper floors are designed as a moment-resisting frame. This configuration creates uncertainty regarding the overall stability system of the building. | Propose strengthening works as required and submit to Pakistan Accord for review and approval. | S6+ 1 month | This will be discussed in Post Inspection CAP Meeting. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | [10 empty] | S8 | Structural System | Lateral stability system | In RCC Building-1, ground floor consists of a flat slab with column capitals, while the upper floors are designed as a moment-resisting frame. This configuration creates uncertainty regarding the overall stability system of the building. | Carry out the remediation work. | S8+ 4 months | Company will contact an Architect to review the built design and confirm the stability of the building. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | S9 | Structural Documentation | Documentation unavailable | This applies to all buildings on the premises. Details of drawings as below: • ACC-2: Architectural drawings are not available. • ACC-3: Architectural drawings and structural drawings are not available. • RCC Building 1: Structural drawings are not available. • RCC Building 2: Architectural drawings are not available. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | Approval for the building layout plan has been requested from KBCA since 21-Mar-2012; response from KBCA is still pending. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Structural Documentation | Lack of safe load plans | No safe load plans were post in the factory. | Building structural engineer to review design documentation to produce safe load plans according to the loading capacity of the structure. | 6 months | We will ill contact with architectural consultant for the same. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Structural Documentation | Lack of safe load plans | No safe load plans were post in the factory. | Factory to post safe load plans on each floor. | S10+1 month | We will ill contact with architectural consultant for the same. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S12 | Other Damage/Defects | Spalling concrete | In the Building 1, signs of concrete spalling have been observed on both the ground and first floors, leading to corrosion of the rebar and cracking of the concrete. This damage may be attributed to prolonged moisture ingress , which is negatively impacting the structure. | Building engineer to inspect the locations (in all the buildings) of spalling of concrete and possible reason of cracks and dampness and propose the remedial solution to repair the structure distress caused by ingress of water and submit to Pakistan Accord for Review. | 3 months | The building engineer will visit the whole premises to check all the repair work and advise us on repair. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S13 | Other Damage/Defects | Spalling concrete | In the Building 1, signs of concrete spalling have been observed on both the ground and first floors, leading to corrosion of the rebar and cracking of the concrete. This damage may be attributed to prolonged moisture ingress , which is negatively impacting the structure. | Provide suitable protection on floor for ingress of water to prevent damage to structure from potential ingress. | S12 +3 months | The building engineer will visit the whole premises to check all the repair work and advise us on repair. |  |  |  | In Progress
[10 empty] | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S14 | Other Damage/Defects | Spalling concrete | In the Building 1, signs of concrete spalling have been observed on both the ground and first floors, leading to corrosion of the rebar and cracking of the concrete. This damage may be attributed to prolonged moisture ingress , which is negatively impacting the structure. | Implement the remedial work. | S13+3 months | This will be done accordingly. |  |  |  | In Progress
[10 empty] | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S15 | Other Damage/Defects | Health and Safety | There is no edge protection provided on the rooftop of the extended portion of RCC-1, which poses a risk of potential injury due to slips, trips, or falls while accessing and maintaining services. | Provide adequate edge protection on the Building-1, and on any other part of other buildings with the same issue. | 1 month | The job was assigned to a fabricator who will complete in the specified time. |  |  |  | In Progress

## E Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Fixtures
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## F Categories
Categories | Means of Escape | Fire Rated Construction | Hazardous Materials | Fire Suppression | Fire Safety Management
Means of Escape | Protection of stairs | Structural fire rating | Chemicals handling | Standpipe system | Fire drills
Fire Rated Construction | Number of exits | Extensive voids | Chemicals storage | Fire extinguishers | Records of systems maintenance
Fire Suppression | Travel distance | Separation of high-risk areas | Diesel storage | Fire pumps | Records of system testing
Hazardous Materials | Exit capacity | Separation of shafts | Gas storage | Sprinkler system | Staff training
Fire Safety Management | Exit access | Separation of occupancies |  | Water supply | Emergency Action Plan
| Escape stair condition | Floor openings |  | Exterior hydrants | Fire vehicle access
| Exit discharge | Storage
| Escape doors | Atrium
Exit signage
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## S Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Leaking Pipes
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type