## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
26-Mar-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Interloop Denim Chak 65, Raiwind, Kasur, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-03-26
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | It was observed that the single-line diagrams attached to the distribution boards did not match the current state of the circuits. | Ensure that the single-line diagrams attached to each distribution board are updated accurately and match the circuits of their distribution boards. | 6 months | All the SLD's will be reviewed and updated according to the current state of circuits. Factory will appoint a qualified person to produce a SLD and submit to Accord for review. Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | We observed that the electrical layout drawings were missing some vital information. This needs to be rectified to eliminate any type of confusion and to have clear schematics of the electrical network. | Consult a Qualified Engineer to complete electrical layout drawings that depict the location and specifications of all electrical equipment and outlets to match the existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. There might be too much information to effectively display on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are visible and up to date with the current electrical installation. | 8 months | Factory will appoint a qualified person to produce an electrical layout drawing and submit to Accord for review. Accord will provide feedback on the layout and advise if further detail is needed. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Circuit breakers | It was observed that circuit breaker ratings were oversized compared to the cables connected. It is essential to address this issue to avoid any safety hazards and ensure the proper functioning of the electrical system. | Consult a qualified engineer who can assess the situation and provide specific recommendations tailored to your electrical system and needs. They can also ensure that any changes or upgrades are done safely and in compliance with electrical codes and standards. | 3 months | Our mentioned breakers are of adjustable type and also adjusted to protect cables as per ampacity mentioned in cable’s technical literature. Factory will share the technical literature of cables with Accord for review. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Hot Spots | Abnormal temperatures on circuit breakers and various other switching devices throughout the facility. If electrical busbars, breakers, cables, and switchboards are showing high temperatures, it's a cause for concern as it could indicate issues that can lead to electrical fires or equipment failure. Also, the thermography report that was provided at the day of inspection was not covering the electrical network of the entire facility. | If necessary, turn off the power to the affected circuits or the entire electrical panel. This will help prevent any further overheating and potential damage. | 1 month | All issues have been rectified. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Hot Spots | Abnormal temperatures on circuit breakers and various other switching devices throughout the facility. If electrical busbars, breakers, cables, and switchboards are showing high temperatures, it's a cause for concern as it could indicate issues that can lead to electrical fires or equipment failure. Also, the thermography report that was provided at the day of inspection was not covering the electrical network of the entire facility. | Check if the circuits are overloaded by running too many appliances or equipment simultaneously. If this is the case, redistribute the load or consider installing additional circuits to handle the electrical demand. Carry out a thermographic survey of the facility to ensure the thermographic report should cover the entire electrical network of the facility. | 1 month | Thermographic surveys will be conducted and submitted to Accord for review. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Hot Spots | Abnormal temperatures on circuit breakers and various other switching devices throughout the facility. If electrical busbars, breakers, cables, and switchboards are showing high temperatures, it's a cause for concern as it could indicate issues that can lead to electrical fires or equipment failure. Also, the thermography report that was provided at the day of inspection was not covering the electrical network of the entire facility. | Consult with a qualified engineer. They can perform a thorough inspection, identify the root cause of the overheating, and recommend appropriate solutions to ensure the safety and reliability of your electrical system. | 6 months | We will built in house capacity by the procurement of thermal imaging camera and quarterly inspections will be carried out afterwards. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | Earth strips in lightning distribution boards were inadequate in terms of size, several earth wires were lugged together as one, the bonding mechanism was not adopted in the main building B2, sewing and stitching machines and tables were not bonded. We also observed that bare copper wire was laid in an open environment before the chiller room. | Consult with a qualified engineer who can assess the facility's requirements and design an earthing system that meets safety standards and regulatory requirements. Refer to BS-7671. In the earth-test report, mention the method of testing and ensure that each pit is disconnected from its distribution bar before values are recorded. | 6 months | 1. Size of both earth strips and earth cables connected to it will be matched. 2. Lugging of earth strips in lightning distribution boards will be discontinued and individual wires will be connected. 3. Sewing machines and tables have been bonded with earth wires. 4. Bare copper wire has been insulated. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Earthing system | Earth strips in lightning distribution boards were inadequate in terms of size, several earth wires were lugged together as one, the bonding mechanism was not adopted in the main building B2, sewing and stitching machines and tables were not bonded. We also observed that bare copper wire was laid in an open environment before the chiller room. | In the earth-test report, mention the method of testing and ensure that each pit is disconnected from its distribution bar before values are recorded. | E7 + 1 month | We have planned this activity in parts because shutdown is required for its completion of the whole plant and earth pit test report will be formulated on annual basis. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Multiple Connections | This issue was noticed in almost every panel in the facility. There was a multi-looping of wires. Multi-looping can build up heat that is generated during normal operations. It can also cause overloading of circuits if the cable current carrying capacity exceeds circuit ratings. | Inspect the facility to identify where multi-looping exists. | 3 months | It was decided that we will share the design document of Panel/DB with Accord team for their review. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Multiple Connections | This issue was noticed in almost every panel in the facility. There was a multi-looping of wires. Multi-looping can build up heat that is generated during normal operations. It can also cause overloading of circuits if the cable current carrying capacity exceeds circuit ratings. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or new distribution boards adjacent to existing panels if there is no space for new circuits. | 3 months | It was decided that we will share the design document of Panel/DB with Accord team for their review. |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was installed in the facility but did not have a risk assessment report. A risk assessment report for the lightning protection system is necessary to inspect the level of risk a building is bearing and the level of protection it needs to prevent any damage from lightning. The lightning protection system was sharing earth pits with the electrical distribution network. This is an issue because the lightning strike can damage the equipment connected to the electrical distribution system due to the high current induced by the lightning strike. | Consult a qualified engineer and conduct a risk assessment to evaluate the vulnerability of the facility. Risk assessment for the lightning protection system and the system design report (if required) should be carried out by a qualified engineer. | 2 month | Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review Risk Assessment report is available. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was installed in the facility but did not have a risk assessment report. A risk assessment report for the lightning protection system is necessary to inspect the level of risk a building is bearing and the level of protection it needs to prevent any damage from lightning. The lightning protection system was sharing earth pits with the electrical distribution network. This is an issue because the lightning strike can damage the equipment connected to the electrical distribution system due to the high current induced by the lightning strike. | Seek guidance from qualified lightning protection professionals or engineers who specialize in designing and installing lightning protection systems. The lightning protection system must comply with IEC-62305 standards for design and installation. | 6 months | Each lighting arrestor has its dedicated redundant earth pit already separated from rest of the electrical system. We will show the same on site and share the drawing of earth pits connected with the lightning protection system for their review. Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Fire Alarm & Detection System (FADS) | Alarm Sounders | While testing the fire alarm detection system it was observed that even though the factory was shut down and there was no noise from machinery, the audibility of the sounders was very low. Furthermore, there were several places where sounders were not placed, and that location was dependent on the nearest sounder in reach. This is a severe issue, and it needs to be addressed accordingly. If there is no audibility in areas then it will not alert the workers which in a result can cause compromised safety measures, delay in emergency alerts, and evacuation. | Consult a qualified engineer and assess the current state of the fire alarm system. Identify areas where the audibility is low and the potential causes of the issue. List the causes and design a suitable solution for the system. | 3 months | We have consulted a qualified engineer to assess the current state of fire alarm system to identify low audibility area. We have list down its causes and already working for its suitable solution. Updated layout is being attached for your review. Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) complying with NFPA 72 and submit to Pakistan Accord for review before purchasing any new equipment. Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Fire Alarm & Detection System (FADS) | Alarm Sounders | While testing the fire alarm detection system it was observed that even though the factory was shut down and there was no noise from machinery, the audibility of the sounders was very low. Furthermore, there were several places where sounders were not placed, and that location was dependent on the nearest sounder in reach. This is a severe issue, and it needs to be addressed accordingly. If there is no audibility in areas then it will not alert the workers which in a result can cause compromised safety measures, delay in emergency alerts, and evacuation. | Consult with fire safety experts or professional fire alarm system installers to assess the situation and determine the most appropriate solutions for improving audibility that comply with NFPA-72. | 3 months | Once installation of FADS is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review. Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Fire Alarm & Detection System (FADS) | Detectors | It was observed that there were some places where smoke detectors were missing. This includes mainly the time office building floors and the main distribution board area. This is an issue because if there is a fire in these areas then the fire alarm detection system will not sense it which can lead to delayed response time, equipment damage, and even a risk to the life of the occupants. | Inspect the facility in terms of blind spots where smoke detectors are needed. Install smoke detectors where needed according to the requirements that comply with standards. Do keep in mind that the equipment you are installing should be listed. | 6 months | Factory will provide full testing and commissioning (T&C) certification from FADS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | Pending Verification
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Emergency Lighting | No emergency lighting | Several locations were found especially in the main building which includes the packing area, stitching section, jig room, and sewing area missing adequate emergency lighting. Emergency lights are essential in an emergency for workers to escape the facility if there is a power failure. | Inspect your facility in terms of blind spots where emergency lights are needed. Install emergency lights where needed according to the requirements that comply with standards. Do keep in mind that the equipment you are installing should be listed. | 6 months | Additional Emergency lights will be installed to improve lux levels. |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | Emergency Lighting | Provided but non-functional | Emergency lights were not working in the time office building which includes stitching lines and packing area. Emergency lighting helps in the aid of evacuation and mitigates potential risks to personnel.Top of Form | Inspect the facility and replace batteries and/or lights that are not working sufficiently. | 2 months | We are conducting inspection of all the lights and batteries will be replaced. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | Emergency Lighting | Provided but non-functional | Emergency lights were not working in the time office building which includes stitching lines and packing area. Emergency lighting helps in the aid of evacuation and mitigates potential risks to personnel.Top of Form | Inspect your facility in terms of blind spots where emergency lights are needed. Install emergency lights where needed according to the requirements that comply with standards. Do keep in mind that the equipment you are installing should be listed. Develop a periodic maintenance program to check and inspect your emergency light backup power to avoid any issues related to the backup supply. | 6 months | We are conducting inspection of all the areas and emergency lights. We will replace the faulty batteries and install the additional lights to improve the lux levels to comply with the standards. |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Emergency Lighting | Independent power source | It was observed that every building in the facility was equipped with an emergency lighting system, but the circuit dedicated to it was not independent instead it was wired by the common supply of floors. This is an issue because if shut down/ power failure occurs the emergency lights will drain their backup. | Install a separate independent circuit for an emergency lighting system that complies with the required standards. | 6 months | Independent power circuit will be provided to emergency lights installed at the floor through its light distribution board with dedicated breaker. |  |  |  | Pending Verification
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Cabling & Wiring | Colour coding | Panels were found with color coding issues. If cables are not installed according to colour coding standards, it can lead to confusion, mistakes, and potential safety hazards. Only use a color code that complies with the standard for any new work. | Begin by identifying each cable and labeling them accordingly, especially if they deviate from the standard color coding. Use durable and visible labels to indicate the function or purpose of each cable. | 2 months | Color coding issue of cables have been rectified. |  |  |  | Pending Verification
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Cabling & Wiring | Colour coding | Panels were found with color coding issues. If cables are not installed according to colour coding standards, it can lead to confusion, mistakes, and potential safety hazards. Only use a color code that complies with the standard for any new work. | Reinstall the cables Using the correct color-coded markers, tags, or sleeves to visually distinguish cables that deviate from the standard color coding. | 2 months | Color coding issue of cables have been rectified. |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Cabling & Wiring | Splicing of cables | Cable joints were found at various locations in the facility. This can result in increased resistance, leading to overheating of the joint. Over time, this can cause insulation degradation, melting of insulation materials, and even fire hazards. Wire connectors were also used all over the facility. This needs to be rectified because connectors can collect fluffs in them which can cause short circuits, increased resistance leading to overheating, and have a risk of fire. For any future work, make sure that there are no cable joints and PVC connectors used. | Establish a routine inspection and maintenance schedule to check cable joints for signs of damage, overheating, or corrosion. Replace any damaged or deteriorated joints to prevent further issues. Remove PVC connectors and develop a periodic maintenance program to ensure that the facility is free from these non-compliance issues. | 4 months | Cable joints and connectors has been removed. Factory will have inspection and maintenance schedule ready for review by Accord on site |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Cabling & Wiring | Fixtures | It was noticed several power sockets were damaged. This is serious as it is hazardous in many ways like electric shock, short circuit, and equipment damage. | Replace every damaged socket with a new one. | 3 months | Damage sockets have been rectified. |  |  |  | Pending Verification
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Cabling & Wiring | Fixtures | It was noticed several power sockets were damaged. This is serious as it is hazardous in many ways like electric shock, short circuit, and equipment damage. | Develop a periodic maintenance program to ensure that every equipment installed in the facility is in good condition and can be used safely. | 3 months | Preventive maintenance schedule has been developed Factory will have inspection and maintenance schedule ready for review by Accord on site |  |  |  | Pending Verification

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
26-Mar-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Interloop Denim Chak 65, Raiwind, Kasur, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-03-26
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Non Compliant Locking mechanism has been observed in Main Production building Production Hall (Ground floor & 1st floor), Chiller Room building Ground floor (Main Exit), Time Office building Ground floor (Day Care centre room) & Roof Emergency Exit door | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | These are normal doors which remain open all the time and we have to lock at time of factory closing on holidays only. However there is no locking mechanism on emergency doors which are totally separated from these doors. Factory will share drawings showing escape routes leading to emergency exits and ensure no locking mechanisms on these routes |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Non Compliant Locking mechanism has been observed in Main Production building Production Hall (Ground floor & 1st floor), Chiller Room building Ground floor (Main Exit), Time Office building Ground floor (Day Care centre room) & Roof Emergency Exit door | Provide easily opening mechanisms complying with Pakistan Accord Building Standard Section 1 Clauses 1.4 & 1.5 | 3 months | These are normal doors which remain open all the time and we have to lock at time of factory closing on holidays only. However there is no locking mechanism on emergency doors which are totally separated from these doors. Factory will share drawings showing escape routes leading to emergency exits and ensure all doors on these routes have easy open mechanisms complying with Pakistan Accord Building Standards |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Sliding doors are installed in following locations Main Production building Ground floor, Main Production building Canteen area, Main Building Stitching area | Replace sliding door(s) with side hung swinging door(s) which swing in the direction of egress travel or alternatively if the sliding doors can accommodate it build a “pocket side swing door” into the sliding panel | 3 months | Two ways pocket doors will be fabricated within the existing sliding doors on escape routes (being used for worker movement only). While as per discussion with Accord, there is no need to fabricate pocket doors which are marked as NO Exit. So, they will remain as it is. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Protection of stairs | Emergency Exit stairs are not protected in Main Production building S-11, S 8, S-6, Time office Building S 1 & S 2. •Main Building Lift shafts which are not protected by fire and smoke resistant construction and open into protected escape stairs. Chiller Building – Exit Discharge stairs from roof not protected – Combustible material storage under stair •Main Production building – Ground floor stitching section exit discharge with tripping hazard | Remove all combustible material stored along stairs | 1 month | Combustible material which was stored along with stairs has been removed |  |  |  | Pending Verification
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | Emergency Exit stairs are not protected in Main Production building S-11, S 8, S-6, Time office Building S 1 & S 2. •Main Building Lift shafts which are not protected by fire and smoke resistant construction and open into protected escape stairs. Chiller Building – Exit Discharge stairs from roof not protected – Combustible material storage under stair •Main Production building – Ground floor stitching section exit discharge with tripping hazard | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and acceptance prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs; Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | Factory will prepare drawings showing proposed fire separating construction and door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | Emergency Exit stairs are not protected in Main Production building S-11, S 8, S-6, Time office Building S 1 & S 2. •Main Building Lift shafts which are not protected by fire and smoke resistant construction and open into protected escape stairs. Chiller Building – Exit Discharge stairs from roof not protected – Combustible material storage under stair •Main Production building – Ground floor stitching section exit discharge with tripping hazard | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. | F5 + 4 months | Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Fire Rated Construction | Structural fire rating | Steel structure of the Main building or parts of the building is not fire protected | Factory consultant to identify level of fire protection needed for the structure based on height, area, provision of sprinklers and frontage space around the building, in accordance with Pakistan Accord Building Standard and reference to NFPA 5000 cl.7.6.2. Submit proposal for level of fire protection required and methods for achieving it to Pakistan Accord for review. | 4 months | As per discussion with Accord, we will work to find the solution for the fire protection of the steel structure. Factory will submit proposals for fire protection of the steel structure to Accord for review |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Fire Rated Construction | Structural fire rating | Steel structure of the Main building or parts of the building is not fire protected | Implement the proposal for addressing the fire protection of the structure based on proposal reviewed previously, and in accordance with Pakistan Accord Building Standard | F7 + 4 months | As per discussion with Accord, we will work to find the solution for the fire protection of the steel structure. Factory will implement the solution for fire protection of the structure in accordance with proposals reviewed previously by Accord |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Fire Rated Construction | Separation of shafts | Lift Shaft separation with fire rated construction issues are observed in Main Production building – Ground floor Washing area and near stitching area. | Submit design documentation to the Pakistan Accord for review, showing proposals for addressing the lift opening into adjacent accommodation | 4 months | We have double door system in lifts and one door remain closed when the lift is on other floor. In addition to this, location of the lift is away from fire exits and does not create any hurdle during evacuation. Factory will prepare drawings showing proposed fire separating construction to shafts, with details of door assembly, location in relation to escape routes and lift door operation, and submit to Accord for review prior to any rectification works. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Fire Rated Construction | Separation of shafts | Lift Shaft separation with fire rated construction issues are observed in Main Production building – Ground floor Washing area and near stitching area. | Provide fire-rated separation between staircase enclosure and lift in accordance with the Pakistan Accord Building Standard, implementing the previously reviewed design proposal | F9 + 4 months | We have double door system in lifts and one door remain closed when the lift is on other floor. In addition to this, location of the lift is away from fire exits and does not create any hurdle during evacuation. Fire rated separation of lift will be completed, including brickwork/ fire rated assemblies and adequate and door operating mechanism, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Fire Rated Construction | Atrium | Main Building (Production) has wide atrium - Potential spread of fire & smoke in between floors : •Main building central Opening between two floors / portions | Prepare drawings showing the proposed fire separation and means of escape from all areas bordering on the atrium and submit to Pakistan Accord for review. | 4 months | We have shared the drawing of first floor of the building depicting all the emergency exits for evacuation with for review. Factory will prepare drawings showing all floors connected to atrium in plan and section, routes and distances from atrium edge to protected stairs, use of floors connected to atrium, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Fire Rated Construction | Atrium | Main Building (Production) has wide atrium - Potential spread of fire & smoke in between floors-Example is : •Main building central Opening between two floors / portions | Provide fire rated construction including opening protection assemblies i.e. fire doors and alternative means of escape according to the layouts and documents reviewed by Pakistan Accord. | F11 + 4 months | If needed, fire rated separation of atrium will be completed, including brickwork/ fire rated assemblies/ glazing, according to proposal previously reviewed and accepted by Accord |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Fire Rated Construction | Storage | Excessive Storage and Occupancy separation issues have been observed in Main Production building – Ground floor (Storage , Offices and Production), Ground floor cutting area, Washing building – Ground floor Store, Time office building – Ground floor Storage. | Identify all designated storage areas. For all storage areas where storage cannot be managed within in-process storage limitations described above, prepare drawings showings proposed fire separation details of storage areas. These shall be submitted to Pakistan Accord for review and acceptance prior to the rectification works. The drawings should cover the following: - Locations of fire rated walls and doors. Details of fire walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Temporary storage was removed from the ground floor main production building. New area will be marked and assigned for the storage of cutting WIP. This is not storage and belongs to the part of the production process for its feeding and execution of smooth operations. So, it will be treated as same hazard category and controls with that of production floor. We have removed the storages from time office ground floor building. Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Rated Construction | Storage | Excessive Storage and Occupancy separation issues have been observed in Main Production building – Ground floor (Storage , Offices and Production), Ground floor cutting area, Washing building – Ground floor Store, Time office building – Ground floor Storage. | Provide the required fire separation as per documentation reviewed by Pakistan Accord. | F13 + 4 months | Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | Pending Verification
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Hazardous Materials | Chemicals storage | Hazardous materials - Chemical storage issues are observed in Chiller room building – Ground floor, 1st floor and Washing building – Ground floor (Store area ) | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet Pakistan building code requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code . | 3 months | We have shared the Chemical inventory list. Separate room will be constructed for the storage of chiller chemicals.Separate room for flammable chemicals will be constructed outside the washing building. Factory will submit drawings with proposal for storage arrangements to meet Pakistan Accord Building Standard requirements. Once reviewed by Accord factory will implement agreed plan. |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
26-Mar-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Interloop Denim Chak 65, Raiwind, Kasur, Punjab, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 2024-03-26
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Structural Documentation | Lack of safe load plans | The factory had load plans on display mentioning the existing loading; however, crucial information regarding the maximum design floor load capacity was missing. | Building Engineer to update the load management plans and to include information on the maximum floor capacity. | 6 months | Maximum design floor load capacity has been incorporated into the load plans and will be shared with Accord for review |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1