## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
23-Jul-2024
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | Zephyr Textiles Limited 63-KM Multan Road Jumber Khurd, Tehsil Pattoki, District Kasur
[9 empty] | Date of Initial Inspection | [12 empty] | 23-Jul-2024
[22 empty] | Work Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | It was found that the substation room layout drawing for the factory was not available. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 1 month | Facility will develop and maintain a substation room layout drawing for the factory. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Single Line Diagram (SLD) | It was found that the electrical single line diagrams (SLDs) for the factory were not available. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 3 months | Facility will Develop and maintain electrical single-line diagrams (SLDs) for the factory, ensuring accurate documentation of the electrical system. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | During the inspection, it was found that electrical layout drawings were not available in the facility, including power layouts, lighting layouts, containment layouts, fire alarm layouts and earthing layout drawings. | Develop comprehensive electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 months | Facility will develop and maintain electrical layout drawings to ensure proper documentation for electric safety. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Circuit breakers | It was observed that the circuit breaker was installed in the Block-1 compressor area without breaker boxes and fixing supports. This inadequate fixing could lead to poor connections, arcing, short circuits, or other electrical faults. | Cover all circuit breakers that are openly installed throughout the facility with concealed metallic enclosures to ensure safety and compliance with standards BS 7671 Section 416. | 2 months | Facility will install a proper breaker box and fixing supports for the circuit breaker in the Block-1 compressor area. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Circuit breakers | It was observed that the circuit breaker in the main LT room panel Block-1 has a broken lever, posing a potential hazard during emergency switching operations. | Replace breakers that have broken lever to ensure safety and secure operation during emergency. | 2 months | Facility will replace the broken lever on the circuit breaker in the main LT room panel (Block-1) to ensure safe and reliable operation. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | It was also found that the multiple circuit breakers had ratings that were not appropriate for the connected cable sizes such as: (Block-1 generator room distribution board, pump area distribution board (100 Ampere breaker with 2.5Sq Mm Cable), LT room panel (400 Ampere breaker with 95 Sq Mm Cable), Block-3 stitching area distribution board (80 Ampere breaker with 4 Sq Mm Cable), Block-3 dyeing area DB (150 Ampere breaker with 4 Sq Mm Cable). | Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current-carrying capacity. | 2 months | Facility will replace incorrectly rated circuit breakers with appropriately sized breakers that match the connected cable sizes. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E7 | DBs & Elec Protection Systems | Hot Spots | During the inspection, hot spots were found in the following electrical panels at a cable termination point. -Observed at the Block-1 main LT room panel, turbine room, rice husk boiler area distribution boards. | Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring the safe and reliable operation of the electrical systems. | 1 month | Facility will rectify the identified hot spots at cable termination points in the Block-1 main LT room panel, turbine room, and rice husk boiler area distribution boards. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E8 | DBs & Elec Protection Systems | Hot Spots | It was also found that the Thermographic report was not available at the site. | Carry out an independent thermographic survey of the entire electrical system periodically to proactively manage and mitigate the risks associated with overheating. Submit the thermographic test report to the Pakistan Accord for review. Thermographic inspection must be carried out at least once in 6 months | E7 + 6 months | Facility will conduct a thermographic survey of electrical systems and maintain a Thermographic Report on-site for monitoring. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E9 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations and many electrical machines did not have earth wires. -Observed at Block-3 (dyeing area, finishing depart and first floor bathrobe section area) distribution boards. | Submit the earth system design to Pakistan Accord for review before installation. | 4 months | Facility will repair and submit the earth system design to Pakistan Accord for review and approval before installation. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | The earthing system was absent in multiple locations and many electrical machines did not have earth wires. -Observed at Block-3 (dyeing area, finishing depart and first floor bathrobe section area) distribution boards. | Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. | E9 + 2 months | Faculty will install earthing systems where absent and ensure all electrical boards are fitted with required earthing cables. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E11 | DBs & Elec Protection Systems | Earthing system | It was found at the Block-1 LT room panels and compressor area distribution boards that Earth bonding connections were not provided to distribution board front gates. | Implement equipotential bonding for panel bodies to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | E9 + 1 month | Facility will provide earth bonding connections to the front gates of distribution boards in LT room panels and compressor area. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E12 | DBs & Elec Protection Systems | Earthing system | It was found at the Block-1 LT room panels and compressor area distribution boards that Earth bonding connections were not provided to metallic trays, and frames. | Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. | E10 + 2 months | Facility will provide earth bonding connections to trays and frames in LT room panels and compressor area distribution boards. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E13 | DBs & Elec Protection Systems | Earthing system | It was noted that the earth bus bar of the Block-1 pump area distribution board was incorrectly connected to the neutral bar, indicating improper grounding practices. | Separate the earth bars from the neutral bars in the distribution boards and ensure they are correctly connected and isolated . | 1 months | Facility will separate the earth bus bar connection in pump area distribution board with grounding standards. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E14 | DBs & Elec Protection Systems | Earthing system | It was also observed that multiple distribution boards including the Block-1 generator room and Block-3 dyeing depart outdoor area had corroded earth bus bars and lacked protective enclosures. A corroded earth bus bar can lead to poor grounding, increased electrical resistance, and potential safety hazards. Without an enclosure, exposed busbars can pose a serious risk of accidental contact. | Replace or clean the bus bar and ensure it is housed in a non-corrosive, protective enclosure. Compliance with BS 7671 18th Edition is essential to ensure electrical safety and prevent future corrosion. | 2 months | Facility will replace corroded earth bus bars and install protective enclosures in Block-1 generator room and Block-3 dyeing department outdoor area distribution boards. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Earthing system | It was also found that the Earth testing record was not available at the site. | Develop and submit the earth testing record to the Pakistan Accord for review. | 4 months | Facility will conduct earth testing and maintain earth testing records on-site. |  |  |  | In Progress
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was found that several distribution boards, cable terminals and bus-bars exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. Observed at Block-1 pump area and R.O plant area distribution boards. | Replace or refurbish corroded electrical panels and bus bars to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. Use IP-rated enclosures to protect panels and bus bars from environmental factors like moisture, dust, and temperature fluctuations. | 2 months | Facility will replace or treat corroded distribution boards, cable terminals, and bus bars in pump area and R.O plant area to prevent electrical failures. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E17 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was observed at ground floor canteen area distribution boards and LT room panels cable terminals and bus-bars exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. | Replace or refurbish corroded electrical panels and bus bars to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 2 months | Facility will replace or refurbish corroded cable terminals and bus bars in ground floor canteen area distribution boards & LT room panels. Implement protective measures to prevent moisture exposure and corrosion. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was also found that there was loose wiring and insufficient working space inside the distribution boards for operation and maintenance. Loose wiring and insufficient space, lead to excessive heat generation which can cause the insulation to melt and potentially lead to fire. Observed in the Block-1 generator room and Block-3 raising machine area distribution boards. | Install wire ducts to organize and route wires neatly, remove loose cables, and ensure that no cables are attached to the bus bars. This may mean the addition of new distribution boards with proper accessibility for cables incoming and outgoing, bus-bar alignment. | 3 months | Facility will ensure properly secure loose wiring and ensure sufficient working space inside distribution boards in Block-1 generator room and Block-3 raising machine area. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E19 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was found that the Block-3 finishing area and Block-6 fabric storage area distribution boards lack a dedicated neutral connection for outgoing power circuits. | Conduct a thorough inspection of the existing wiring to identify circuits sharing a neutral wire. Provide dedicated neutral wires for each circuit, ensuring that each circuit's return path is properly isolated in accordance with BS 7671 (18th Edition) regulation 314.4. | E18 + 2 months | Facility will provide a dedicated neutral connection for outgoing power circuits in Block-3 finishing area and Block-6 fabric storage area distribution boards |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | It was also found that the Non-IP rated distribution boards and breaker box were installed in the Block-1 RO plant and the dyeing depart outdoor area. | Replace the RO plant area distribution board with an IP-rated panel (IP-65) and breaker boxes or relocate them to in indoor area. | 4 months | Facility will make sure to replace the R.O. plant area distribution board with an IP-65 rated panel and breaker boxes, or relocate it to an indoor area. |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Loop Connection | During the inspection loop connections were identified within the Block-1 generator room, Block-3 finishing area Block-4 carton storage area and Block-6 fabric storage distribution boards. In these loop connections, one circuit breaker is energized by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilized to provide each circuit with the required live, neutral, and earth connections. | 2 months | Facility will modify all electrical panels to eliminate loop connections and implement a busbar system. |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Multiple Connections | During our inspection, multilooping was observed in a number of electrical panels and stitching machine power plugs across the facility such as Block-1 generator room, pump area, Block-3 stitching and finishing area distribution boards . In these cases, multiple circuits were being protected by a single circuit breaker. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022) | 2 months | Facility will modify the electrical installation to ensure each circuit is protected by a dedicated circuit breaker. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E23 | DBs & Elec Protection Systems | Openings | During the inspection, it was found that many distribution boards and cable trunking have openings that may cause potential hazards due to environmental factors. Observed at Block-1 LT room panels, HT room and generator area main cable trench, Block-3 finishing area cable trays . | Seal the openings/holes of panels, cable trays and trenches with metallic enclosures, fire-resistant sealants, gaskets, or fillers. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | 2 months | Facility will seal openings/holes in panels, cable trays, and trenches using metallic enclosures, fire-resistant sealants, gaskets, or fillers. Facility will conduct regular maintenance and maintain comprehensive records to ensure IP ratings remain intact. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E24 | DBs & Elec Protection Systems | Adequate accessibility | At multiple locations including the Block-1 main LT room, old ETP room, Block-3 dyeing depart and stitching area, it was found that the electrical distribution boards do not possess the required space for inspection or easy access to the panels and their components. | Electrical equipment shall be arranged to ensure adequate space is available for both the initial installation and the subsequent replacement of individual components. This arrangement shall comply with the requirements outlined in Section 132.12 of BS 7671: 18th Edition + Amendment 2 (2022), providing sufficient clearance for safe and efficient installation and maintenance. | 2 months | Facility will ensure adequate space for installation and maintenance of electrical equipment to allow safe component replacement and operation. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Lint & dust inside panel board | It was found that a significant accumulation of lint and dust in multiple distribution boards and cable trays. -Observed at Block-1 generator room distribution board, compressor area vfd panel, pump area and R.O plant area distribution board. | All electrical distribution boards and trunking runs shall be inspected and cleaned of any dust or lint in accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022). A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 2 months | Facility will Clean accumulated lint and dust from distribution boards and cable trays. Facility will implement a regular cleaning and maintenance schedule to prevent fire hazards and ensure safe operation. |  |  |  | In Progress
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no LPS risk assessment available to confirm its adequacy. | Hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. Submit the risk assessment and design of the existing lighting protection system to the Pakistan Accord for review. | 1 month | Facility will engage a qualified engineer to conduct an adequacy study of the existing Lightning Protection System (LPS) |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E27 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | A lightning protection system was provided, however, there was no LPS risk assessment available to confirm its adequacy. | If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard BS 7671. | E26 + 4 month | Facility will conduct an LPS risk assessment to verify the adequacy of the existing Lightning Protection System. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E28 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | It was observed that the bare conductor of the Lightning Protection System was damaged and not properly supported. | The LPS bare conductor should be secured in accordance with standards and ensure that it is safely routed and protected from damages. Establish a routine maintenance schedule to inspect and maintain the LPS, ensuring ongoing protection against corrosion. | E26 + 4 month | Facility will secure LPS bare conductors as per standards, ensuring safe routing and protection from damage. Facility will also implement a routine maintenance schedule to inspect and prevent corrosion for continued effectiveness. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Fire Alarm & Detection System (FADS) | Fire Alarm Panel | It was found that an addressable fire alarm system had been installed for the Block-4 warehouse area and the Block-3 first-floor bathrobe stitching area along with fire-rated cabling was used, However, the factory did not possess any design documents, drawings, or test certificates related to the listing of the panel, cabling, or devices. | Submit the addressable fads system necessary design documents, wiring diagrams, and test certificates to the Pakistan Accord for review to confirm the fire alarm panel, cabling, and devices are listed and certified. Ensure that each area in the existing fire alarm panel is correctly programmed according to the specific location, such as the carton warehouse and the bathrobe stitching area. This will prevent any confusion during an emergency. | 3 months | Facility will submit design documents, wiring diagrams, and test certificates of the addressable FADS system to Pakistan Accord for review. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E30 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | It was observed that in the Block-1 utility section, Block-2 canteen area, Block-3 finishing, dyeing area, Block-5 administrative offices, and Block-6 Fabric storage area, a manual hooter system was installed along with stand-alone fire detectors. However, several deficiencies were noted, including the absence of fire-rated cables, the use of non-listed devices, insufficient audibility, and the lack of visual alarms | (1) Submit design documentation for new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 3 months | Facility will submit design documentation for the new FADS system to Pakistan Accord for review before procurement. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E30+ 1 month | Facility will submit documentation to Pakistan Accord confirming that an L/C has been opened for the import of required FADS components as per the previously submitted design. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E32+ 4 month | Facility will submit documentation to Pakistan Accord confirming that all imported and locally procured materials for the FADS installation have been purchased and are available on-site. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E33 + 5 months | Facility will submit full as-built documentation to Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E34 + 5 months | Facility will notify Pakistan Accord upon FADS installation completion for verification inspection to ensure compliance with the reviewed design documentation. |  |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E34 + 3 months | Facility will provide full Testing & Commissioning (T&C) certification from the FADS installer and arrange for a final T&C verification inspection with the installer, factory technical team, and Pakistan Accord. |  |  |  | In Progress
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Emergency Lighting | Provided but insufficient | It was found that the emergency lights provided in the facility were insufficient to cover the entire facility. The emergency lighting did not provide adequate illumination levels, leading to dark or poorly lit areas during power outages. Observed at Block-2 canteen area, Block-3 Finishing and dyeing production area, finishing area warehouse section, Block-5 office blocks and Block-6 Fabric storage area. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. Submit the emergency lighting system design to the Pakistan Accord for review before the installation. | 3 months | Facility will conduct a survey to identify areas lacking emergency lighting and install additional luminaires, and submit the emergency lighting system design to Pakistan Accord for review before installation. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E37 | Emergency Lighting | Provided but non-functional | During the inspection, it was observed that emergency lighting was provided but not functional in several locations. -Observed at Block-3 dyeing area, stitching area and Block-4 finished goods store. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant listed emergency lighting fixtures to ensure they provide adequate illumination. | E36 + 2 months | Facility will Inspect all emergency lighting units and repair or replace defective units with compliant fixtures. |  |  |  | In Progress
No | 3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | The ventilation system was inadequate, with insufficient air flow leading to heat accumulation in the HT room. | Redesign the ventilation layout to enhance the distribution of airflow, ensuring that critical areas around the HT room receive adequate ventilation. This might involve repositioning vents or adding ductwork. | 2 months | Facility will redesign the ventilation layout to improve airflow distribution, ensuring adequate ventilation in critical areas around the HT room by repositioning vents or adding ductwork. |  |  |  | In Progress
No | 3 | 8 |  | 154 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Generator, Transformer & Sub-Station Room | Ventilation and illumination | Several sections of the HT room were poorly lit, with light levels falling below the minimum required for safe operation and maintenance. | Add more lighting fixtures in poorly lit areas to ensure an even distribution of light throughout the HT room. Focus on areas that require the highest visibility, such as around control panels in accordance with BS 7671, Section 413. | 2 months | Facility will install additional lighting fixtures in poorly lit areas of the HT room. |  |  |  | In Progress
No | 3 | 8 |  | 155 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Cabling & Wiring | Cables support and protection | It was found that at different locations cables were running without cable containment, such as cable trays, conduits, or ducting. cables were laid directly over the floor. -Observed at Block-1 HT room cable, compressor area cable and generator cable, Block-3 dyeing area machine cable, and main gate HT cable. | Secure cables with appropriate supports or containments to prevent sagging, stress, and potential hazards, in accordance with BS 7671 18th Edition + A2 (2022) Regulation 522.8.5. Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | 3 months | Facility will secure cables with appropriate supports or containments to prevent sagging, stress, and hazards. Facility will implement a cable management system with regular inspections. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E41 | Cabling & Wiring | Cables support and protection | It was found that in Block-2 canteen area a cigarette was being lit by short-circuiting an electrical circuit that generated heat. The combination of a short circuit and heat generation significantly increases the risk of an electrical fire. | Prohibit and monitor against the practice of using electrical circuits for lighting cigarettes or any other unsafe activities. | E40 + 2 months | Facility will clearly prohibit and strictly monitor the use of electrical circuits for lighting cigarettes or any other unsafe activities to prevent fire hazards. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E42 | Cabling & Wiring | Cable trench and channel cleanliness | During the inspection of the facility, It was found that the cleanliness of the cable trunking system had not been maintained. Numerous cable trenches were found to be filled with a significant amount of fluff and dust, which poses a serious fire risk. -Observed at Block-1 main LT room cable containment room and generator room cable trench. | Clean cable containment room and all cable trenches to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 2 months | Facility will clean cable containment rooms and trenches to remove accumulated dust and fluff, eliminating potential fire hazards. Facility will implement a regular maintenance schedule with routine inspections and cleaning. |  |  |  | In Progress
No | 3 | 8 |  | 162 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E43 | Cabling & Wiring | Splicing of cables | It was found that the cables terminations were installed without cable lugs, which resulted in breaking strands, and loose Connections. Observed at Block-1 generator room and Block-3 finishing area distribution boards. | Install cable lugs on all improperly terminated cables within the distribution board to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 3 months | Facility will install cable lugs on all improperly terminated cables within distribution boards to secure connections and prevent loose strands. Facility will implement an SOP mandating the use of cable lugs for all future terminations, with regular training and audits |  |  |  | In Progress
No | 3 | 8 |  | 163 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E44 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in the Block-3 stitching area machine cable. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical short circuits and fires. | Replace all PVC tape joints with fire rated terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | E43 + 2 months | Facility will replace all PVC tape joints with fire-rated connectors to ensure secure and stable connections. Facility will establish a policy prohibiting PVC tape for electrical jointing, conduct regular inspections, and provide continuous staff training on proper jointing techniques. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E45 | Cabling & Wiring | Splicing of cables | It was also found that the PVC connectors were used for circuit termination in the Block-1 pump area distribution board. | Prohibit the use of PVC connectors and, use accessories that comply with the standards. | E44 + 1 month | Facility will replace PVC connectors with standard-compliant termination accessories in the Block-1 pump area distribution board. |  |  |  | In Progress
[9 empty] | Initial | [10 empty] | E46 | Cabling & Wiring | Splicing of cables | It was also found that at Block-3 dyeing area machine wires were inserted directly into power receptacles without a power plug. | Replace the directly inserted power wires with proper power plugs to ensure safe and secure connections. | E44 + 1 month | Facility will ensure all machine wires in the Block-3 dyeing area are properly connected using appropriate power plugs. |  |  |  | In Progress
No | 3 | 8 |  | 164 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E47 | Cabling & Wiring | Colour coding | During the inspection of multiple distribution boards, deviations from standard cable colour coding practices were identified. -Observed at Block-3 (finishing area, cutting area, packing area and first floor bathrobe section distribution boards) . | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labeling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. Develop and enforce a strict protocol for cable colour coding to be followed for all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. | 2 months | Facility will conduct an audit of all distribution boards to correct cable color coding. Facility will also ensure re-label cables as needed and enforce a strict protocol with regular training for compliance in future installations. |  |  |  | In Progress
No | 3 | 8 |  | 165 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E48 | Cabling & Wiring | Fixtures | A loose and broken fixture was found in the Block-3 stitching area exhaust fan controller. | Replace and secure the fixture with appropriate fixed supports to prevent movement and ensure stable connections. | 2 months | Facility will replace and securely fix the fixture with appropriate supports to prevent movement. |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
[8 empty] | 04-Sep-24 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
[10 empty] | Remediation Summary of Actions Required | [10 empty] | Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Zephyr Textiles Limited 63-KM Multan Road Jumber Khurd, Tehsil Pattoki, District Kasur
[8 empty] | Date of Initial Inspection | [12 empty] | 04-Sep-2024
[21 empty] | Financing Schedule | Work Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found at majority doors in building. - Escape doors are lockable in block 1, 2, 3 and 5. - Escape doors in all blocks have non-compliant opening mechanism which can create hindrance in escape. - Sliding escape door from metal free zone in block 3. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | Facility will make sure to remove all locking devices from doors on egress routes to ensure unobstructed exit from inside. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found at majority doors in building. - Escape doors are lockable in block 1, 2, 3 and 5. - Escape doors in all blocks have non-compliant opening mechanism which can create hindrance in escape. - Sliding escape door from metal free zone in block 3. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | F1 + 3 month | Facility will replace escape doors with side-hung doors and sliding doors with side-swinging doors that open in the direction of exit travel. |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F3 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found at majority doors in building. - Escape doors are lockable in block 1, 2, 3 and 5. - Escape doors in all blocks have non-compliant opening mechanism which can create hindrance in escape. - Sliding escape door from metal free zone in block 3. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F2 + 3 month | Facility will ensure that escape doors are regularly monitored to ensure no locking devices obstruct easy access to emergency exits. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F4 | Means of Escape | Travel distance | - Common path of travel distances exceed permitted limits (35m) in block 3 as highlighted in figure 6. - Common path of travel distance exceed permitted limit (36m) in block 4 as highlighted in figure 10. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Building Standard. | 4 months | Facility will make sure to reduce common path of travel distances by implementing alternative egress routes. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F5 | Means of Escape | Travel distance | - Common path of travel distances exceed permitted limits (35m) in block 3 as highlighted in figure 6. - Common path of travel distance exceed permitted limit (36m) in block 4 as highlighted in figure 10. | Implement the plan previously reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard. | F4 + 4 month | Facility will ensure to modify escape routes to comply with permitted travel distance limits. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F6 | Means of Escape | Protection of stairs | All Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. - Unprotected openings into stairs S1 block 2 from canteen on ground level, S2 block 3 from production on ground level, S6 & S7 (lift shaft). - Unprotected penetrations into stairs S2 block 3 all levels. - Doors not fire doors in all of the protected stairs. - Fire load in stairs S2 block 3 level ground. | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | Facility will make sure that all fire load and stored items are removed from stairways. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | All Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. - Unprotected openings into stairs S1 block 2 from canteen on ground level, S2 block 3 from production on ground level, S6 & S7 (lift shaft). - Unprotected penetrations into stairs S2 block 3 all levels. - Doors not fire doors in all of the protected stairs. - Fire load in stairs S2 block 3 level ground. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | Facility will prepare and submit detailed drawings to Accord for review, including a layout plan showing the location of fire-rated walls and doors protecting the stairs. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | All Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. - Unprotected openings into stairs S1 block 2 from canteen on ground level, S2 block 3 from production on ground level, S6 & S7 (lift shaft). - Unprotected penetrations into stairs S2 block 3 all levels. - Doors not fire doors in all of the protected stairs. - Fire load in stairs S2 block 3 level ground. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F7 + 4 Month | Facility will ensure all emergency escape stairs are fire-separated from the rest of the building using 2-hour fire-resistant construction with 90-minute fire doors. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F9 | Means of Escape | Number of exits | The carton storage above dyeing hall has no proper entry exit as the occupants can only go to level 1 from cargo lift. | Review each floor and area to ensure that the number of exits complies with Accord Building Standard. Develop plan and drawings to provide additional exits where necessary. Submit the plan and drawings to Accord for review and approval prior to commencing rectification works. | 4 months | Facility will conduct a comprehensive review of each floor and area as per required number of exits. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F10 | Means of Escape | Number of exits | The carton storage above dyeing hall has no proper entry exit as the occupants can only go to level 1 from cargo lift. | Implement the above plan as agreed with Accord. Exit numbers from all floors and parts of the building should comply with Accord Building Standard. | F9 + 4 month | Facility will implement the approved exit plan as agreed with Accord Building Standard. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F11 | Means of Escape | Exit discharge | Exits from block 2, 3 and one of the exits from block 4 converge in a single point of failure as the alternative exit discharge route is blocked by B Grade temporary warehouse. | Review each building’s discharge to ensure that the number of exit discharge routes complies with Pakistan Accord Building Standard. Develop plan and drawings to provide additional exit discharge routes where necessary. Submit the plan and drawings to Pakistan Accord for review and approval prior to commencing rectification works. | 4 months | Facility will review each building’s exit discharge regarding the required number of exit discharge routes. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F12 | Means of Escape | Exit discharge | Exits from block 2, 3 and one of the exits from block 4 converge in a single point of failure as the alternative exit discharge route is blocked by B Grade temporary warehouse. | Implement the above plan as agreed with Pakistan Accord. Number of exit discharge routes should comply with Pakistan Accord Building Standard. | F11+4 months | Facility will make sure to implement the approved exit discharge plan as agreed with Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit signage | - Missing exit signs in corridors and circulation areas of block 3,4 and 6. - Missing exit signs in production areas of block 3. - Missing exit signs at both exits from site. - Exit signs are not clear / misleading in block 3 and 6. - Electrically powered exit signs are not a tested and listed system. | Remove misleading directional escape signs. | 2 weeks | Facility will ensure that all misleading directional escape signs are identified and removed. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit signage | - Missing exit signs in corridors and circulation areas of block 3,4 and 6. - Missing exit signs in production areas of block 3. - Missing exit signs at both exits from site. - Exit signs are not clear / misleading in block 3 and 6. - Electrically powered exit signs are not a tested and listed system. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | Facility will install exit signage to ensure that access to exits is clearly marked with approved, readily visible signs from all areas of the floor and at exits. |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit signage | - Missing exit signs in corridors and circulation areas of block 3,4 and 6. - Missing exit signs in production areas of block 3. - Missing exit signs at both exits from site. - Exit signs are not clear / misleading in block 3 and 6. - Electrically powered exit signs are not a tested and listed system. | Ensure that all exit signage is checked periodically and in good working condition. | F14+3 months | Facility will establish a schedule of inspection and maintenance program to ensure all exit signage remains in good working condition and is periodically checked for functionality. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Rated Construction | Separation of shafts | - Lift shafts in block 1 are not separated with fire rated construction. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Facility will prepare and submit detailed drawings to Accord for review and approval before starting work. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | F17 | Fire Rated Construction | Separation of shafts | - Lift shafts in block 1 are not separated with fire rated construction. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F16+4 months | Facility will ensure 2-hour fire-rated protection is provided to lift shafts in accordance with the layouts and documents reviewed by Pakistan Accord. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F18 | Fire Rated Construction | Separation of high-risk areas | - Electrical room in dyeing hall block 3 is not fire separated from production via a fire rated protection assemblies i.e. fire doors. - Fire pump room is not separated from ETP area via fire rated construction and protection assemblies. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | Facility will provide fire-rated protection, including fire doors, to separate the electrical room. Ensure the fire pump room is properly fire-separated from the ETP area using fire-rated construction. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F19 | Fire Rated Construction | Separation of high-risk areas | - Electrical room in dyeing hall block 3 is not fire separated from production via a fire rated protection assemblies i.e. fire doors. - Fire pump room is not separated from ETP area via fire rated construction and protection assemblies. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F18+4 months | Facility will Implement 2-hour fire-rated construction, including 90-minute fire-rated door in accordance with the layouts and documents reviewed by Pakistan Accord. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F20 | Fire Rated Construction | Separation of occupancies | - Office area not fire separated from the production area in block 3 (the door is not a fire door). | Prepare a plan and drawings showing the proposed separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Different occupancy types in the building - Proposed fire separation details (including fire rating of walls and doors) | 4 months | Facility will prepare and submit a plan and drawings to Accord for review and approval before initiating rectification work. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F21 | Fire Rated Construction | Separation of occupancies | - Office area not fire separated from the production area in block 3 (the door is not a fire door). | Provide fire rated separation between occupancies as per proposal reviewed by Pakistan Accord. | F20+4 months | Facility will implement fire-rated separation between different occupancies. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F22 | Fire Rated Construction | Floor openings | - Chutes and/or conveyor belts are not fire separated in block 3 connection ground floor to bathrobe. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings - Proposed fire separation details (including fire rating of walls and doors) | 4 months | Facility will prepare and submit a plan and drawings to Accord for review and approval before starting work. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F23 | Fire Rated Construction | Floor openings | - Chutes and/or conveyor belts are not fire separated in block 3 connection ground floor to bathrobe. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F22+4 months | Facility will implement fire-rated separation between floors as per the plan reviewed by Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Storage | Dedicated storage area not separated by fire rated construction - Storage areas are not fire separated from the rest of the building in block 3 where; finished fabric store not fire separated from production and finished fabric storage alongside knits quality inspection is also not fire separated from production. - Block 4 storage is not fire separated from block 3 production. - Block 4 high-piled storage is not fire separated from block 3 production. | Remove storage from exit discharge routes. | 2 weeks | Facility will remove all storage from exit discharge routes to ensure clear, unobstructed, and compliant emergency routes. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Storage | Dedicated storage area not separated by fire rated construction - Storage areas are not fire separated from the rest of the building in block 3 where; finished fabric store not fire separated from production and finished fabric storage alongside knits quality inspection is also not fire separated from production. - Block 4 storage is not fire separated from block 3 production. - Block 4 high-piled storage is not fire separated from block 3 production. | Identify all designated storage areas. Identify which storage areas will follow the in-process storage limitations described above and which will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details for review and approval by Accord prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | Facility will declare all designated storage areas requiring fire separation. Prepare and submit drawings to Accord for review. |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Rated Construction | Storage | Dedicated storage area not separated by fire rated construction - Storage areas are not fire separated from the rest of the building in block 3 where; finished fabric store not fire separated from production and finished fabric storage alongside knits quality inspection is also not fire separated from production. - Block 4 storage is not fire separated from block 3 production. - Block 4 high-piled storage is not fire separated from block 3 production. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F25 + 4 month | Facility will implement the approved fire separation plan on-site in accordance with the previously reviewed documentation |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F27 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Fire Extinguishers. - Inadequate records of maintenance of Fire Doors. | Prepare maintenance schedule for all life safety systems. | 3 months | Facility will implement a maintenance schedule for all life safety systems, ensuring regular inspections and testing. |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F28 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Fire Extinguishers. - Inadequate records of maintenance of Fire Doors. | - Prepare a schedule of proposed system maintenance. - Identify how systems will be maintained and who is responsible. - The schedule to be submitted to Accord for review and approval. | 3 months | Facility will make sure that proper records are maintained for the inspection, testing, and maintenance |  |  |  | In Progress
[8 empty] | Initial | [10 empty] | F29 | Fire Safety Management | Records of systems maintenance | - Inadequate records of maintenance of Fire Extinguishers. - Inadequate records of maintenance of Fire Doors. | - Ensure all systems are being maintained as per the schedule agreed with Accord. - Keep maintenance records. | F28+3 months | Facility will ensure all life safety systems are maintained according to the schedule agreed with Accord and keep accurate maintenance records. |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Safety Management | Emergency Action Plan | - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | Facility will make sure that evacuation plans are provided on each level and EAP reports are maintained. |  |  |  | In Progress
3 | 8 |  | 152 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Safety Management | Emergency Action Plan | - There is no EAP document which details procedures, roles and responsibilities in the event of fire. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F30+2 months | Facility will Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room in block 2 (fire doors missing). - Inadequate ventilation of chemical storage areas block 2. | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA 30 requirements. Prepare drawings showing the proposed chemical storage areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all chemical storage areas - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) - Ventilation provisions to each of these rooms | 4 months | Facility will make sure to collect MSDS, classify chemicals, and submit NFPA 30-compliant storage plans to Accord for approval. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Hazardous Materials | Chemicals storage | - Flammable materials are not stored in a fire separated room in block 2 (fire doors missing). - Inadequate ventilation of chemical storage areas block 2. | Implement the above plan on site. All chemical storage areas to be compliant with Accord Standard | F32+4 months | Facility will implement the approved chemical storage plan on-site, ensuring all storage areas comply with Accord Standards. |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
03 & 04-Sep-24
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [12 empty] | Zephyr Textiles Limited - 63-KM Multan Road Jumber Khurd, Tehsil Pattoki, District Kasur, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 03 & 04-Sep-2024
[22 empty] | Work Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Structural Documentation | Differs from as-built structure | This relates to the building, where the provided plans differ from the as-built structure. • The available as-built architectural drawings of block 4 do not match the actual structures of the building (location of bracing not matching with as-built). | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | Facility will update the as-built architectural drawings of Block 4 to accurately reflect the actual structure. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Structural Documentation | Documentation unavailable | This relates to whole factory. Complete as-built Structural drawings of all buildings were unavailable. | Building Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation. | 6 months | Facility will develop and maintain complete as-built structural drawings for all buildings in the factory. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Structural Documentation | Lack of safe load plans | No safe load plans were posted in the factory. | Building Structural Engineer to produce loading plans for all floors within the factory considering floor capacity and column capacity. Loading to be actively managed by Factory Management. | 6 months | Facility will prepare and display safe load plans in the factory to ensure clear guidance on load limits. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Other Damage/Defects | Column impact damage | This issue refers to Block 6. Damages observed in multiple columns which appear to be due to the impact of trolleys/vehicles. Columns were repaired previously but the material was unidentified. | Propose a remedial solution and share with the Pakistan Accord for review. | 3 months | Facility will propose a remedial solution and share with the Pakistan Accord for review. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Other Damage/Defects | Column impact damage | This issue refers to Block 6. Damages observed in multiple columns which appear to be due to the impact of trolleys/vehicles. Columns were repaired previously but the material was unidentified. | Implement the proposed and reviewed remedial measures. Continue to monitor condition of columns in highly trafficked areas | S4+3 months | Facility will implement approved remedial measures and regularly monitor column conditions in high-traffic areas. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Corrosion of reinforcement | This relates to the exposed rebars at stitching hall roof and ETP tank slab which pose a high risk of corrosion which is main concern related to exposed reinforcement of treatment tank slab. | Proposed remedial action for opening in slab to cover reinforcement and submit to Pakistan Accord for review. | 3 months | Facility will make sure that opening in the slab will be sealed with formwork and filled with approved concrete to cover the exposed reinforcement. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Other Damage/Defects | Corrosion of reinforcement | This relates to the exposed rebars at stitching hall roof and ETP tank slab which pose a high risk of corrosion which is main concern related to exposed reinforcement of treatment tank slab. | Implement the remedial works. | S6+3 month | Facility will make sure that exposed rebars at the stitching hall roof and ETP tank slab will be covered with approved concrete to protect them from corrosion. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Other Damage/Defects | Moisture ingress | This refers to the ground-floor stitching hall areas where there were signs of moisture ingress may be due to water outlets. | Building Engineer to inspect the areas which is experiencing water ingress and propose measures to prevent further damage and carry out repair works. | 6 months | The Building Engineer will inspect areas experiencing water ingress, identify the cause, and propose measures to prevent further damage. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Other Damage/Defects | Spalling concrete | This refers to the block 3 and block 4 central column where spalling of concrete and signs of seepage were visible, the main cause of spalling and cracking may be due to water ingress through water outlets at roof level. | Building Engineer to inspect the areas which is damaged and propose measures to prevent further damage and carry out repair works. | 6 months | The Building Engineer will inspect the damaged areas, propose measures to prevent further damage, and carry out the necessary repair works. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Other Damage/Defects | Health and Safety | This concerns Inadequate Edge protection at roof. The following items present a risk of potential injury resulting from slip, trip or fall from roof during the access and maintenance of services – Health & Safety concern. At the top of buildings, it is observed that access to roof lacks the edge protection, which might result in trip or fall hazard for the maintenance workers at the time of servicing. | Provide appropriate edge protection to all the roofs. | 1 month | Facility will make sure edge protection will be installed to prevent these hazards and ensure the safety of maintenance workers. |  |  |  | In Progress
No | 3 | 8 |  | 130 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 132 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 145 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 147 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 148 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 149 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 151 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 152 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## E-Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Cable size
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## F-Categories
Categories | Means of Escape | Fire Rated Construction | Hazardous Materials | Fire Suppression | Fire Safety Management
Means of Escape | Protection of stairs | Structural fire rating | Chemicals handling | Standpipe system | Fire drills
Fire Rated Construction | Number of exits | Extensive voids | Chemicals storage | Fire extinguishers | Records of systems maintenance
Fire Suppression | Travel distance | Separation of high-risk areas | Diesel storage | Fire pumps | Records of system testing
Hazardous Materials | Exit capacity | Separation of shafts | Gas storage | Sprinkler system | Staff training
Fire Safety Management | Exit access | Separation of occupancies |  | Water supply | Emergency Action Plan
| Escape stair condition | Floor openings |  | Exterior hydrants | Fire vehicle access
| Exit discharge | Storage
| Escape doors | Atrium
Exit signage

## S-Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Column impact damage
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type