## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
30-Nov-2023
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Amna Industries (Pvt.) Ltd. (Unit 2) , Plot # 184, Sector 23, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 30-Nov-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | Single Line Diagrams were not updated. | Consult a qualified engineer to design the entire Single Line Diagrams and rectify design issues. | 6 months | Factory will consult a qualified electrical engineer and provide a SLD for review by Accord |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | As-built Layout drawings were not updated. | Consult a Qualified Engineer complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing, consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. | 8 months | Factory will complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation for review by Accord |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | DBs & Elec Protection Systems | Hot Spots | Thermographic & Insulation Test Reports were not provided. | Building electrical engineer to prepare Thermographic & Insulation Testing report and submit to Pakistan Accord for review | 6 months | Factory electrical engineer will prepare Thermographic & Insulation Testing report and submit to Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | DBs & Elec Protection Systems | Earthing system | Earth testing report were not available on site. | Building electrical engineer to prepare Earth testing report and submit to Pakistan Accord for review report | 1 month | Factory electrical engineer to prepare Earth testing report and submit to Pakistan Accord for review report |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | Lightning protection system is not installed in the facility. Any document related to LPS assessment was not presented. | Risk assessment for Lightning Protection System should be carried out by qualified engineer and design system accordingly if required. | 6 months | Factory will prepare risk assessment and if LPS required, submit drawings with proposed design to Accord for review. Once installation complete and tested Factory will provide Accord with as-built drawings of LPS system |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | Maintenance records were not updated. | Maintenance records shall be maintained periodically. | 6 months | Maintenance records will be kept on site for inspection by Accord maintained periodically. |  |  |  | Pending Verification
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Earthing system | Body earthing missing from the metical frame of the panels. This was noted in several locations. | Connect all metal bodies of electrical panels to the earth terminals within electrical panels. | 6 months | All metal bodies of electrical panels will be connected to the earth terminals within electrical panels. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Circuit breakers | There is cross-circuiting (Looping, Bunching at Molded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. | For any future work avoid looping and bunch of cable at MCCB/MCB or bus bar terminal, use individual circuit and overcurrent device for every incoming and outgoing circuit at the distribution boards. | 1 month | Factory will review cable arrangement to identify where looping occurs |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Circuit breakers | There is cross-circuiting (Looping, Bunching at Molded Case Circuit Breaker/ Miniature Circuit Breaker (MCCB/MCB) or Bus bar terminal) observed in the panels. | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels. | 3 months | Factory will modify the installation so that circuits do not share breakers. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Lint & dust inside panel board | It was noted in several locations that the cleanliness was not being maintained within the electrical panels | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt. | 1 month | Monthly cleaning checklist has been developed and will be shared with Accord |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Lint & dust inside panel board | It was noted in several locations that the cleanliness was not being maintained within the electrical panels | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 1 month | All DBs and main panels are being cleaned accordingly. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Panel/cabling/busbar | An electrical panel was not externally rated and is showing signs of water ingress and rusting. | For water ingress protection replace provide IP rated covers prevent water reaching the existing panel. | 2 months | Factory will provide IP rated covers to prevent moisture reaching panel |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | Cabling & Wiring | Cables support and protection | It was noted in several location where electrical cables were not installed correctly and not provided adequate protection from physical damage. | Provide protection to prevent cables being walked on that could cause damage to the cables. | 3 months | All loose wiring has been fixed |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | Cabling & Wiring | Cables support and protection | It was noted in several location where electrical cables were not installed correctly and not provided adequate protection from physical damage and correct containment. | Secure all cables and provide correct cable containment. | 3 months | All loose wiring has been fixed |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | Cabling & Wiring | Splicing of cables | It was noted in several locations throughout the facility where the flexible cables for equipment have been cut and / or damaged. The cables have been jointed back together using an unsuitable method. | Replace the affected cables with: - continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or - use joint boxes and appropriate connectors to joint cables. | 4 months | All damage cables has been replaced and fixed properly |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | Cabling & Wiring | Colour coding | It was observed that incorrect cable colors (green, pink, and turquoise) are being used instead of the standard red, yellow, and blue in multiple locations throughout the facility. The use of incorrect cable colours in electrical wiring can lead to confusion and potential safety hazards. | As there is a mix of old and new wiring colours, the cables should be clearly marked with the relevant colour codes to prevent incorrect application of the phase and neutral. | 2 months | Factory will replace incorrectly coloured wiring so that all wiring has correct colour coding |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Lint & dust inside panel board | Combustible material found near multiple electrical devices. | Remove all combustible material from within and around all electrical panels in the facility and ensure that all electric circuitry is clear of combustible materials. | 1 month | Combustible material has been removed |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Lint & dust inside panel board | Combustible material found near multiple electrical devices. | Remove combustible material away from electrical devices | 1 month | Combustible material has been removed |  |  |  | Pending Verification
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Openings | In several locations throughout the facility electrical panels openings are not correctly sealed. | Seal all openings in electrical panels (using plates and cable glands) to prevent the ingress of dust and dirt. | 3 months | Factory will seal all openings in electrical panels |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Circuit breakers | The rating of protective devices have been covered over. | Accurately label and mark breaker sizes for clear identification and ensure that they are captured on the SLD. | 3 months | Factory will accurately label and mark breaker sizes for clear identification and ensure that they are captured on the SLD |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | DBs & Elec Protection Systems | Circuit breakers | Main Building on level(s) L00 - Ground Floor. There is a downstream transition from a 100A breaker to a 16A breaker. Cable connection size to breaker is incorrect and cable requires protection (0.75mm2 cable to 20A breaker) | Consult a qualified engineer to review the entire installation and advise the correct breaker sizes. Check cable connection size to breaker is correct and ensure cable is protected. | 3 months | Factory will consult a qualified engineer to review the entire installation and advise the correct breaker sizes. Factory will change cable size/ breaker to suit. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | DBs & Elec Protection Systems | Earthing system | Earthing connections are missing from panel. | Connect all earth cables into earthing terminals within panels. | 6 months | Factory will connect all earth cables into earthing terminals within panels |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | DBs & Elec Protection Systems | Adequate accessibility | Main Building on level(s) L00 - Ground Floor. Structure and piping in front of the electrical panel is obstructing fully opening the panel door, limiting access to panel | Ensure obstructions to electrical panel door are removed, enabling the panel door to open fully and providing access for maintenance and operational purposes | 1 month | Factory will ensure obstructions to electrical panel door are removed |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Cabling & Wiring | Cables support and protection | Cables not installed correctly in electrical panel. | Reinstall and secure the cables correctly to prevent movement. | 3 months | Factory will install cables correctly |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Circuit breakers | Main Building on level(s) L02 - 2nd Floor: There is no main breaker in the electrical panel | Install a main breaker in the panel to allow shutdown of all power, enabling isolation during maintenance, emergencies, or in the event of a fault. | 3 months | Factory will install a main breaker in the panel to allow shutdown of all powe |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Cabling & Wiring | Cables support and protection | Main Building on level(s) -L00 – Ground Floor and Roof: Electrical sockets located beside generator and at roof level are not IP rated | All external electrical components must be IP rated for protection against environmental factors. Ensure wiring to socket is continuous and enclosed in weatherproof conduit to prevent exposure. Replace the damaged socket. | 3 months | All external electrical components will be IP rated for protection against environment |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | DBs & Elec Protection Systems | Circuit breakers | Main Building on level(s) L02 - 2nd Floor: Breaker for AC in the production manager's office is in the riser and is in poor condition on the floor. The cables are not correctly fixed to place to prevent movement. | Mount the breaker in an appropriate location, ensuring it is at high level and secure all cables to a method of cable containment | 3 months | Factory had removed unnecessary breaker and the cables. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L01 - 1st Floor: There are signs of distress at the cable termination | Inspect the electrical panel to identify the source of distress to cable, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause which may involve tightening connections, redistributing loads, or replacing faulty components. | 03 months | Damage cable has been removed. |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L03 - Rooftop: Cable connecting to the motor is passed from external area on the roof through a window to an internal area | Reroute the cable from the external area on the roof to the internal area through proper conduit or cable tray | 03 months | Cables will be re-routed through proper conduits |  |  |  | Pending Verification
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L00 - Ground Floor: Exposed wiring in cable conduit, located beside generator | Cover electrical connections using suitable insulating material. | 03 months | Factory will cover all electrical connections using suitable insulating material |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L00 - Ground Floor: External cables to the generator lack proper cable support leading to sharp bends. This also causes is tension on cable terminations due to additional weight on bolts .Openings are not correctly sealed on the frame, where the cable is running, | Provide cable tray support for the cables, install cable glands, and seal all openings in the frame. | 03 months | Factory will provide adequate support trays for cables |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L01 - 1st Floor: Damaged electrical equipment has not been replaced. It was observed that a socket on the wall is loosely fitted and damaged. | Equipment should be isolated from the electrical distribution system (turned off). If the equipment is required to operate it should be replaced before doing so. | 01 month | Damage electrical equipment has been replaced, socket also properly been fitted. |  |  |  | Pending Verification
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L01 - 1st Floor: Cables are not correctly fixed in place to prevent movement | Fix conduits to the cable supports | 03 months | Support clamps have been installed. |  |  |  | Pending Verification
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Cabling & Wiring | Cables support and protection | Main Building on level(s) L01 - 1st Floor: Support clamps required to conduits | Add U-shaped supports to conduits along walls | 03 months | Factory will provide adequate supports for conduits |  |  |  | Pending Verification
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Emergency Lighting | Provided but insufficient | Inadequate Emergency lighting throughout all buildings: - Emergency lighting provided but did not function in test - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs - No emergency lighting in some areas 1. No emergency lighting on roof areas 2. Very few lights in the rooms on the roof | Regularly test the emergency lighting system on each floor | 03 months | Regularly test emergency lighting on each floor and kept test records on site for review by Accord |  |  |  | Pending Verification
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Emergency Lighting | Provided but insufficient | Inadequate Emergency lighting throughout all buildings: - Emergency lighting provided but did not function in test - Adequate illumination levels are not provided by emergency lighting along egress routes and/or at exit stairs - No emergency lighting in some areas 1. No emergency lighting on roof areas 2. Very few lights in the rooms on the roof | Provide emergency lighting in accordance with Pakistan Building Code and NFPA 101. | 03 months | Emergency lighting system will be upgraded to meet Pakistan Accord Building Standard and maintained in proper working condition. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | Fire detection and alarm system not being consistent with acceptable standards. Some of the related issues include: - Not a listed system so it does not provide alarm and notification features consistent with acceptable standards. - Incomplete coverage of fire alarm devices in some areas, especially on Ground Level - Fire alarm devices not listed (to be confirmed) - Detectors incorrectly installed which could cause delayed activation. - Detectors not installed above suspended ceiling - Detectors not installed top of stairs - Sounders inaudible due to low volume or high ambient noise (e.g., low audibility on Ground Level staircase, one enclosed office, emergency exit and warehouse area, low audibility on Level 1 in the account department and product development room, low audibility in centre production area and office area of Level 2, no audibility at sampling area on Level 2, almost no audibility on roof ) | (1) Submit design documentation for upgrading of current system or new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | 03 months | Factory will appoint consultant and submit design documentation for a fire alarm & detections system (FADS) and submit to Pakistan Accord for review before purchasing any new equipment |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E37 + 1 month | If any new listed components need to be purchased Factory will submit documentation to Accord showing that an L/C has been opened |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E38 + 4 months | Once all materials have been in-housed Factory will advise Accord that all materials are available on-site and start installation |  |  |  | In Progress
3 | 8 |  | 149 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E39 + 5 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 150 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E41 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E41 + 3 months | Factory will advise Accord when the FADS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 151 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E42 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire detection and alarm system (FADS) was observed as not being consistent with acceptable standards. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E42 + 3 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
30-Nov-2023
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Amna Industries (Pvt.) Ltd. (Unit 2) , Plot # 184, Sector 23, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 30-Nov-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed in several locations within the building and along the exterior exit discharge pathways. | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | Factory has removed the all locking devices. Factory has permanently lock the grill gate with the chain at the time of duty hours. The extra door was installed, but now its removed |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge points. Doors on escape routes leading to outside or away from the building must not have locking devices, must have mechanisms that allow easy opening from inside without lock or key and must swing in the direction of travel to an emergency exit. Locking mechanisms were observed in several locations within the building and along the exterior exit discharge pathways. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Factory will provide easily opening mechanisms on doors on all escape routes, that are openable from the inside in the direction of travel |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | Doors on all escape routes, including those leading to outside or away from the building or doors serving a single room with an occupancy capacity of more than 50 people, must swing in the direction of travel to an emergency exit. Several doors on escape routes, including the examples below, were observed to swing in the wrong direction (inwards). | Replace exit doors with doors swinging in the direction of egress travel and in accordance with Pakistan Accord Building Standard | 3 months | There was a two way door used for the both direction inward and outward. Factory had removed all locking devices from the door. |  |  |  | Pending Verification
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | Sliding exit doors observed where only swinging doors provide an acceptable level of risk. | Replace sliding door(s) with side hung swinging door(s) or provide a side hung pocket door within the sliding panel, that swings in the direction of egress travel | 3 months | Factory will replace sliding doors with swing doors, provide bypass doors nearby or pocket doors built into the existing sliding door |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Number of exits | This relates to areas where a single means of egress is provided, but more than one means of escape is required. This was observed in the canteen on Level 2. | Propose alternative means of egress from the areas identified to ensure there are sufficient number of exits and sufficient exits to accommodate the occupant load and travel distance requirements, in accordance with the Pakistan Accord Building Standard and Submit proposals to Pakistan Accord for review. | 4 months | In areas where number of exits is insufficient, factory will prepare drawings showing proposed alternative exits and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Number of exits | This relates to areas where a single means of egress is provided, but more than one means of escape is required. This was observed in the canteen on Level 2. | Provide alternative means of egress from the areas identified by implementing proposal submitted earlier to Pakistan Accord for review. | F5 + 4 months | Factory will ensure two exits are available there. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Combustible materials stored in stairway | Remove all combustible materials stored in stairways. | 1 months | Factory will remove all combustible materials from stairways |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Exit stairways not protected by fire and smoke resistant construction and openings protective assemblies, e.g., fire doors - Exit stairway exposed to unprotected openings | Submit design documentation to the Pakistan Accord showing the planned changes to meet the requirements. | 4 months | Factory will prepare drawings showing proposed fire separating construction and door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | Exit stairways, which are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies, i.e., fire doors. The following is a non-exhaustive list of issues during the inspection relates to the inspected buildings: - Automatic door closers are not installed/functioning in several locations | Provide all fire doors with self-closing and self-latching devices, and push-bar panic hardware where required in accordance with Pakistan Accord Building Standard. If fire doors are required to be held open for functional reasons, install magnetic hold-open devices that release on activation of fire alarm system. | F8 + 4 months | Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed on Levels 1 and 2 where office areas and the canteen need to escape via the production area for their second means of escape | Propose modifications to exit where required from production areas without having to pass through other higher risk areas and submit to Pakistan Accord for review. | 4 months | Factory will prepare drawings showing propos for escape route that does not pass through a higher risk area and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit access | Exit access through higher risk intervening spaces, observed on Levels 1 and 2 where office areas and the canteen need to escape via the production area for their second means of escape | Arrange exit access so that it is not necessary to pass through any hazardous areas as per Pakistan Accord Building Standard. | F10 + 4 months | Alternative access to exits will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior and exterior stairways to public way are exposed to unprotected openings | Remove any exterior storage within 3.05m horizontally and vertically of unprotected openings and ensure that necessary widths of discharge routes are not compromised. | 1 month | Factory will remove all combustible materials from within 3.05m horizontally and vertically of unprotected openings |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior and exterior stairways to public way are exposed to unprotected openings | Propose means for providing protected routes from exits and escape stairs away from the building and submit to the Pakistan Accord for review. | 4 months | Factory will prepare drawings showing proposal to protect external exit routes, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit discharge | Exit discharge routes outside the building, which are not protected from adjacent hazards by fire and smoke resistant construction. Exit discharge pathways from interior and exterior stairways to public way are exposed to unprotected openings | Protect exit route at exterior of the building from unprotected openings to allow a safe, free and unobstructed passage away from the building in accordance with the Accord Pakistan Building Standard. | F13 + 4 months | Protection of external escape routes will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Escape stair condition | Handrails not being provided on the main exit stair, which can cause falls during evacuation | Provide handrails on both sides of emergency exit stairs in accordance with Pakistan Accord Building Standard | 2 months | Factory will provide handrails on both sides of emergency exit stairs in accordance with Pakistan Accord Building Standard |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Fire Rated Construction | Separation of shafts | Lift shafts and service shafts which penetrate floor that are not protected by fire and smoke resistant construction (see report for examples) that allow fire and smoke spread between floors. | Submit proposal for fire protection of lift shaft openings to Pakistan Accord for review. | 4 months | Factory will prepare drawings showing proposal for fire rated construction to separate shafts, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Fire Rated Construction | Separation of shafts | Lift shafts and service shafts which penetrate floor that are not protected by fire and smoke resistant construction (see report for examples) that allow fire and smoke spread between floors. | Separate lift shaft by fire-rated construction with fire rated opening protective assemblies, in accordance with Accord Pakistan Building Standard, implementing the previously reviewed design proposal | F17 + 4 months | Fire rated separation of shafts will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Where one occupy type is 10% or less of the floor area of a floor area they can be regarded as “incidental” to the main occupancy and do not need to be fire separated from that occupancy. Occupancies observed that may not be incidental and are not separated by fire and smoke resisting construction are as follows (non-exhaustive): - Different occupancy types not separated by fire and smoke resisting construction (Prayer area,office and production area Level 2) | Propose design and layout showing how different occupancies can be rearranged and/or enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | Factory will prepare drawings showing proposal for fire separating construction to separate occupancies, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Where one occupy type is 10% or less of the floor area of a floor area they can be regarded as “incidental” to the main occupancy and do not need to be fire separated from that occupancy. Occupancies observed that may not be incidental and are not separated by fire and smoke resisting construction are as follows (non-exhaustive): - Different occupancy types not separated by fire and smoke resisting construction (Prayer area,office and production area Level 2) | Separate different occupancy types by 2-hr fire-rated construction with 1.5-hr opening protective assemblies as per reviewed design. | F17 + 4 months | Factory will prepare drawings showing proposal for fire separating construction to separate occupancies, and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Fire Rated Construction | Separation of occupancies | Separate different occupancy types by fire and smoke resisting construction and opening protective assemblies. Occupancies observed that may not be incidental and are not separated by fire and smoke resisting construction are as follows (non-exhaustive): - Unsealed penetrations and openings are located in fire-rated separating assemblies (storage and canteen areas, production and office areas on Levels 1 & 2).. | Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated. | 4 months | Fire rated separation of occupancies will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Fire Rated Construction | Storage | Miscellaneous (in process) storage in non-storage occupancies is acceptable provided that: - Miscellaneous (in process) storage areas do not exceed 10 percent of the floor are - Miscellaneous (in process) storage areas do not exceed 2.45m (8ft) in height - Miscellaneous (in process) storage areas do not exceed 23m² (250ft²) in one area - Miscellaneous (in process) storage areas are separated from other storage areas by at least 3m (10ft) | Propose design and layout showing how storage cannot be re-arranged so that it complies with the limitations given for in-process storage, it will be enclosed with fire rated construction and submit documentation to Pakistan Accord for review | 4 months | Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations and how larger storage areas need to be separated, and submit to Accord for review. |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Fire Rated Construction | Storage | Miscellaneous (in process) storage in non-storage occupancies is acceptable provided that: - Miscellaneous (in process) storage areas do not exceed 10 percent of the floor are - Miscellaneous (in process) storage areas do not exceed 2.45m (8ft) in height - Miscellaneous (in process) storage areas do not exceed 23m² (250ft²) in one area - Miscellaneous (in process) storage areas are separated from other storage areas by at least 3m (10ft) | Where storage areas cannot be rearranged to meet “in-process” requirements set out above, separate storage with 2-hr fire-rated construction and with 1.5-hr opening protective assemblies. Maintain fire ratings by sealing all penetrations and openings with a firestop system or device of at least 1 hour rating, but not less than the fire resistance rating of the assembly penetrated | F21 + 4 months | Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Electrical room not separated by fire and smoke resisting construction | Separate electrical room by 2-hr fire rated construction. | 4 months | Fire rated separation of high-risk areas will be provided, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Pump room/house not separated by 2-hr fire rated construction or 50-ft (5.3m) separation from adjacent buildings. | Separate pump room/house by 2-hr fire rated construction or 50-ft (5.3m) separation from adjacent buildings. | 4 months | Fire rated separation of high-risk areas will be provided, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Separation of high-risk areas | Separate high-risk plant areas from other areas by fire and smoke resisting construction and opening protective assemblies. - Rooms with boilers and/or steam generators not separated by fire and smoke construction - Exterior generator not separated from adjacent exterior exit discharge pathway by fire and smoke resisting construction | Separate room with boiler(s) and/or steam generator(s) by 2-hr fire rated construction. | 4 months | Fire rated separation of high-risk areas will be provided, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Hazardous Materials | Chemicals handling | Storage, handling, and use of flammable and combustible liquids | Factory to collect MSDS sheets for all chemicals stored, classify materials, and propose storage arrangements to meet NFPA requirements. These requirements may include limiting storage quantities and providing fire rated separations in accordance with the Pakistan Building Code and NFPA 30. | 4 months | The empty paint bucket has been removed from the area Factory will provide Data Sheets (MSDS) for all chemicals, including their identifications. Factory will share inventory of MSDS sheets with Accord for review |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Hazardous Materials | Gas storage | Presence of a gas cylinders inside the buildings inspected | Up to two (2) gas cylinders (each 50 kg maximum) are permitted to be stored in an interior control area if the cylinders are adequately secured and the room is appropriately ventilated and protected as per NFPA 58. Ventilation must be direct to outside meaning the room needs to have at least one exterior wall, which cannot be adjacent to exterior exits or exterior exit discharge pathways. Protection refers to 2-hr fire rated separation of the room with cylinders and assuring the cylinders and their storage room is not within 3.05 meters of an escape route or exit. | 3 months | The gas cylinder tied together with the chain lock and proper ventilation |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
30-Nov-2023
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Amna Industries (Pvt.) Ltd. (Unit 2) , Plot # 184, Sector 23, Korangi Industrial Area, Karachi, Pakistan
[8 empty] | Date of Initial Inspection | [12 empty] | 30-Nov-2023
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Structural System | Lateral stability system | This relates to the main production building, for which there is no clearly defined lateral stability system. Lateral stability seems only to be addressed through moment frame action between the flat slab with drop down panels and moment connection to the columns. Diagonal cracks in the non-structural blockwork walls were observed at a few locations, which leads us to believe that the lateral stability system may need strengthening. | Structural Engineer to carry out building stability analysis against the lateral loads and propose additional stability system if required. Submit results of stability analysis and any proposed remediation measures (if required) to Pakistan Accord for review before undertaking the works. | 3 months | Factory will appoint a structural engineer to assess the lateral stability of the existing structure, and propose additional stability remediation if required and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Structural System | Lateral stability system | This relates to the main production building, for which there is no clearly defined lateral stability system. Lateral stability seems only to be addressed through moment frame action between the flat slab with drop down panels and moment connection to the columns. Diagonal cracks in the non-structural blockwork walls were observed at a few locations, which leads us to believe that the lateral stability system may need strengthening. | If building has adequate lateral stability system then repair cracking to brickwork infill walls. If lateral stability system needs strengthening, then implement the proposed remediation measures as reviewed and in accordance with Pakistan Accord Building Standard | S1+4 months | If lateral stability found to be insufficient, then implement the remedial works according to proposals reviewed by Accord. If lateral stability system found to be adequate, repair cracked brickwork |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Cracking | Beams | This relates to the main roof level, where horizontal cracking was observed at multiple locations. These cracks appear to be within the plaster/render of the RC beam, however, some of the cracks are clearly wider than others and may be affecting the lateral stability of the parapet beams. | Remove sections of plaster finish from the beams at the locations of cracks and investigate if cracks penetrate the RC beams. If cracks penetrate through the RC beams, Building Engineer to investigate cause of cracking and identify appropriate remediation. Submit the design assessment and the proposed remedial works to the Pakistan Accord for review. | 2 months | Factory will appoint an engineer to investigate whether cracking affects the structural performance of the parapet beams, and if so propose remedial measures and submit to Accord for review. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Cracking | Beams | This relates to the main roof level, where horizontal cracking was observed at multiple locations. These cracks appear to be within the plaster/render of the RC beam, however, some of the cracks are clearly wider than others and may be affecting the lateral stability of the parapet beams. | Carry out remediation works or repair cracks if shown to be within the plaster only. | S3+ 3 months | If cracking is only superficial, repair plasterwork, otherwise complete remedial work as per proposal submitted to Accord previously for review |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Other Damage/Defects | Moisture ingress | This relates to the North vertical extension at the roof, where moisture ingress to precast beams and ceiling panels appears to be causing deterioration of structural elements. Bottom reinforcement in the precast slab tiles is rusted and appears to be in poor condition at some locations. Cracks also observed on the top surface of precast beams. | Precast slab tiles: Propose remedial measures to prevent further damage to the slab. Precast beams: Building structural engineer to investigate cracks in the beam and ensure that the bearing provided by the beams for the precast tiles is adequate. If not then propose remedial works so that the precast tiles have sufficient bearing. Submit proposals to Pakistan Accord for review before undertaking remedial works to the beams. | 3 months | Factory will appoint an engineer to investigate causes of moisture ingress and repair to avoid further ingress. Propose measures to repair structural damage and submit to Accord for review. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Moisture ingress | This relates to the North vertical extension at the roof, where moisture ingress to precast beams and ceiling panels appears to be causing deterioration of structural elements. | Complete any remedial work required to address the deterioration of the structural elements. | S5 + 3 months | Factory will complete remedial works to damaged structural elements |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural System | Lateral stability system | This relates to the North vertical extension at roof, for which no lateral bracing system was observed. Neither vertical nor horizontal bracings were observed for the steel frame to ensure stability of this structure under extreme wind loading. | Building Engineer to verify welded connection between all steel beam & column connections (North & South). Submit the site investigation results to Pakistan Accord for review. | 3 months | Factory will appoint an engineer to investigate steel beam to column connections and propose strengthening measures in needed. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural System | Lateral stability system | This relates to the North vertical extension at roof, for which no lateral bracing system was observed. Neither vertical nor horizontal bracings were observed for the steel frame to ensure stability of this structure under extreme wind loading. | Building Engineer to carry out stability analysis against the lateral loads for the North roof extension structure and propose additional stability system if required. Submit proposals for bracing system if required to Pakistan Accord for review. | 3 months | Factory will appoint an engineer to assess stability against lateral loading of North roof extension, and submit proposals for bracing system if required to Pakistan Accord for review . |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Structural System | Lateral stability system | This relates to the North vertical extension at roof, for which no lateral bracing system was observed. Neither vertical nor horizontal bracings were observed for the steel frame to ensure stability of this structure under extreme wind loading. | Implement a lateral bracing system as required. | S8+4 months | Factory will provide lateral bracing if required |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Loading | Uncontrolled loading | This relates to the main production building. No indication of design loading capacity by means of safe load plans was found anywhere in factory. Uncontrolled loading was observed in various locations on 1st Floor and Roof | Building Engineer to produce loading plans for all floors within the factory giving consideration to floor capacity and column capacity. Loading plans are to be displayed on the walls of each floor level. Loading to be actively managed by Factory Management. | 3 months | Factory will appoint building Engineer to produce safe loading plans for all floors within the factory |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S11 | Structural Design | Undocumented extension | Portions of the roof are vertically extended with steel & masonry over the North & South areas. Structural layouts are missing for this vertical extension. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | Factory will appoint building Engineer to produce accurate and complete as-built drawings for the building |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1