## Electrical
[9 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
24-Jul-24
Corrective Action Plan - Electrical
[9 empty] | Factory Name & Address | [12 empty] | Union Fabrics (Pvt.) Limited - Stitching, Plot # D-14/C-1, Bara Board SITE, Karachi Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 24-Jul-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Sub-station room layout drg | Substation room layout drawings were not available for the factory. | Develop detailed substation room layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 3 months | Proposal will be taken from different Engineering Firms who will provide quotations, after careful review of their proposals, a professional engineering firm will be hired for designing of sub-station room layout. It will be ensure that all critical equipment and pathways should be accurately documented. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Sub-station room layout drg | Substation room layout drawings were not available for the factory. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | E1 + 1 month | It has been decided that a circular/memo will be issued to the concerned personnel within the factory informing them that in case if there is any change or changes in electrical equipment or devices same will be informed to the Electrical Engineer via memo who will develop proposed electrical drawing, get the same approved and SLD will be created. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Single Line Diagram (SLD) | electrical single-line diagrams (SLDs) for the factory were missing some vital information and also did not match the existing installation. | Develop comprehensive electrical single-line diagrams for the entire facility following the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 months | We are Editing the SLD diagrams and putting in all the vital information. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | electrical single-line diagrams (SLDs) for the factory were missing some vital information and also did not match the existing installation. | Implement a regular review and update process for the single-line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | E3 + 1 month | We're developing an SOP document that will have a date for regular review and update for it. We will train maintenance personnel on how to interpret and utilize it. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | Diagrams & Drawings | Electrical layout drawing | it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. | Develop comprehensive electrical layout drawings following the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 8 month | It has been decided that from now onwards all electrical layouts will be included in SLD and electrical network diagram as per suggested standard. Quotations are being taken and same will be taken up. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | Diagrams & Drawings | Electrical layout drawing | it was noted that the factory lacked electrical layout drawings - including small power layouts, lighting layouts, and containment layouts. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | E5 + 1 month | Electrical management system has been updated/upgraded Systems department has been asked to follow the same. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Circuit breakers | multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. This issue was observed in the main LT panel and Fire hydrant panel. | Evaluate the breaker ratings and cable sizes for all circuits in the facility According to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable current carrying capacity. If the breaker has adjustable settings, it must be configured to allow current within the cable ampacity after applying derating factors. | 3 months | Standard BS 7671 has been procured and same will be evaluated to ensure check the same. Third party professional will be hired to do the same. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. This issue was observed in some locations including, the ground floor of utility building DB, and 1st floor main DB | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature, as illustrated in the example images below. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring the safe and reliable operation of the electrical systems. | 1 month | It has been decided that company will procure 1 temperature meter and mechanism for the inspection has been prepared in electrical management system. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Hot Spots | The survey identified numerous hot spots within panels and distribution boards. This issue was observed in some locations including, the ground floor of utility building DB, and 1st floor main DB | Regular thermographic inspections should be incorporated into the maintenance schedule every 6 months to proactively manage and mitigate the risks associated with overheating. | E8 + 6 months | Same has been regularized in the electrical management system. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | DBs & Elec Protection Systems | Earthing system | The main earth terminal was installed at an unsuitable location. The earthing cables were not appropriately sized According to the relevant earthing standards. Equipotential bonding for the cable trays was missing. The number of earth wires did not match the number of phase wires. This can be due to the cable joints in earth wires. These issues were observed throughout the facility. It is imperative to implement remedial actions across the entire facility to ensure safety and compliance. | Design and evaluate the earthing system installation throughout the facility. Replace all earthing cables with appropriately sized cables as per the requirements of BS 7671 18th Edition + A2 (2022) Appendix 4, Section 5. Verify that all earthing conductors meet the minimum cross-sectional area specified. Implement equipotential bonding for all cable trays to comply with BS 7671 Regulation 411.3.1.2. Ensure all exposed conductive parts are bonded to the main earthing terminal. Every circuit should have its independent earth wire. Ensure that there is no Multilooping or jointing of earth wires. Relocate earth terminal to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54 | 6 months | Quotation has been taken from different vendors to properly design and evaluate earthing system. As standard BS 7671 has been procured. Same will be taken up. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | The main earth terminal was installed at an unsuitable location. The earthing cables were not appropriately sized According to the relevant earthing standards. Equipotential bonding for the cable trays was missing. The number of earth wires did not match the number of phase wires. This can be due to the cable joints in earth wires. These issues were observed throughout the facility. It is imperative to implement remedial actions across the entire facility to ensure safety and compliance. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 6 months | After proper work on earthing system. Inspection and maintenance will be carried out. Systems department has preparing the document in coordination with electrical engineering team and Electrical Management System is being prepared. Same will be implemented. |  |  |  | In Progress
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Multiple Connections | Multilooping was observed in several electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. This issue was observed in every main DB of each floor. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each circuit following Section 430 of BS 7671 18th Edition + A2 (2022) | 3 months | Assessment is being carried out. Upon completion same will be updated. |  |  |  | In Progress
[20 empty] | E13 | DBs & Elec Protection Systems | Openings | Openings were discovered in the main electrical panels. This issue was observed at LT panel room. | Corrective actions are required to seal all openings to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 3 months | Assessment is being carried out. Upon completion same will be updated. |  |  |  | In Progress
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Openings | Openings were discovered in the main electrical panels. This issue was observed at LT panel room. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure that there are no openings and that the IP ratings of the panels remain uncompromised. | 6 months | Electrical management system has been updated/upgraded Systems department has been asked to follow the same. |  |  |  | In Progress
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in some of the distribution boards & panels. This issue was observed in the electrical panels in lift room 1 & 2. | All electrical panels and trunking runs shall be inspected and cleaned of any dust or lint in Accordance with Section 522.4.2 of BS7671 18th Edition + A2 (2022) | 1 month | Standard has been procured. Electrical management system is being prepared in regards to inspection and maintenance of the same. |  |  |  | In Progress
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Lint & dust inside panel board | The inspection revealed a significant accumulation of lint and dust in some of the distribution boards & panels. This issue was observed in the electrical panels in lift room 1 & 2. | A regular maintenance procedure shall be established to ensure routine inspection and cleaning of all electrical panels and trunking runs. This will prevent the accumulation of lint and dust, thereby maintaining the safety and efficiency of the electrical systems. | 3 months | Standard has been procured. Electrical management system is being prepared in regards to inspection and maintenance of the same. |  |  |  | In Progress
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | No lightning protection system was installed, and there was no risk assessment provided to confirm whether it is required or not. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment. This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 2 months | The vendor which has installed lightning protection system has been asked to provide risk assessment. |  |  |  | In Progress
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | No lightning protection system was installed, and there was no risk assessment provided to confirm whether it is required or not. | If the risk assessment concludes that an LPS is necessary, proceed with the design and installation of an appropriate system in compliance with relevant standards such as BS EN 62305 (Protection against Lightning). | 6 months | Lightning protection system has been installed. Drawings and technical sheets are available for review. |  |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire alarm system was found non-addressable, non-listed, having incomplete detection coverage throughout the facility. | Submit design documentation for upgrading of current or new replacement FADS system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | New fire alarm system has been designed as per suggested standard. Attached for review. In addition technical sheets of chosen brand also attached. |  |  |  | In Progress
No | 3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire alarm system was found non-addressable, non-listed, having incomplete detection coverage throughout the facility. | Submit documentation to the Pakistan Accord showing that an L/C has been opened for the import of any components required for the FADS design submitted earlier. | E19 + 1 month | Pending, upon approval same will be shared. |  |  |  | In Progress
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire alarm system was found non-addressable, non-listed, having incomplete detection coverage throughout the facility. | Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | E20 + 4 months | Pending, upon approval same will be shared. |  |  |  | In Progress
No | 3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire alarm system was found non-addressable, non-listed, having incomplete detection coverage throughout the facility. | Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | E21 + 5 months | Pending, upon approval same will be shared. |  |  |  | In Progress
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire alarm system was found non-addressable, non-listed, having incomplete detection coverage throughout the facility. | Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | E22 + 3 months | Pending, upon approval same will be shared. |  |  |  | In Progress
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | The fire alarm system was found non-addressable, non-listed, having incomplete detection coverage throughout the facility. | Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | E23 + 3 months | Pending, upon approval same will be shared. |  |  |  | In Progress
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | Emergency Lighting | Provided but non-functional | emergency lighting was provided but not functional in the canteen area. | Conduct a thorough inspection of all emergency lighting units throughout the facility to identify specific locations and units that are non-functional. This involves checking both the lights and the power sources, including batteries and wiring connections. Repair any faulty emergency lighting units immediately. If repair is not feasible, replace the defective units with new, compliant emergency lighting fixtures to ensure they provide adequate illumination during an emergency. | 2 months | All installed emergency lights are checked and issues has been rectified on immediate level. Also system has been prepared, technical people are trained to check and rectify issues as per decided period. | Done |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Emergency Lighting | Provided but non-functional | emergency lighting was provided but not functional in the canteen area. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | Reference to our internal documentation system Document No. UF-FHS-03-008 of Fire & Health Safety Management System has been revised as per standard. Same has been attached for review. | Done |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Emergency Lighting | Provided but insufficient | 1st floor and 2nd floor lack sufficient emergency lighting coverage. | Conduct a comprehensive survey to identify areas lacking adequate emergency lighting. Install additional emergency luminaires in these areas to meet the coverage requirements specified in the Building Code of Pakistan Fire Safety Provisions 2016, ensuring sufficient illumination for safe evacuation. | 3 months | Designing of emergency light as per suggested standard has been carried out. Designing document (As-built) and technical sheet of emergency lights attached for review please. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Emergency Lighting | Provided but insufficient | 2nd floor and 2nd floor lack sufficient emergency lighting coverage. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | Inspection and maintenance procedure UF-FHS-04-008 has been revised. Available for review. | Done |  |  | In Progress
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Emergency Lighting | Provided but insufficient | The backup power supply to the emergency luminaires is insufficient in few areas. | Upgrade the backup power supply to ensure it can adequately support all emergency luminaires during a power failure. This includes installing additional battery packs or generators as necessary to comply with the Building Code of Pakistan Fire Safety Provisions 2016 | 6 months | Additional batteries are provided to maintain the emergency lights and exit signages. Same has been put up in the SOP of availability of spare batteries for both emergency lights and exit signs. | Done |  |  | In Progress
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Emergency Lighting | Provided but insufficient | External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations. | Install external emergency luminaires to enable safe evacuation during hours of darkness to a safe place outside the building(s) | 6 months | Designing of emergency luminaries as per suggested standard has been carried out. Designing document (As-built) and technical sheet of emergency lights attached for review please. |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Emergency Lighting | Independent power source | the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately when general lighting power fails, as required by the Building Code of Pakistan Fire Safety Provisions 2016. | 6 months | Electrical department has evaluated and modified the electrical connections. Now the emergency lights are connected in a manner that if there will be a power failure than emergency light of said area will be activate Accordingly. For the future same has been put up in the SOP and will be followed. | Done |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Emergency Lighting | Independent power source | the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | Reference to our internal documentation system Document No. UF-FHS-03-008 of Fire & Health Safety Management System has been revised as per standard. Same has been available for review. | Done |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Cabling & Wiring | Cables support and protection | proper supports were not provided for cables, they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. This issue was observed at lift rooms and generator room. | Secure cables with appropriate supports and insulate any exposed connections to prevent sagging, stress, and potential hazards. (Reference: BS 7671 18th Edition + A2 (2022) Regulation 522.8.5 for mechanical support and 526.5 for proper terminations) | 3 months | We'll do the best possible to install appropriate supports for cables and insulate any exposed connection According to the standard provided. |  |  |  | In Progress
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Cabling & Wiring | Cables support and protection | proper supports were not provided for cables, they were laid directly on the ground and hung along the walls. Additionally, several locations had open and exposed electrical connections. This issue was observed at lift rooms and generator room. | Implement a comprehensive cable management system with regular inspections to ensure cables remain properly supported and insulated over time. | 6 months | We will implement a comprehensive cable management system at your pointed areas and all other places. We'll keep it maintained as well. |  |  |  | In Progress
[20 empty] | E35 | Cabling & Wiring | Cable trench and channel cleanliness | the cleanliness of the cable trunking system had not been maintained. These issues were observed throughout the facility. It is imperative to implement remedial actions across the entire facility to ensure safety and compliance. | Clean all cable trunking systems to remove accumulated dust and fluff, ensuring that any potential fire hazards are mitigated. | 2 months | Schedule and mechanism to clean all electrical equipment, panel wires and trenches has been prepared. |  |  |  | In Progress
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Cabling & Wiring | Cable trench and channel cleanliness | the cleanliness of the cable trunking system had not been maintained. These issues were observed throughout the facility. It is imperative to implement remedial actions across the entire facility to ensure safety and compliance. | Implement a regular maintenance schedule that includes routine inspections and cleaning of the cable trunking systems to prevent future accumulation of dust and fluff, thereby maintaining a safe environment and complying with safety standards. | 6 months | Schedule and mechanism to clean all electrical equipment, panel wires and trenches has been prepared. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgear were made without cable lugs. These issues were observed throughout the facility. | install cable lugs on all improperly terminated cables within panels and switchgear to secure connections and prevent breaking strands and loose connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022) | 4 months | Assessment is being carried out to identify and rectify said issue. Electrical management system is being prepared with the coordination of electrical engineers as per suggested standard. Upon preparation same will be followed and shared to Accord team for review. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Cabling & Wiring | Splicing of cables | Cables terminations within panels and switchgear were made without cable lugs. These issues were observed throughout the facility. | Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 6 months | Electrical management system is being prepared with the coordination of electrical engineers as per suggested standard. Upon preparation same will be followed and shared to Accord team for review. |  |  |  | In Progress
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations. These issues were observed throughout the facility. | Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections following Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 4 months | Assessment being carried out. Upon completion same will be taken up. SOP will be added in electrical management system to follow as a part of the system. |  |  |  | In Progress
[9 empty] | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E40 | Cabling & Wiring | Splicing of cables | PVC tape joints were found in several locations. These issues were observed throughout the facility. | Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance and provide continuous training for staff on proper jointing techniques. | 6 months | SOP has been shared to systems department who are preparing electrical management systems. |  |  |  | In Progress

## Fire
[9 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
[9 empty] | 24-Jul-24 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
[11 empty] | Remediation Summary of Actions Required | [10 empty] | Corrective Action Plan- Fire
[9 empty] | Factory Name & Address | [12 empty] | Union Fabrics (Pvt.) Ltd- Stitching Plot # D-14/C-1, Bara Board, SITE, Karachi, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 24-Jul-2024
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F1 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in both buildings and facility exit gates. - Sliding doors serve for escape from areas with more than 10 occupants are observed in production building level 1, 2, 3, 4 and 5. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | Assessment of the entire factory has been carried out. Locking Mechanism of 42 doors needs to be rectified. |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F2 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in both buildings and facility exit gates. - Sliding doors serve for escape from areas with more than 10 occupants are observed in production building level 1, 2, 3, 4 and 5. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. Replace sliding doors with swing doors or provide bypass doors nearby or pocket doors built into the existing sliding door, that are side swinging and open in the direction of travel to an exit. | 3 months | Assessment of the entire facility has been carried out . Total of 09 pocket doors will be fabricated in the sliding door in production building at all levels. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F3 | Means of Escape | Escape doors | Lockable mechanisms on doors/gates along egress routes and/or at exit discharge point, found in both buildings and facility exit gates. - Sliding doors serve for escape from areas with more than 10 occupants are observed in production building level 1, 2, 3, 4 and 5. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F2 + 3 months | Work instruction of Fire & Health Safety Management System No. No. UF-FHS-03-014 has been revised as per standard of ACCORD, Building Code of Pakistan, same also will be implemented. Attached for info. | Done Already |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F4 | Means of Escape | Protection of stairs | All Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. - Unprotected openings into all stairs of both buildings. - Fire load and services passing through stair S2 of production building. | Remove fire load and any other obstructions due to stored items from stairs. | 2 weeks | All combustible material has been removed. In addition an awareness session to admin & housekeeping staff has been arranged to comply with the same. Also instructions in native languages pasted that "Please do not spare or stock anything here either temporary". Pictures attached. | Done Already |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F5 | Means of Escape | Protection of stairs | All Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. - Unprotected openings into all stairs of both buildings. - Fire load and services passing through stair S2 of production building. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g.. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | All Exit Stairways will be protected from adjacent hazards by fire and smoke resistant construction for which drawings are already developed and factory is in process of taking quotations from various civil contractors and fire door suppliers. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F6 | Means of Escape | Protection of stairs | All Exit stairways are not protected from adjacent hazards by fire and smoke resistant construction including opening protective assemblies and there is fire load in the staircase. - Unprotected openings into all stairs of both buildings. - Fire load and services passing through stair S2 of production building. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1 and 8.6.4. Key requirements include: - All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. | F5 + 4 months | All Exit Stairways will be protected from adjacent hazards by fire and smoke resistant construction for which drawings are already developed and factory is in process of taking quotations from various civil contractors and fire door suppliers. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F7 | Means of Escape | Exit access | Per Pakistan Accord Building Standard, escape routes within the building should be sufficiently wide and safe for use in and event of an emergency. - Protected stair S1 discharges inside the production building at a distance from building exit. - Insufficient headroom at the entry into staircase S3 of production building level 5. | Fix headroom height safety signage and padding around underside of lintel where door height is less than 2050mm on the escape route. | 2 weeks | The current headroom height is 1880 mm. There is difference of 170 mm. Since we have an overhead water tank whose columns are constructed on that beam therefore we can try to increase the height of the door up to 50 mm; but once we install the door, height will again be 1880mm. but we will place head safety sign and also install rubber pad. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F8 | Means of Escape | Exit access | Per Pakistan Accord Building Standard, escape routes within the building should be sufficiently wide and safe for use in and event of an emergency. - Protected stair S1 discharges inside the production building at a distance from building exit. - Insufficient headroom at the entry into staircase S3 of production building level 5. | Propose modifications to ensure adequate headroom at required locations to ensure safe passage on the escape route or propose alternative paths that comply with Pakistan Accord Standard and present to Pakistan Accord for review. For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge routes. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies (e.g.. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | The current headroom height is 1880 mm. There is difference of 170 mm. Since we have an overhead water tank whose columns are constructed on that beam therefore we can try to increase the height of the door up to 50 mm; but once we install the door, height will again be 1880mm. but we will place head safety sign and also install rubber pad. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F9 | Means of Escape | Exit access | Per Pakistan Accord Building Standard, escape routes within the building should be sufficiently wide and safe for use in and event of an emergency. - Protected stair S1 discharges inside the production building at a distance from building exit. - Insufficient headroom at the entry into staircase S3 of production building level 5. | Implement measures to ensure adequate clear height along all escape routes or provide alternative escape route as required after Pakistan Accord review. Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Accord Building Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetrations through doors are not permitted. All fire doors require self-closers. Doors into exit discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge routes need to be fire stopped. Unprotected openings (e.g.. holes or window/ louver openings) are not permitted. | F8 + 4 months | Assessment of entire factory has been carried out and found that there is ONE Window at Stair 1 (5th Floor), THREE Windows at Stair 2 (2nd, 3rd, 4th Floor) and FIVE Windows at Stair 3 at all floors. However after more assessment it has been concluded that there is no need to close these windows because we have already decided to install fire retardant doors at all the stairs therefore fire cannot travel from inside to outside either way. | To be discussed with ACCORD Team |  |  | In Progress
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Exit signage | Missing exit signage on exit doors, throughout floors and final exit to building and premises. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Building Standard and BCP 10.15.1, 10.15.2 and 10.15.3. | 3 months | We are in process of developing floor wise drawings to show the location of these signage. Quotations for listed signs will be taken, vendor will be finalized and approval to start work will be sought from the management. |  |  |  | In Progress
No | 3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit signage | Missing exit signage on exit doors, throughout floors and final exit to building and premises. | Ensure that all exit signage is checked periodically and in good working condition. | F10 + 3 months | Work instruction of Fire & Health Safety Management System No. UF-FHS-03-019 has been revised as per standard of ACCORD, Building Code of Pakistan, same also will be implemented. | Done Already |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F12 | Fire Rated Construction | Separation of high-risk areas | - Fire pump room is not fire separated from the rest of the building. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g. storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g.. door listing, self-closers, door opening direction) | 4 months | This point need to be discussed with ACCORD Team as In current facility it is not possible to construct separate fire pump room. However fire room has been cleared and fire load is removed; further we will also construct fire rated walls and install fire rated door to save the pump room. Drawing will be developed and approval will be taken from ACCORD Team |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F13 | Fire Rated Construction | Separation of high-risk areas | - Fire pump room is not fire separated from the rest of the building. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F12 + 4 months | Designing of fire pump room with protected fire rated walls and door to fulfill the requirement. Drawing and technical sheet of door available. |  |  |  | In Progress
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Fire Rated Construction | Separation of shafts | The lift shafts have unprotected opening in production building. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g.. listing, fire rating period, self-closers, door opening direction) | 4 months | There are two in nos. lifts in production buildings having 6 levels each. Fire rated shutter 2 hour rating has been chosen to fulfill this requirement. Drawings and technical sheet available for review. |  |  |  | In Progress
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | Fire Safety Inspection | F15 | Fire Rated Construction | Separation of shafts | The lift shafts have unprotected opening in production building. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F14 + 4 months | Fire rated shutter 2 hour rating has been chosen to fulfill this requirement. Drawings and technical sheet available for review. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F16 | Fire Rated Construction | Floor openings | - Chutes and/or conveyor belts are not fire separated connecting multiple levels of production building. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings - Proposed fire separation details (including fire rating of walls and doors) | 4 months | There are four in nos. total doors (Fire rated) required to fulfil this requirement. Only need to change the door with the existing one. Drawing and technical sheet available. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F17 | Fire Rated Construction | Floor openings | - Chutes and/or conveyor belts are not fire separated connecting multiple levels of production building. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F16 + 4 months | There are four in nos. total doors (Fire rated) required to fulfil this requirement. Only need to change the door with the existing one. Drawing and technical sheet available. |  |  |  | In Progress
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Fire Rated Construction | Storage | - Storage areas are not fire separated from the rest of the building observed in production building level 5. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above). | Identify all designated storage areas. Identify which storage areas will follow the in-process storage limitations described above and which will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details for review and approval by Accord prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g.. listing, fire rating period, self-closers, door opening direction) | 4 months | Design has been prepared. Currently between store and cutting section there is a sheet present which can cause fire, heat or smoke transfer. New construction has been designed (available for review). |  |  |  | In Progress
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Fire Rated Construction | Storage | - Storage areas are not fire separated from the rest of the building observed in production building level 5. - Presence of areas where storage does not meet miscellaneous in-process storage requirements (listed above). | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F18 + 4 months | Design has been prepared. Currently between store and cutting section there is a sheet present which can cause fire, heat or smoke transfer. New construction has been designed (available for review). |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F20 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided. | (1) Submit design documentation for sprinkler system along with required standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 13, NFPA 14, 20, 22, and 24 | 4 months | Designing has been carried out. Attached for review also hydraulic calculation and technical sheets of fire pump, equipment's, sprinkler and related things available for technical review. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F21 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier | F20 + 1 months | Pending, after approval of same will be shared. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F22 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F21 + 3 months | Pending, after approval of same will be shared. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F23 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided. | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | F22 + 3 months | Pending, after approval of same will be shared. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F24 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided. | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F23 + 3 months | Pending, after approval of same will be shared. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F25 | Fire Suppression | Sprinkler system | - Sprinkler system is not provided. | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F24 + 4 months = 18 months | Pending, after approval of same will be shared. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F26 | Fire Suppression | Fire pumps | - Fire pump set is not listed. - Fire pumps are not in a fire separated room. | Provide electric duty pump, diesel backup fire pumps and jockey pump, together with individual drivers and controllers, in accordance with NFPA 20 as part of the supporting infrastructure to the SUPS system and following steps (1) to (6) above. | 18 months | As per the new designing of fire sprinkler and standpipe system, hydraulic calculations and all related factors as per NFPA standards 1500 US GPM pump set needs to be installed. hydraulic calculation and technical sheet of UL Listed and FM Approved has been available for review. |  |  |  | In Progress
No | [8 empty] | Initial | [10 empty] | F27 | Fire Suppression | Standpipe system | - Missing standpipe outlets in stairs. | Provide Class 1 standpipe system with adequate risers and connections, in accordance with NFPA 14 as part of the supporting infrastructure to the SUPS system and following steps (1) to (6) above. | 18 months | In new designing same has been considered. Design available for review. |  |  |  | In Progress

## Structural
[9 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
2024-07-24
Corrective Action Plan - Structural
[9 empty] | Factory Name & Address | [12 empty] | Union Fabrics (Pvt.) Ltd - Stitching, Plot # D-14/C-1, Bara Board SITE, Karachi, Sindh, Pakistan
[9 empty] | Date of Initial Inspection | [12 empty] | 2024-07-24
[22 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[22 empty] | No | No | No
UPLOAD | INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
No | 3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Potential Overstress | Highly stressed columns | The columns at the ground floor of the production building appears to be overstressed against the observed load. | Factory Engineer to review design, loads and columns stresses in area identified below and submit the report to Accord for review. | S2+ 3 months | Factory will hire Third Party Inspection Firm/ Structural Consultant to check whether column stresses, loads and design lies within the allowable limit or not. Core Testing of Columns for Compressive strength on various locations in order to confirm the strength of column and submit the results to Accord for assessment Accordingly |  |  |  | In Progress
No | 3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Potential Overstress | Highly stressed columns | The columns at the ground floor of the production building appears to be overstressed against the observed load. | Verify insitu concrete strengths either by 100mm diameter cores or existing cylinder strength data for the columns identified in report and inform Accord about the results to recheck the column calculation. | 3 months | Factory will hire Third Party Inspection Firm/ Structural Consultant to verify column concrete strengths by extraction of cores and to recheck the column calculations. |  |  |  | In Progress
No | 3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Potential Overstress | Highly stressed columns | The columns at the ground floor of the production building appears to be overstressed against the observed load. | Actively manage the loading for all floor plates within the factory considering the floor load plans. | S1 + 3 months | Factory Compliance team will monitor floor loadings on monthly/ weekly basis to make sure that factory stuff must not exceed the floor loading capacity, mentioned in the floor load plan. |  |  |  | In Progress
No | 3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Structural System | Lateral stability system | There is no apparent stability system in the production building before the construction joint as Flat slab with drop panels is provided, rest of the building is Beam Slab construction. | Building Engineer to review the design and check for the lateral stability of the building and submit results of assessment to Pakistan Accord for review. | 7 months | Factory will hire Third Party Inspection Firm/ Consultant to review the design and check for the lateral stability of the building. |  |  |  | In Progress
No | 3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Other Damage/Defects | Moisture ingress | The Drainpipe was installed after the construction of the Production Building, the cores were cut from the slab for installation of pipes. The presence of water coolers in the area is contributing to moisture ingress. This was observed on 4th, 3rd, 2nd and 1st floors. | Building Engineer to inspect the area and address the moisture ingress from cores, propose measures to prevent further damage and carry out necessary repair works. | 6 months | Subject Area has been inspected and the Cores that were cut to pass the drain line was sealed. Further to this Chemical Grouting will be done to control water seepage/ leakage from drinking area. |  |  |  | In Progress
No | 3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Other Damage/Defects | Health and Safety | There was no safe access to roof level of Utility building, the staircase provided is not safe. | Provide appropriate and safe stair for the roof access. | 1 month | MS Stairs at the subject location has been proposed for safe access to Roof. Construction of MS Stairs also done as per Accord Requirement. |  |  |  | In Progress
No | 3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Structural Documentation | Documentation unavailable | All the structural drawings of the buildings are not available, following structural drawings are not available and needs to be prepared • The structural drawings of production building for the Flat area are not available. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | Factory will hire Structural Engineering Consultants and NDT facility in order to identify the structural building elements in details and prepare the as-built structural drawings Accordingly. |  |  |  | In Progress
No | 3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Structural Documentation | Documentation unavailable | All the structural drawings of the buildings are not available, following structural drawings are not available and needs to be prepared • The structural drawings of the Utility buildings are not Available. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | As built drawings of the factory buildings are available, only data of steel provided in the utility building is missing. For this data, Factory will hire Third Party Firm for NDT to complete As Built Documentation. |  |  |  | In Progress
No | 3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Structural Documentation | Differs from as-built structure | The as-built plans for the Production Building are not matching the as- built drawings as the staircases are not marked on all levels. | Building Structural Engineer to check, collect information and produce accurate and complete as-built documentation. | 6 months | Factory will hire Structural Engineering Consultants and NDT facility in order to identify the structural building elements in details and prepare the as-built structural drawings Accordingly. |  |  |  | In Progress
No | 3 | 8 |  | 119 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 120 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 121 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 122 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 123 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 124 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 125 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 126 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 127 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 128 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 129 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 130 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 131 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 132 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 133 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 134 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 135 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 136 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 137 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 138 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 139 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 140 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 141 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 142 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 143 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 144 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 145 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 146 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 147 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 148 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 149 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 150 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 151 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 152 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 153 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 154 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 155 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 156 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 157 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 158 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 159 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 160 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 161 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 162 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 163 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 164 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 165 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 166 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 167 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 168 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 169 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 170 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 171 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 172 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 173 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 174 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 175 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 176 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 177 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 314 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 315 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 346 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 349 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 350 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 351 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 352 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 353 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 354 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 355 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 356 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 357 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 358 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 359 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 360 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 361 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 362 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 363 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 364 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 365 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 366 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 367 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 368 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 369 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 370 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 371 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 372 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 373 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 374 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 375 | 421 | 6 | 5 |  |  | Fire | No | No |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 376 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 377 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 378 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 379 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 380 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 381 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 382 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 383 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 384 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 385 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 416 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 417 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 418 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 419 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 420 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 421 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 422 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 423 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 424 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 425 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 426 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 427 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 428 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 429 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 430 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 431 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 432 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 433 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 434 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 435 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 436 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 437 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 438 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 439 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 440 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 502 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 503 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 504 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 505 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 506 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 507 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 508 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 509 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 510 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 511 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 512 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 513 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 514 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 515 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box
No | 3 | 8 |  | 516 | 421 | 6 | 5 |  |  | Fire | No |  |  | Essay response | Essay, bottomless text box

## E Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | General & Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors | General Lighting | Room separation | Cable size
Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery | Fixtures
add one |  | Openings | Manual Call Points |  | Back-up power supply
|  | Adequate accessibility | Alarm Sounders
|  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type

## F Categories
Categories | Means of Escape | Fire Rated Construction | Hazardous Materials | Fire Suppression | Fire Safety Management
Means of Escape | Protection of stairs | Structural fire rating | Chemicals handling | Standpipe system | Fire drills
Fire Rated Construction | Number of exits | Extensive voids | Chemicals storage | Fire extinguishers | Records of systems maintenance
Fire Suppression | Travel distance | Separation of high-risk areas | Diesel storage | Fire pumps | Records of system testing
Hazardous Materials | Exit capacity | Separation of shafts | Gas storage | Sprinkler system | Staff training
Fire Safety Management | Exit access | Separation of occupancies |  | Water supply | Emergency Action Plan
| Escape stair condition | Floor openings |  | Exterior hydrants | Fire vehicle access
| Exit discharge | Storage
| Escape doors | Atrium
Exit signage

## S Categories
Table1 | Table2 | Table3 | Table4 | Table5 | Table6 | Table7
Categories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability
Leaking Pipes
Table 8
Inspection Type
Initial
Follow Up
Pre-T&CV
T&CV
Final T&CV
Another type
And another type