## Electrical
[8 empty] | Last Inspection Date | [12 empty] | ELECTRICAL SAFETY
02-Feb-2024
Corrective Action Plan - Electrical
[8 empty] | Factory Name & Address | [12 empty] | Ashabi Tex Pvt Ltd, Plot No D-23, South Ave, SITE Industrial Area, SITE, Karachi
[8 empty] | Date of Initial Inspection | [12 empty] | 2 February 2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | INSPECTION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | E1 | Diagrams & Drawings | Single Line Diagram (SLD) | Single Line Diagrams related to this facility were not provided. | Consult a qualified electrical engineer to produce a Single Line Diagram to include information on all panels, distribution boards and on sub-distribution boards. Ensure all relevant details are accurately depicted to maintain the integrity and safety of the electrical system. | 6 months | Factory is planning to hire consultant for the designing Electrical lay out and SLD's. Factory will ensure that in-situ electrical layout is matched with SLD |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | E2 | Diagrams & Drawings | Electrical layout drawing | As-built Layout drawings were not available | Consult a qualified electrical engineer to provide drawings for complete electrical layout drawings that clearly depict the location and specifications of all electrical equipment and outlets to match existing installation. These drawings should accurately reflect the current electrical infrastructure in the facility. As there might be too much information to be effectively displayed on a single drawing. Consider splitting the drawing into separate diagrams and ensure that the details of each panel are clearly visible and up to date with the current electrical installation. Risk assessment for Lightning Protection System should be carried out by qualified engineer and design system accordingly if required. | 8 months | Factory is planning to hire consultant for the designing Electrical lay out,SLD's and Lightning Protection System, he will also responsible for risk assessment for lightning protection system. Factory will submit completed electrical layout drawing to Accord for review and feedback |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | E3 | Diagrams & Drawings | Electrical layout drawing | Thermographic & Insulation Test Reports were not available. Earth testing report was also not available | Earth Test, Thermographic & Insulation Testing report shall be prepared | 6 months | we are planning for hiring of qualified consultant to conduct all required testings with his guidelines according to standards Factory will submit thermographic test to Accord for review |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | E4 | Generator, Transformer & Sub-Station Room | Room separation | This relates to the main building on first floor. In main LT Room, it does not have any door to avoid the movement of unauthorized/unqualified person in Panel area | Need to take immediate temporary arrangements to restrict the access of unauthorized person in the electrical room | 1 month | we have arranged temporary chain berrication to restrict unauthorized access. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | E5 | Generator, Transformer & Sub-Station Room | Room separation | This relates to the main building on first floor. In main LT Room, it does not have any door to avoid the movement of unauthorized/unqualified person in Panel area | Appropriate permanent arrangement shall be done to restrict the access of unauthorized person in the electrical room. | 2 months | facility has decided to install permanent aluminum door for controlling unauthorized access. Facility will also display authorized and trained staffs Pictures for denying unauthorized person. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | E6 | DBs & Elec Protection Systems | Circuit breakers | This relates to the main building on first floor. Cable sizes and breaker ratings were not coordinated in different Distribution Boards. This has been found in all DBs with few exceptions. For instance - DB ATEX_EP-02 has16Sq.mm cu/pvc cable installed with larger size of 100A circuit breakers | Replace breaker or cables with correct cable or breaker sizes to ensure that the breaker size is less than the current carrying capacity of the cable. | 1 months | Factory is planning to hire consultant for the designing Electrical lay out as per requirements and standards after finalization and approval of layout, facility will standardized cable sizes and breaker ratings in accordance with required capacity. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E7 | DBs & Elec Protection Systems | Circuit breakers | This relates to the main building on first floor. Cable sizes and breaker ratings were not coordinated in different Distribution Boards. | A thorough inspection shall be carried out to check breaker-cable coordination in the entire facility and do remedial action if required | 3 months | Facility will also give this responsibility to the hiring consultant. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E8 | DBs & Elec Protection Systems | Openings | This relates to the main building on first floor. Unsealed panel openings were found in DBs throughout the facility. . Some of them are mentioned below for reference: - ATEX-EP-02, ATEX-EP-03, ATEX-EP-05 | Seal all openings in DBs or Panels (using plates and cable glands) to prevent the ingress of dust and dirt | 3 months | we are planning for Seal all DB's openings step by step. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E9 | DBs & Elec Protection Systems | Openings | This relates to the main building on first floor. Unsealed panel openings were found in DBs throughout the facility. . Some of them are mentioned below for reference: - ATEX-EP-02, ATEX-EP-03, ATEX-EP-06 | Initiate a regular maintenance and cleaning schedule for all electrical panels. Ensure that electrical panels are cleaned, inspected, and free from dust and dirt | 2 months | factory has developed weekly DB's and Cable Trays cleaning Schedule. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E10 | Cabling & Wiring | Splicing of cables | This relates to the main building on first floor. PVC tape joints on cables inside the panels and general wiring found throughout the facility, eg. in - ATEX -EP-02 and EP-03 | Replace the affected cables with -continuous cables of the appropriate length to ensure a direct, uninterrupted electrical connection or -use joint boxes and appropriate connectors to joint cables | 4 months | Facility has planed to replace joined cables to continuous cables |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E11 | DBs & Elec Protection Systems | Earthing system | This relates to the main building on first floor. Earth connection is missing in all DBs of the facility. There was not a single point connected with earth. Some of them are mentioned below for reference. - ATEX-EP-02 bus bar without cables - ATEX-EP-05 &04, 03 - Old DB cotton warehouse - ATEX-EP-08 | Earth Testing of existing pits shall be carried out to check the condition. If value is not within the standard limits, need rectification measures to get desired results, otherwise install new earth pits as per standard requirements to get satisfactory results of earthing system | 2 months | Factory is planning to hire consultant for the designing earthing system as per standards. |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E12 | DBs & Elec Protection Systems | Earthing system | This relates to the main building on first floor. Earth connection is missing in all DBs of the facility. There was not a single point connected with earth. | All Panels, DBs, any other metal arrangement exposed to electrical installations shall be earthed properly using appropriate size of earth cables to avoid any safety hazard for the workers and equipment. | 6 months | Factory is planning to hire consultant for the designing Proper earthing system as per standards. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E13 | DBs & Elec Protection Systems | Hot Spots | This relates to the main building on first floor. In different locations, hot spots indicating abnormal temperature were found, some here for reference. - LT Panel having temp of 189 °C at a termination point as shown in Fig 16. - EP-03 59C on blue phase | Figures showing max. temperature over 189 °C need immediate rectification action which could be load redistribution, connection tightening, replacement of faulty equipment etc | 1 week | We have replaced the hotspot cable from the LT panel and Distribute the load on that phase. |  |  |  | Pending Verification
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E14 | DBs & Elec Protection Systems | Hot Spots | This relates to the main building on first floor. In different locations, hot spots indicating abnormal temperature were found | Inspect the electrical equipment fed from the panel to identify the source of abnormal temperatures, which may be caused by loose connections, overloaded circuits, or other issues. Address and repair the cause of abnormal temperatures, which may involve tightening connections, redistributing loads, replacing faulty components, or be moved to alternative phase to address neutral. | 1 month | we are on working on it. |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E15 | DBs & Elec Protection Systems | Hot Spots | This relates to the main building on first floor. In different locations, hot spots indicating abnormal temperature were found | Create a schedule to have a thermograph survey carried out by a training person on the entire electrical system at Intervals of no less than 6 months. Carry out thermographic survey | E14 + 6 months | We are planning thermograph survey and inspections on monthly basis, and will share reports with Accord at least every 6 -months |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E16 | DBs & Elec Protection Systems | Lint & dust inside panel board | This relates to the main building on first floor. Dust & Dirt found in all DBs throughout the facility. Few are mentioned below for reference. - DB ATEX-EP-01 & 2 - DB ATEX-EP-03 - Old DB in cotton warehouse | Ensure that all panels or DBs are cleaned throughout the facility and free from dust and lint. | 1 month | factory is performing DB's cleaning on weekly purpose as per developed Schedule. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E17 | DBs & Elec Protection Systems | Lint & dust inside panel board | This relates to the main building on first floor. Dust & Dirt found in all DBs throughout the facility. | Prepare a periodic maintenance schedule. | 3 months | factory has developed weekly DB's and Cable Trays cleaning Schedule. |  |  |  | In Progress
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E18 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the main building on first floor. Some DBs have dedicated neutral missing which could lead to overloaded neutral conductors, increases fire risk, eg. - DB ATEX-EP-02 and EP-03 | Ensure every circuit has dedicated neutral in place to avoid any kind of overload condition. | 5 months | we will do this work as per requirements. Factory will ensure that every circuit has dedicated neutral in place |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E19 | DBs & Elec Protection Systems | Earthing system | This relates to the main building on first floor. In DBs, earth bonding of doors was found missing. Below are for reference. This issue persists throughout the facility. ATEX-EP-01 and ATEX-EP-03 | Earth bonding of DB’s door or any other metal arrangement exposed to electrical installations shall be earthed properly using appropriate size of earth cables to avoid any safety hazard for the workers and equipment | 6 months | Factory is planning to hire consultant for designing earthing system as per standards. |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E20 | DBs & Elec Protection Systems | Earthing system | This relates to the main building on first floor. Ordinary 2 pin power plug was used in multiple locations which does not have earth connection which could pose potential safety hazard | These subpar 2 pin power plugs should be replaced by 3 pin power plugs fulfilling standard requirements having proper earth cable connection to avoid any safety hazard to workers or operator of the equipment | 6 months | we will replace all 2 pin plugs by 3 pin power plugs |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E21 | Generator, Transformer & Sub-Station Room | Working clearance | This relates to the main building on first floor. Combustible material near electrical installation, was found in different areas in the factory, eg: - Inspection room 1 - LT room | Remove all combustible material from within and around all electrical panels in the facility. Ensure that all electric circuitry is clear of combustible materials | 1 month | job has been done |  |  |  | Pending Verification
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E22 | Generator, Transformer & Sub-Station Room | Working clearance | This relates to the main building on first floor. Combustible material near electrical installation | Remove combustible material away from electrical devices | 1 month | work has been done |  |  |  | In Progress
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E23 | Generator, Transformer & Sub-Station Room | Working clearance | This relates to the main building on first floor. Combustible material near electrical installation | Conduct periodic maintenance and maintain the records | 3 months | Facility has developed electrical panels Inspection Report to ensure unobstructed electric Panel Area. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E24 | Cabling & Wiring | Cables support and protection | This relates to the main building on first floor. Loose wiring was found in different areas. Eg. - storage and packing areas. | All type of wiring should be done in appropriate cable containment arrangement. Loose wiring shall be avoided in future works | 3 months | All work will be completed ASAP Factory will ensure that wiring is done with appropriate cable containment to avoid any loose wiring |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E25 | DBs & Elec Protection Systems | Multiple Connections | This relates to the main building on first floor. Multi-looping was found in different distribution boards. Few are mentioned for reference. - EP-03 and EP-02 - ATEX-EP-05 | Modify the installation so that circuits do not share breakers. This may mean the addition of new breakers with existing panels or add new distribution board adjacent to existing panel. | 3 months | we are avoiding this practice in future and will remove all multi looping in our DB's Breakers. |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E26 | Cabling & Wiring | Colour coding | This relates to the main building on first floor. There were some deviations from color coding standards. Green cables were found feeding phase circuits in different distribution boards, eg: - EP-04 and EP-06 | Cabling should be replaced into their respective color codes where necessary to avoid any hazard due to misinterpretation. | 2 months | We will replace Green Cables which are using as phase feeding circuit by dedicated Color Code. |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E27 | Cabling & Wiring | Splicing of cables | This relates to the main building on first floor. In different areas, stranded cables were terminated without cable lugs, creates breaking of strands due applied tightening force, and could lead to temperature rise in remaining strands due to overload | All stranded cables terminations shall be installed with proper cable lugs. For any future works avoid terminating stranded cables without lugs. | 4 months | We have initiated working on EP05, we have installed lugs on all the cables and we will also working on remaining DB's ASAP. |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E28 | Cabling & Wiring | Fixtures | This relates to the main building on first floor: - Damaged power supply board, feeding multiple equipment . - Power socket outlet was found without appropriate fixing arrangement | Replace this termination point which is deteriorated and operating at extreme high temperature, posed serious safety risks, could lead to unscheduled breakdown or tripping, need immediate action. | 3 months | work has been done |  |  |  | Pending Verification
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E29 | Cabling & Wiring | Fixtures | This relates to the main building on first floor: - Damaged power supply board, feeding multiple equipment . - Power socket outlet was found without appropriate fixing arrangement | Damaged and broken power supply boards shall be replaced to avoid any safety hazard. All sockets shall be installed with appropriate fixing arrangement for the smooth and safe operation | 3 months | work has been done |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E30 | Cabling & Wiring | Fixtures | This relates to the main building on first floor. Wooden boards for switching of light and fan circuits were found throughout the facility. These may not provide adequate insulation against electrical current, potentially leading to electrical hazards such as short circuits, fires, or electric shocks | All electrical components must be protected against fire risk factors. Replace it with appropriate switchboard of non-combustible material, mounted on wall surface with no exposed wiring | 3 months | we will work on it. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E31 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the main building on first floor, which does not meet with Accord requirements. Some issues observed include: - Non-listed components - Fire alarm control panel is non-addressable - detectors were missing in some areas - inappropriate placement of detectors | Ensure effective operation of currently installed alarm and detection system in the building. | 1 month | Factory is planning to hire consultant for designing FADS on NFPA standards |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the main building on first floor, which does not meet with Accord requirements. | (1) Submit design documentation for new replacement system to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Fire Alarm and Detection System (FADS) with NFPA 72 | E31 + 2 months | By january 2025 further design, documentation and installing listed equipments specification will be submitted to Accord by march-2025. |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the main building on first floor, which does not meet with Accord requirements. | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier | E32 + 1 month | L/C and Documents will be provided after approval of design and product to Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the main building on first floor, which does not meet with Accord requirements. | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation. | E33 + 4 months | we will Submit relevant Document Before Commissioning. |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the main building on first floor, which does not meet with Accord requirements. | (4) Once installation of the FADS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review | E34 + 5 months | Facility will submit as built FADS layouts and other documents upon completion. |  |  |  | In Progress
3 | 8 |  | 145 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the main building on first floor, which does not meet with Accord requirements. | (5) Factory to advise Pakistan Accord when FADS installation fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | E35 +3 months | Facility will conduct inspection and verification of the installed system as per guidelines provided by pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 146 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This relates to the main building on first floor, which does not meet with Accord requirements. | (6) Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete | E36 + 3 months | Factory will follow pakistan guidelines for T&C certificates |  |  |  | In Progress
3 | 8 |  | 147 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E38 | Emergency Lighting | Provided but insufficient | This relates to the main building on first floor. In multiple locations, it was noted that the provided emergency lighting fixtures were not working . Few areas are mentioned below: - Both exit doors in Material storage, Production area, Maintenance workshop. - Faulty emergency lights or lights without wiring arrangements | Ensure all emergency lighting fixtures shall be in working condition. | 3 months | these lights will be replaced and redesign according to standards by hiring consultant |  |  |  | In Progress
3 | 8 |  | 148 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | E39 | Emergency Lighting | Provided but insufficient | This relates to the main building on first floor. In multiple locations, it was noted that the provided emergency lighting fixtures were not working . | Emergency lighting system shall be assessed by qualified engineer and modify it as per standard requirement. Furthermore, the emergency lights shall be listed type. | 3 months | these lights will be replaced and redesign according to standards by hiring consultant |  |  |  | In Progress

## Fire
[8 empty] | Last Inspection Date | [12 empty] | FIRE SAFETY
02-Feb-2024
Corrective Action Plan - Fire
[8 empty] | Factory Name & Address | [12 empty] | Ashabi Tex Pvt Ltd, Plot No D-23, South Ave, SITE Industrial Area, SITE, Karachi
[8 empty] | Date of Initial Inspection | [12 empty] | 2 February 2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | F1 | Means of Escape | Escape doors | Doors on escape routes leading to outside or away from the building must not have locking devices, must have latching mechanisms that allow for easy opening. During the inspection, locking mechanisms were observed in most of the doors including: - doors at Stairs S-1, S-2 and S-3 on 1st floor | Remove all non-compliant locking features from doors on all egress paths in accordance with Pakistan Accord Building Standard. | 1 month | Factory has removed all locking mechanisms and installed push bar on all Emergency Exits |  |  |  | Pending Verification
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | F2 | Means of Escape | Escape doors | Doors on escape routes leading to outside or away from the building must not have locking devices, must have latching mechanisms that allow for easy opening. | Provide easily opening mechanisms complying with NFPA 101 and Pakistan Accord Building Standard clauses 1.4 & 1.5 | 3 months | Factory has removed all locking mechanisms and installed push bar on all Emergency Exits |  |  |  | Pending Verification
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | F3 | Means of Escape | Escape doors | This relates to the 2 main exit gates leading to outside the property at Ground level. Door on escape routes leading to outside do not need to be fire rated but must not be lockable and must swing in the direction of exit. | Remove all non-compliant locking features from main exit gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 | 1 month | Facility will discuss with Pakistan Accord we can't neglect security, law enforcement situation in Pakistan. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | F4 | Means of Escape | Escape doors | This relates to the 2 main exit gates leading to outside the property at Ground level. Door on escape routes leading to outside do not need to be fire rated but must not be lockable and must swing in the direction of exit. | Provide opening mechanism on doors in the direction of travel and minimum leaf width should comply with Pakistan Accord Building Standards and BCP 10.9.1.4. Incorporate outward opening side swing panels in the gates leading out of the property able to cater for all occupants of the building | 3 months | Facility will discuss with Pakistan Accord we can't neglect security, law enforcement situation in Pakistan. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | F5 | Means of Escape | Protection of stairs | This relates to the main staircase S-1 at all levels. Stairs must be fire separated from the rest of the building using 2 hour fire resisting construction with 90 minute fire rated doors. | Remove combustible material from staircase enclosure. | 1 month | All combustible material removed. |  |  |  | Pending Verification
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | F6 | Means of Escape | Protection of stairs | This relates to the main staircase S-1 at all levels. Stairs must be fire separated from the rest of the building using 2 hour fire resisting construction with 90 minute fire rated doors. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). | 4 months | Facility has decided to hire consultant to design and eliminate the risk of fire from the main staircase, design will include two hours fire resisting construction as per design facility commit to install 90 minute fire rated door. Factory will prepare drawings showing proposed fire separating construction and door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F7 | Means of Escape | Protection of stairs | This relates to the main staircase S-1 at all levels. Stairs must be fire separated from the rest of the building using 2 hour fire resisting construction with 90 minute fire rated doors. | Ensure all stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors. Penetrations through doors are not permitted. All fire doors require self-closers. Doors into stairs should be kept closed (but not locked) at all times. | F6 + 4 months | Facility has decided to hire consultant to design and eliminate the risk of fire from the main staircase, design will include two hours fire resisting construction as per design facility commit to install 90 minute fire rated door. Fire rated separation of stairs will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F8 | Means of Escape | Protection of stairs | This relates to protection of Exterior escape steel stairs S-2 & S-3 at all levels. Stairs must be fire separated from internal accommodation and external fire loads using 2 hour fire resisting construction with 90 minute fire rated doors. Issues observed: - stairways not protected where they pass openings en route to Ground floor level. - non fire-rated doors opening into both staircases (S-2 and S-3) at 1st floor level. - S-2 steel escape stair has short landing (18 inches) at 1st floor level - S-3 steel escape stair has slip/trip hazard. | Rectify the water dropping issue at S-3 stairs causing a slipping hazard. | 1 months | Facility has decided to reconstruct workers toilet in December-2024 |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F9 | Means of Escape | Protection of stairs | This relates to protection of Exterior escape steel stairs S-2 & S-3 at all levels. Stairs must be fire separated from internal accommodation and external fire loads using 2 hour fire resisting construction with 90 minute fire rated doors.. | Provide fire rated protection to the external steel stairway in accordance with Pakistan Accord Standard. Provide listed fire rated doors/protective assemblies at openings in accordance with requirements of the Pakistan Accord Standard and BCP Table 8.6.3.1. Prepare design with documentation that demonstrates compliance with the Standard and submit to Accord for approval before the upgrading works begin | 4 months | Facility has decided to hire consultant to design and eliminate the risk of fire from the Steel staircase, design will include two hours fire resisting construction as per design facility commit to install 90 minute fire rated door. Factory will prepare drawings showing proposed fire separating construction and door assemblies to protect stairs and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F10 | Means of Escape | Protection of stairs | This relates to protection of Exterior escape steel stairs S-2 & S-3 at all levels. Stairs must be fire separated from internal accommodation and external fire loads using 2 hour fire resisting construction with 90 minute fire rated doors.. | Implement the design as per documentation reviewed by Pakistan Accord | F9 + 4 months | After approval of design factory will implement |  |  |  | In Progress
3 | 8 |  | 120 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F11 | Means of Escape | Exit discharge | This relates to final exit discharge of S-3 east side steel escape stairs at Ground level that does not provide safe passage away from the building. Some of the issues that were observed: - unlevel floor without adequate width leading off the property. - temporary obstructions. - re-entry into the building after final exit discharge which is in use of other factory | Remove temporary obstacles from the passage | 1 month | work is under progress facility will complete by January-2025 |  |  |  | In Progress
3 | 8 |  | 121 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F12 | Means of Escape | Exit discharge | This relates to final exit discharge of S-3 east side steel escape stairs at Ground level that does not provide safe passage away from the building. | Design layout that protect exit route at exterior of the building to allow a safe, free and unobstructed passage away from the building in accordance with the Pakistan Accord Building Standards and submitted to Pakistan Accord for review. | 4 months | Facility has decided to hire consultant for designing. Factory will prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification work. |  |  |  | In Progress
3 | 8 |  | 122 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F13 | Means of Escape | Exit discharge | This relates to final exit discharge of S-3 east side steel escape stairs at Ground level that does not provide safe passage away from the building. | Implement the design reviewed by Pakistan Accord. | F12 + 4 months | After approval of design factory will implement Factory will ensure external exit discharge routes are adequately fire separated from the rest of the building. |  |  |  | In Progress
3 | 8 |  | 123 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F14 | Means of Escape | Exit access | This relates to width of aisles leading to floor exits on the production floor that are less than 915 mm (36 in.) at 1st Floor | Remove obstacles on escape path and/ or rearrange distribution of workspaces to ensure minimum requirements of escape width. | 1 month | Facility has decided to hire consultant for redesigning aisle leading exits as per NFPA |  |  |  | In Progress
3 | 8 |  | 124 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F15 | Means of Escape | Exit access | This relates to width of aisles leading to floor exits on the production floor that are less than 915 mm (36 in.) at 1st Floor | Provide the required width for aisles leading to floor exits, by rearranging workspaces if necessary, to comply with Pakistan Accord Building Standard and BCP 10.10.5.3. | 4 months | Facility has decided to hire consultant for redesigning aisle leading exits as per NFPA Factory will provide the required width for aisles leading to floor exit |  |  |  | In Progress
3 | 8 |  | 125 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F16 | Means of Escape | Exit access | This relates to width of aisles leading to floor exits on the production floor that are less than 915 mm (36 in.) at 1st Floor | Maintain un-obstructed escape pathway as per requirements. | F15 + 4 months | Facility has arranged training and monitoring mechanism to ensure clearance of walkways all the time. |  |  |  | Pending Verification
3 | 8 |  | 126 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F17 | Means of Escape | Exit access | This relates to Insufficient headroom observed at main stairs serving 1st to Ground floor level | Fix headroom height safety signage and other measures required to ensure safe passage where head height is less than 2.05 m on the escape route | 1 month | we have installed the signage. |  |  |  | Pending Verification
3 | 8 |  | 127 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F18 | Means of Escape | Exit access | This relates to Insufficient headroom observed at main stairs serving 1st to Ground floor level | Propose modifications to ensure adequate headroom at required locations to ensure safe passage on the escape route or propose alternative paths that comply with Pakistan Accord Standard and present to Pakistan Accord for review. | 4 months | Facility has decided to hire consultant for redesigning aisle leading exits as per NFPA |  |  |  | In Progress
3 | 8 |  | 128 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F19 | Means of Escape | Exit access | This relates to Insufficient headroom observed at main stairs serving 1st to Ground floor level | Implement measures to ensure adequate clear height along all escape routes or provide alternative escape route as required after Pakistan Accord review. | F18 + 4 months | Facility has decided to hire consultant for redesigning aisle leading routes as per NFPA Factory will ensure suitable headroom for safe use of escape routes |  |  |  | In Progress
3 | 8 |  | 129 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F20 | Means of Escape | Travel distance | This relates to the escape path excessive travel distance issue at south-west corner of the Roof and 1st floor level Cutting section | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. | 4 months | Facility has decided to hire consultant for redesigning aisle leading routes as per NFPA Factory will prepare drawings showing proposal for addressing excessive travel distances to floor and building exits and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 130 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F21 | Means of Escape | Travel distance | This relates to the escape path excessive travel distance issue at south-west corner of the Roof and 1st floor level Cutting section | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Building Standard | F20 + 4 months | After approval of design factory will implement |  |  |  | In Progress
3 | 8 |  | 131 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F22 | Means of Escape | Exit signage | This relates to lack of exit and directional signage throughout the building. - Existing exit signage found non-operational due to faulty batteries or wiring | Rectify all issues i.e. (batteries, wiring etc) of existing installed Exit signage throughout the building. | 2 months | Issue Resolved |  |  |  | Pending Verification
3 | 8 |  | 132 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F23 | Means of Escape | Exit signage | This relates to lack of exit and directional signage throughout the building. - Existing exit signage found non-operational due to faulty batteries or wiring | Provide exit signage where missing so that access to exits are indicated by approved, readily visible signs from all areas of the floor and clearly visible at exits points complying with Pakistan Accord Building Standards and BCP 10.15.1, 10.15.2 and 10.15.3. | F22 + 2 months | Facility has decided to hire consultant for redesigning layout as per BCP and other Standards. |  |  |  | In Progress
3 | 8 |  | 133 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F24 | Fire Rated Construction | Separation of shafts | This relates to unprotected openings of Lift shaft at Ground and 1st floor levels | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to Pakistan Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | we have requested our consultant to provide design and solution of for elimination of fire and safety hazards. Factory will prepare drawings showing proposed fire separating construction to shafts, with details of door assembly, location in relation to escape routes and lift door operation, and submit to Accord for review prior to any rectification works |  |  |  | In Progress
3 | 8 |  | 134 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F25 | Fire Rated Construction | Separation of shafts | This relates to unprotected openings of Lift shaft at Ground and 1st floor levels | Provide 2-hour fire rated protection to lift shafts according to the layout and documents reviewed by Pakistan Accord. | F24 + 4 months | we have requested our consultant to provide design and solution of for elimination of fire and safety hazards. Fire rated separation of shaft will be completed, including brickwork/ fire rated assemblies and adequate and door operating mechanism, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 135 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F26 | Fire Rated Construction | Separation of high-risk areas | This relates to Fire separation of high-risk areas from production and storage at 1st floor. Lack of fire separation of high-risk areas were observed for: - main Electric panel room from escape stairs. - machine maintenance room from storage and production floor | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction). | 4 months | we have requested our consultant to provide design and solution of for elimination of fire and safety hazards. Factory will prepare drawings showing proposed fire separating construction to high-risk areas and submit to Accord for review prior to the rectification works |  |  |  | In Progress
3 | 8 |  | 136 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F27 | Fire Rated Construction | Separation of high-risk areas | This relates to Fire separation of main Electric panel room from escape stairs and machine maintenance room from storage and production areas | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord | F26 + 4 months | we have requested our consultant to provide design and solution of for elimination of fire and safety hazards. Fire rated separation of high-risk areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 137 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F28 | Fire Rated Construction | Storage | Extensive storage areas need to be fire separated from the rest of the building using 2 hour fire resisting walls with 90 minutes fire rated doors. Limited in-process storage is permitted in production areas, subject to meeting all of the following criteria (unsprinklered building): - Combined storage areas do not exceed 10% of the production floor area, - Storage height is less than 2.45m, - Storage areas are grouped into islands not exceeding 23 m2, and - Islands are separated from other storage islands by at least 3m gap. The following deficiencies have been observed on site, including (list not exhaustive): - Lack of Fire separation between Storage areas at 1st floor | Identify all designated storage areas. Identify which storage areas can be rearranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | we are relocating our finish good warehouse to second floor where facility to construct separated finish good warehouse, we will submit drawing to Pakistan Accord for review.And other location we will request our consultant to provide design and solution for all storage areas. Factory will prepare drawings showing how in-process storage will be kept in demarcated floor areas within allowable limitations. Where storage cannot be managed within in-process storage limitations prepare drawings showings proposed fire separation details of storage areas, and submit to Accord for review |  |  |  | In Progress
3 | 8 |  | 138 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F29 | Fire Rated Construction | Storage | Lack of Fire separation between Storage areas at 1st floor | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard | F28+ 4 months | Factory will mark up areas designated for in-process storage on floors. Fire rated separation of large storage areas will be completed, including brickwork/ fire rated assemblies, according to proposal previously reviewed by Accord |  |  |  | In Progress
3 | 8 |  | 139 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F30 | Fire Suppression | Standpipe system | This relates to a lack of Standpipe system generally throughout the building. There is no Fire Hydrant/ Standpipe system was found and is required for this building as it has more than 2 stories and a floor area of more than 2,350m2 | (1) Submit design documentation for modified standpipe system and supporting infrastructure to Pakistan Accord for review before purchasing any new equipment. Design documentation to include drawings, technical data sheets and product certifications of all listed equipment to show full compliance of the Suppression System (SUPS) with NFPA 14, 20, 22, and 24. | 4 months | Facility has decided to hire consultant for designing of standpipe system. After receiving drawings we will submitted to Pakistan accord for review. |  |  |  | In Progress
3 | 8 |  | 140 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F31 | Fire Suppression | Standpipe system | There is no Fire Hydrant/ Standpipe system was found and is required for this building as it has more than 2 stories and a floor area of more than 2,350m2 | (2) Submit documentation to Pakistan Accord showing that an L/C has been opened for import of any components required for the SUPS design submitted earlier. | F30 + 1 month | During import process we will submit requested and necessary documents to Pakistan Accord |  |  |  | In Progress
3 | 8 |  | 141 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F32 | Fire Suppression | Standpipe system | There is no Fire Hydrant/ Standpipe system was found and is required for this building as it has more than 2 stories and a floor area of more than 2,350m3 | (3) Submit documentation to Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on site for installation of the SUPS. | F31 + 4 months | we will submit |  |  |  | In Progress
3 | 8 |  | 142 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F33 | Fire Suppression | Standpipe system | There is no Fire Hydrant/ Standpipe system was found and is required for this building as it has more than 2 stories and a floor area of more than 2,350m4 | (4) Once installation of the SUPS system is complete, factory to submit full "as-built" documentation of the system to Pakistan Accord for review. | F32 + 3 months | Once installation is complete Factory will submit full "as-built" documentation of the system to the Pakistan Accord for review |  |  |  | In Progress
3 | 8 |  | 143 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F34 | Fire Suppression | Standpipe system | There is no Fire Hydrant/ Standpipe system was found and is required for this building as it has more than 2 stories and a floor area of more than 2,350m5 | (5) Factory to advise Pakistan Accord when SUPS installation fully completed and fully functional. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation | F33 + 3 months | Factory will advise Accord when the SUPS is ready for a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation |  |  |  | In Progress
3 | 8 |  | 144 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | F35 | Fire Suppression | Standpipe system | There is no Fire Hydrant/ Standpipe system was found and is required for this building as it has more than 2 stories and a floor area of more than 2,350m6 | (6) Provide full testing and commissioning (T&C) certification from the SUPS system installer and make provision for attendance of the system installer, factory technical personnel and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the SUPS system will be complete | F34 + 3 months | Factory will provide full testing and commissioning (T&C) certification from SUPS system installer and arrange for attendance of the system installer, factory technical personnel, and Accord technical team to witness a final T&C demonstration verification on site |  |  |  | In Progress

## Structural
[8 empty] | Last Inspection Date | [12 empty] | STRUCTURAL SAFETY
02-Feb-2024
Corrective Action Plan - Structural
[8 empty] | Factory Name & Address | [12 empty] | Ashabi Tex Pvt Ltd, Plot No D-23, South Ave, SITE Industrial Area, SITE, Karachi
[8 empty] | Date of Initial Inspection | [12 empty] | 2 February 2024
[21 empty] | Remediation Schedule | Finance Schedule | Finance Plan Agreed
[21 empty] | No | No | No
INSPECTION SCOPE ID | ISSUE TYPE ID | SUBHEADER ID | CODE PROVISION ID | OBSERVATION TYPE ID | OBSERVATION TYPE BASE ID | OBSERVATION CONTROL TYPE ID | ISSUE ID | INSPECTION TYPE | ISSUE TYPE | REQUIRED | ACTION VERIFIED | ACTION VERIFIED DATE | OBSERVATION TYPE | OBSERVATION BASE TYPE | OBSERVATION AVAILABLE OPTIONS | OBSERVATION EXAMPLE | OBSERVATION HELP | OBSERVATION | ITEM NO | CATEGORY | SUB-CATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | FACTORY ACTION PLAN | AGREED TIMELINE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
3 | 8 |  | 106 | 421 | 6 | 5 |  | Initial | [10 empty] | S1 | Loading | Uncontrolled loading | Potential overloading of fabric storage is observed at some areas of the 1st floor level especially in the fabric warehouse. No drawings indicating design load capacity were available and there were no safe load plans posted anywhere in the factory. | Factory to appoint a Structural Engineer to review the safe load capacity of the floors and advise on load limitations if necessary | 1 month | Facility has decided to hire a consultant for development of structural drawings and load management plan. |  |  |  | In Progress
3 | 8 |  | 107 | 421 | 6 | 5 |  | Initial | [10 empty] | S2 | Loading | Uncontrolled loading | Potential overloading of fabric storage is observed at some areas of the 1st floor level especially in the fabric warehouse. | Safe load capacities to be displayed in factory and loading actively managed by Factory Management. | 6 months | Waiting for the drawings and load management plan from consultant for safe load management on production floor display. Factory will submit safe load plans to Accord for review |  |  |  | In Progress
3 | 8 |  | 111 | 421 | 6 | 5 |  | Initial | [10 empty] | S3 | Other Damage/Defects | Spalling concrete | This relates to the roof over the toilets at the roof level. Precast slab tiles over the toilets roof are cracked and damaged, supported on precast beams spanning onto masonry walls. A water tank is supported over the roof. | Building Engineer to inspect the area and propose remedial measures to prevent further damage to slab and submit to Pakistan Accord for review. Consider replacing the precast tiles to an alternate slab solution. | 3 months | Our consultant will perform inspection and advise us, we will work accordingly. |  |  |  | In Progress
3 | 8 |  | 112 | 421 | 6 | 5 |  | Initial | [10 empty] | S4 | Other Damage/Defects | Spalling concrete | This relates to the roof over the toilets at the roof level. Precast slab tiles over the toilets roof are cracked and damaged, supported on precast beams spanning onto masonry walls. A water tank is supported over the roof. | Complete the remedial works as per reviewed proposal. | S3+ 3 months | Guideline solutions and actions advised by the consultant will be discussed with Pakistan Accord for review. |  |  |  | In Progress
3 | 8 |  | 113 | 421 | 6 | 5 |  | Initial | [10 empty] | S5 | Cracking | Beams | The RC roof beams at gls. 10/G appear to have cracks due to excessive shear forces | Sections of plaster finish to beams to be removed to investigate if cracks penetrate the building structure | 2 months | Waiting for the consultants advise. |  |  |  | In Progress
3 | 8 |  | 114 | 421 | 6 | 5 |  | Initial | [10 empty] | S6 | Cracking | Beams | The RC roof beams at gls. 10/G appear to have cracks due to excessive shear forces | Building Engineer to carry out design check on beams to confirm that these cracks are non-structural. Building Engineer to prepare Safe load plans. | S5 + 4 months | Consultant will submit necessary documents for accords review. |  |  |  | In Progress
3 | 8 |  | 116 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S7 | Cracking | Slabs | Cracks observed in the roof slab adjacent to the lifts good at the roof level. It appears to be that this portion of roof slab was overloaded in the past and over the time it has been deteriorated due to weathering | Structural Engineer to investigate cause of cracking. | 2 months | Consultant will inspect and submit documented investigation record with us for review of Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 117 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S8 | Cracking | Slabs | Cracks observed in the roof slab adjacent to the lifts good at the roof level. | Structural Engineer to carry out design check on slab to confirm whether these cracks are structural or not and carry out remediation works if required. | S7 + 4 months | Our consultant will perform inspection and advise us, we will work accordingly. |  |  |  | In Progress
3 | 8 |  | 118 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S9 | Structural Design | Drawings differ from as-built | As-built structural drawings to be updated to include the following (non-exhaustive): - Structural framing of steel structure, water tanks, precast beams, tiles and load bearing masonry walls above the roof level - Overhang slabs, steel stairs, location of RC walls, foundation layout, columns and beams on the floor layout, cross-sections | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as-built documentation to be submitted to Pakistan Accord for review. | 6 months | Consultant will inspect & produce accurate as build documentation to be submitted to Pakistan Accord. |  |  |  | In Progress
3 | 8 |  | 119 | 421 | 6 | 5 |  | Initial | Fire | No | No |  | Essay response | Essay, bottomless text box |  |  |  |  | S10 | Other Damage/Defects | Moisture ingress | Water ingress, pooling, leakage was observed that has resulted in rusting of reinforcement, damaging the structural concrete on a number of places, such as: - overhead water tanks at roof level - walls at roof level - beams and slabs at 1st FLoor level | Building Engineer to inspect damaged areas and propose measures to carry out repair works and prevent further damage in future. Consider providing adequate roof falls and waterproofing on the roof and inside the overhead water tanks. | 6 months | Our consultant will perform inspection and advice his guidelines, these guidelines will be forwarded and discussed with Pakistan Accord after approval we will remediate accordingly. |  |  |  | In Progress

## ECategories
ETable_A | ETable1 | ETable2 | ETable3 | ETable4 | ETable5 | ETable6 | ETable7
Inspection Type | ECategories | Diagrams & Drawings | DBs & Elec Protection Systems | Fire Alarm & Detection System (FADS) | Emergency Lighting | Generator, Transformer & Sub-Station Room | Cabling & Wiring
Initial | Diagrams & Drawings | Sub-station room layout drg | Circuit breakers | No FADS | No emergency lighting | Ventilation and illumination | Cables support and protection
Follow Up | DBs & Elec Protection Systems | Single Line Diagram (SLD) | Hot Spots | Non-functional or incomplete | Provided but non-functional | Working clearance | Cable trench and channel cleanliness
another electrical inspection type | Fire Alarm & Detection System (FADS) | Electrical layout drawing | Earthing system | Single floor alarm | Provided but insufficient | Breathing system | Splicing of cables
and another one | Emergency Lighting |  | Panel/cabling/busbar | Single station alarm | Independent power source | Transformer arcing horn | Colour coding
a third type too | Generator, Transformer & Sub-Station Room |  | Loop Connection | Detectors |  | Room separation | Fixtures
| Cabling & Wiring |  | Multiple Connections | Fire Alarm Panel |  | Battery
|  |  | Openings | Manual Call Points |  | Back-up power supply
|  |  | Adequate accessibility | Alarm Sounders
|  |  | Lint & dust inside panel board | Maintenance records
Lightning Protection System (LPS)

## FCategories
FTable_A | FTable1 | FTable2 | FTable3 | FTable4 | FTable5 | FTable6 | FTable7
Inspection Type | FCategories | Means of Escape | Fire Rated Construction | Fire Suppression | Hazardous Materials | Fire Safety Management | Cabling & Wiring
Initial | Means of Escape | Protection of stairs | Structural fire rating | Standpipe system | No emergency lighting | Fire drills | Cables support and protection
Follow Up | Fire Rated Construction | Number of exits | Extensive voids | Fire extinguishers | Provided but non-functional | Records of systems maintenance | Cable trench and channel cleanliness
Pre-T&CV | Fire Suppression | Travel distance | Separation of high-risk areas | Fire pumps | Provided but insufficient | Records of system testing | Splicing of cables
T&CV | Hazardous Materials | Exit capacity | Separation of shafts | Sprinkler system | Independent power source | Staff training | Colour coding
Final T&CV | Fire Safety Management | Exit access | Separation of occupancies | Water supply |  | Emergency Action Plan
| Cable & Wiring | Escape stair condition | Floor openings | Exterior hydrants |  | Fire vehicle access
|  | Exit discharge | Storage
|  | Escape doors | Atrium
Exit signage
F

## SCategories
STable_A | STable1 | STable2 | STable3 | STable4 | STable5 | STable6 | STable7
Inspection Type | SCategories | Structural Documentation | Structural System | Potential Overstress | Cracking | Loading | Other Damage/Defects
Initial | Structural Documentation | Documentation unavailable | Vertical load path | Highly stressed columns | Column | Uncontrolled loading | Corrosion of reinforcement
Follow Up | Structural System | Differs from as-built structure | Lateral stability system | Punching shear | Beams | Water tanks | Spalling concrete
Pre-T&CV | Potential Overstress | Undocumented modification | Slender columns | Building settlement | Slabs | Maximum load markings | Corrosion of structural steel
T&CV | Cracking | Undocumented extension | Lack of local stability |  | Walls | Safe load plans | Column impact damage
Final T&CV | Loading | Non-engineered structure | Connection details |  | Non structural |  | Excessive deflection or vibration
| Other Damage/Defects | Lack of safe load plans |  |  | Material interface |  | Moisture ingress
Health and Safety
Thermal effects
Brickwork instability

## Identifier (hidden)
dummyVersion | dummyVersionid | dummyIsIntialOA
Version | 1 | 1