## Structural
Date
20-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Bestec BD Ltd. (Previously PRM FASHIONS PVT. LTD.), SS SFB #5, SECTOR # 3, KARNAPHULI EXPORT PROCESSING ZONE, CHITTAGONG-4204, BANGLADESH., Chattogram, Chittagong
Date of Inspection |  | 2017-05-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Discrepancies between provided drawing and as -built condition . | Building Eng. Required to prepare as built drawings reflecting the actual conditions. | On Going | Jun 8 2017 | On 01/02/2018: During inspection, it was found that factory updated as-built drawing. Till the date of inspection, factory didn't submit the as-built drawing to ACCORD. On 29/07/2018: As built drawing and other structural documents are prepared and submitted to ACCORD. Factory received a review mail from ACCORD on 5th April 2018. Factory was required to submit revised documents within 19th April 2018.Factory did not submit the revised documents till the date of inspection. On 30/04/2019: As built drawings have been produced as part of Engineering Assessment (EA) and submitted to ACCORD on 17-04-2019 which is under review. On 25/07/2019: Factory prepared the as built drawings as part of EA and got their EA acceptance from ACCORD on 29/05/2019. So, this issue has been covered in EA report, but it could not be verified due to unavailability of original documents. On 16-Mar-2025: Bestec BD Ltd. took over PRM FASHIONS PVT. LTD. in May 2024 and has been officially listed as an independent factory under the RSC in January 2025. The EA document for the Production Building under PRM FASHIONS PVT. LTD. was accepted by ACCORD on May 29, 2019, with a remediation deadline of June 30, 2019, but the required work was never initiated. During the inspection, the factory was unable to provide EA documents, including as-built drawings, load plan, test reports, retrofitting plans etc. The factory is required to produce or collect these documents and submit them to the RSC for review by May 15, 2025. On 26-Nov-2025: Factory was required to submit the EA documents to RSC for review within 30-Sep-2025. Till the date of inspection, factory did not submit the receivable documents to RSC for review. Factory is required to submit the receivable documents to RSC for review without any further delay. Progress Status: 0% RPO Comments: On 25-Feb-2026, the design documents (EA) are pending to be submitted to RSC. | Within 6 weeks | In Progress
Initial Inspection |  | 2 | Absence of Load plan | Produce and actively Manage a load plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | On Going | Jun 8 2017 | On 01/02/2018: During inspection, a set of load plan was found posted on each floor which is not accepted by Accord. Factory is required to submit the load plan to Accord along with Engineering Assessment if loading is considered more than 42 psf. However, floor loading was found below 42 psf except dining areas. On 29/07/2018: Load plan has been prepared and submitted to ACCORD. Factory received a review mail from ACCORD on 5th April 2018. Factory was required to submit revised documents within 19th April 2018.Factory did not submit the revised documents till the date of inspection. During inspection, loading was observed within 42 psf. On 30/04/2019: Load plan has been produced and submitted to ACCORD. Factory received a review mail from ACCORD on 03-04-2019. Factory submitted revised documents on 17-04-2019. During inspection, loading was observed within 42 psf. On 25/07/2019: Factory management got their EA acceptance from ACCORD on 29/05/2019. So this issue has been covered in EA report but it could not be verified due to unavailability of original documents. During inspection loading was found within the allowable load limit (42 psf). Load plan was found posted on each floor. On 16-Mar-2025: During the inspection, no load plan was found posted, and storage was observed on the ramp. However, the floor loading was found below 42 psf. The factory is required to produce and implement an interim load plan based on the structural capacity until finalization of EA. On 26-Nov-2025: During the inspection, floor loading was found below 42 psf for typical floor area. The factory is required to prepare the load plan as part of the EA and submit to RSC for review. Progress Status: 0% RPO Comments: On 25-Feb-2026, the design documents (EA) are pending to be submitted to RSC. | Within 6 weeks | In Progress
Initial Inspection |  | 3 | Absence of Load plan | Continue to implement load plan | On Going | Jun 8 2017 | On 01/02/2018: During inspection, a set of load plan was found posted on each floor which is not accepted by Accord. Factory is required to submit the load plan to Accord along with Engineering Assessment if loading is considered more than 42 psf. However, floor loading was found below 42 psf except dining areas. Factory will post load plan as per accepted EA. On 29/07/2018: Load plan has been prepared and submitted to ACCORD. Factory received a review mail from ACCORD on 5th April 2018. Factory was required to submit revised documents within 19th April 2018.Factory did not submit the revised documents till the date of inspection. During inspection, loading was observed within 42 psf. On 30/04/2019: Load plan has been produced and submitted to ACCORD. Factory received a review mail from ACCORD on 03-04-2019. Factory submitted revised documents on 17-04-2019. During inspection, loading was observed within 42 psf. On 25/07/2019: Factory management got their EA acceptance from ACCORD on 29/05/2019. So this issue has been covered in EA report but it could not be verified due to unavailability of original documents. During inspection loading was found within the allowable load limit (42 psf). Load plan was found posted on each floor. On 16-Mar-2025: After getting acceptance of EA from RSC, the factory is required to follow the accepted load plan. On 26-Nov-2025: Factory is required to follow the accepted load plan after getting acceptance of the EA from RSC. Progress Status: 0% RPO Comments: On 25-Feb-2026, the design documents (EA) are pending to be submitted to RSC. | Within 6 Months | In Progress
Follow Up Inspection |  | 4 | New Finding 1: Dampness was found in roof due to leakage in water supply pipe and improper slope. | Factory is required to take necessary action to repair water pipe leakage and construct proper slope in roof. | Completed | Mar 15 2018 | On 01/02/2018: During inspection, dampness was found in roof due to leakage in water supply pipe and improper slope. Factory is required to take necessary action to repair water pipe leakage and construct proper slope in roof. On 29/07/2018: During inspection, no dampness was found on roof due to leakage in water supply pipe. Factory authority constructed proper slope in roof. On 30/04/2019: This issue has been corrected from previous inspection. Factory authority provided proper slope on roof. On 25/07/2019: Corrected from previous inspection. During inspection, no dampness was found on roof. On 16-Mar-2025: Corrected previously. On 26-Nov-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 5 | New Finding 2: Dampness was found in masonry wall (north-east stair) | Factory Engineer will suggest proper remedial plan to repair dampness | It will be completed within 10-March 2026. | Jun 16 2019 | On 30/04/2019: During inspection, dampness was found in masonry wall. Factory is required to take necessary action to solve this issue. On 25/07/2019: Dampness was found in masonry wall. Factory did not take any necessary action. On 16-Mar-2025: Dampness was found on beam, slab and brick wall. On 26-Nov-2025: Although limited repairs were carried out, dampness was still found at several locations during the inspection, Building engineer is required to repair all the dampness on walls and beams with a suitable method. Progress Status: 20% RPO Comments: On 25-Feb-2026, The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 – weeks) | In Progress
Follow Up Inspection |  | 6 | New Finding 3: Trolley impact on column (Production Building) | Factory is required to repair the damage and provide safety guards around the columns to protect from trolley impact. | Completed | Sep 25 2025 | On 16-Mar-2025: Edges of some columns were found damaged due to trolley impact. The factory is required to repair the damage and provide safety guards around the columns to protect from further impact. On 26-Nov-2025: Factory repaired the column surface and installed column guards to prevent trolley impact. During inspection, no further trolley impact was found on typical floor columns. | (within 6 months) | Corrected
Follow Up Inspection |  | 7 | New Finding 4: Non-structural elements found unbraced/not anchored (Production Building) | The factory is required to brace/anchor all non-structural elements (PVC tanks, storage racks) to prevent falling during earthquake. | Completed | Sep 25 2025 | On 16-Mar-2025: Steel storage racks were found unanchored/unbraced at several locations and PVC water tanks were found unbraced on the roof. On 26-Nov-2025: Factory adequately braced or anchored all the non-structural elements. | (within 6 months) | Corrected
Follow Up Inspection |  | 8 | New Finding 5: Removal of supporting brick wall (Utility Shed) | The factory is required to update the as-built drawings, reconstruct the brick walls for adequate support of the steel roof shed or submit a safety check report confirming the adequacy of structural members and connections. | On Going | May 15 2025 | On 16-Mar-2025: The structure's area has been reduced to the north side, where the shed is temporarily supported by steel pipes. The building engineer is required to update the as-built drawing as per onsite condition, reconstruct the brick wall to provide adequate support for the shed, or submit a Safety Check report confirming the adequacy of the structural members and connections. On 26-Nov-2025: Till the date of inspection, factory has not constructed the required brick walls nor submitted a receivable safety check report confirming the adequacy of the structural members and connections. The Building Engineer is required to update the as-built drawings as per the site condition and, without any further delay, either reconstruct the brick walls or submit a safety check report verifying the adequacy of the structural members and connections. Progress Status: 0% RPO Comments: On 25-Feb-2026, the design documents (Safety Check Report) are pending to be submitted to RSC. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 9 | New Finding 6: Improper connection and missing lateral load transfer media Wastage Shed 1(single storied, 105 sqm) Wastage Shed 2 (single storied, 36 sqm) | The building engineer is required to check the connection & stability system (safety check) for the whole structure and suggest proper alternatives accordingly following the Accord Building Standard. | On Going | May 15 2025 | On 16-Mar-2025: Improper connection and no lateral load transfer media were observed. The building engineer is required to check the connection & stability system (safety check) for the whole structure and suggest proper alternatives accordingly following the Accord Building Standard. On 26-Nov-2025: This issue is required to be covered in the safety check report. Till the date of inspection, the factory has not submitted any receivable safety check report for Wastage Shed-1. However, Wastage Shed-2 has already been demolished. The Building Engineer is required to submit a receivable safety check report for Wastage Shed-1 to the RSC for review, or, if the factory intends to demolish the structure, a consent letter along with a reasonable demolition timeline must be provided without any further delay. Progress Status: 40% RPO Comments: On 25-Feb-2026, the design documents (EA) are pending to be submitted to RSC. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 10 | New Finding 7: Lack of as-built drawing Fire Hydrant Room (32 sqm) Wastage Shed 1 & 2 Gas Cylinder Room (35 sqm) Guard Room (21 sqm) | The factory is required to produce as-built drawings as per onsite condition. | On Going | May 15 2025 | On 16-Mar-2025: During the inspection, as-built drawings were not available for single storied ancillary structures. The building engineer is required to produce the as-built drawings and submit the drawings to RSC. On 26-Nov-2025: This issue is required to be covered in the as-built drawings. Till the date of inspection, factory has not submitted the receivable documents to RSC for review. However during the inspection, discrepancies were found in the available on-site as-built drawings, including inconsistencies in structural dimensions, member details, and connection details. The building engineer is required to revise the as-built drawings as per actual site condition and submit the receivable documents to RSC for review without any further delay. Progress Status: 10% RPO Comments: On 25-Feb-2026, the design documents (EA) are pending to be submitted to RSC. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 11 | New finding-08: Cracks and water ingress at north side Stair roof slab. | Building engineer is required to investigate the depth and reason of cracks and water ingress. Any safety measures, if required as suggested by the consultant, must be taken immediately to ensure safety. Investigation report must include the use of non-de | On Going | Jan 7 2026 | On 26-Nov-2025: During inspection, cracks and water ingress found at north side Stair roof slab. Building engineer is required to investigate the depth and reason of cracks and water ingress. Any safety measures, if required as suggested by the consultant, must be taken immediately to ensure safety. Investigation report must include the use of non-destructive testing (NDT) methods to determine the depth and propagation of cracks, the location and extent of deterioration, and to estimate in-situ material properties. The investigation report, along with the detailed repair methodology, must be submitted to RSC for review. Any remediation work raised from the crack & water ingress investigation report is required to be implemented after getting acceptance from RSC. RPO Comments: On 25-Feb-2025, the design documents (Crack Investigation) are pending to be submitted to RSC. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 12 | New finding-09: Standing water at 1st floor open area of Production Building. | Building engineer is required to improve the drainage system maintaining adequate sloping and drainage pipe. |  | Jun 14 2026 | On 03-May-2026: During inspection, standing water was found at 1st floor open area of Production Building. Building engineer is required to improve the drainage system maintaining adequate sloping and drainage pipe. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 13 | New finding-10: Dampness on roof slab of Guard Room. | Building engineer is required to repair all the dampness with a suitable method. |  | Jun 14 2026 | On 03-May-2026: During inspection, dampness was found on roof slab of Guard Room. Building engineer is required to repair all the dampness with a suitable method. | (within 6 weeks) | In Progress

## Fire
Date
20-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Bestec BD Ltd. (Previously PRM FASHIONS PVT. LTD.), SS SFB #5, SECTOR # 3, KARNAPHULI EXPORT PROCESSING ZONE, CHITTAGONG-4204, BANGLADESH., Chattogram, Chittagong
Date of Inspection |  | 2017-04-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stair no-1 enclosure is not separated from work areas and other spaces on each floor by fire-rated construction(Non rated doors, unsealed penetrations and openings etc. such as HRD office, maintenance room, CAD room, Goods in/out room ). | Provide minimum 1-hr rated doors for buildings with 3 or fewer stories and 1.5-hr fire rated doors for buildings that are 4 or more stories. Seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets. | Completed | Aug 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: The factory has installed fire door for exit stairs separation from production floor but QC room( 3rd), goods in & out room ( 1st) & idle machine room (ground) floors are remaining. On 08/04/2018: The factory has installed fire door on all floors except maintenance room on top of stair-1. The door coordinators of all double leaf doors are not working properly. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Refer to issue # 22. | Within 3 months | Corrected
Initial Inspection |  | 2 | Unsealed penetrations and openings are located in the exit stair enclosures. Location: North side stair no-2 each floor. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separations. | Completed | Aug 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: Corrected. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Refer to issue # 22. | Within 3 months | Corrected
Initial Inspection |  | 3 | Unsealed penetrations and openings are located in the fire rated floor/ceiling assemblies. Location: Sub-station room to storage area & store room to egress path on ground floor, production floor on 2nd & 3rd floor. | Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | Completed | Aug 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: Corrected. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Egress doors/gates with locking features not complying with NFPA101 are provided at building. Location: Ground floor & roof. | Remove locking features from all egress doors/gates. If locks are required for security reasons, utilize specialized door locking features complying with NFPA101. | Completed | Apr 8 2017 | On 08/08/2017: Corrected as per site conditions. On 15/11/2017: Corrected as per site observations. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. Non-compliant locking features were not observed with exit doors. | Immediately | Corrected
Initial Inspection |  | 5 | Storage was located in all exit stairs & ramp enclosure ( machine storage) on ground floor. | Remove/relocate (separate by fire rated construction for idle machine room) storage from the exit stairs and egress path. | Completed | Jun 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: Corrected as per site observations. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 6 | Parapets or guards are not provided in the roof accordance with Accord standard. | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | Completed | Aug 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: Corrected. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 7 | Automatic fire alarm & detection system installation requires detailed review to confirm compliance with NFPA 72 and ACCORD standards. Still few areas are out of detection system. | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the ACCORD for review and approval. | Submitted | Aug 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: It was same as it was before. On 08/04/2018: Factory has submitted proposed drawing of fire alarm system to Accord for review on 27/02/2018. Note: Installation work is 80 % done. On 16/10/2018: Fire alarm installation work is underway. On 03/09/2019: Installation of fire alarm system is underway. On 16-Mar-25: Ownership of this factory has been changed from "PRM FASHIONS PVT. LTD" to "Bestec BD Ltd." . Current owner rented this factory from BEPZA in May-2024 and enlisted to RSC as an independent factory on January-2025. Reportedly, they were unable to collect the Accord's approved drawing of FADS from the previous factory. However, Installation was found almost completed. Few areas were found without devices. FACP was found in normal condition. The factory has to prepare the design drawing and submit to RSC for initial review. On 30-Dec-25: The factory has got the rejected FADS drawing with some observations on 24-Dec-2025. The factory is actively working to address the observations and reportedly, will submit the revised initial drawing within 10-Jan-2026 to RSC for review. The FADS was found installed and the FACP was found in normal condition during the inspection. RPO Comments: On 25-Feb-2026, the design documents (FADS scanned copy) are pending to be submitted to RSC. | Within 3 months | In Progress
Initial Inspection |  | 8 | The existing building has an occupied floor greater than 10 meter (33 feet) and requires standpipe system detailed review to confirm compliance with NFPA 14 and ACCORD standards. | Submit the as-built design of standpipe system throughout the building in accordance with NFPA 14. | Submitted | Aug 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: It was same as it was before. On 08/04/2018: Factory has submitted proposed drawing of standpipe system to Accord for review on 27/02/2018. Note: Factory has already installed negative suction pump. On 16/10/2018: Drawing has been reviewed for positive suction pump by Accord but re-installation work of fire pump is not started yet. Standpipe installation work is underway. On 03/09/2019: Factory has modified the water reservoir tank and underground fire pump room construction is underway. On 16-Mar-25: Ownership of this factory has been changed from "PRM FASHIONS PVT. LTD" to "Bestec BD Ltd." . Current owner rented this factory from BEPZA in May-2024 and enlisted to RSC as an independent factory on January-2025. Reportedly, they were unable to collect the Accord's approved drawing of SUPS from the previous factory. However, Installation was found almost completed. Angle valve was installed more than 5 feet from the floor finished level. The factory has to prepare the design drawing and submit to RSC for initial review. On 30-Dec-25: The factory has got the rejected SUPS drawing with some observations on 24-Dec-2025. The factory is actively working to address the observations and reportedly, will submit the revised initial drawing within 10-Jan-2026 to RSC for review. The standpipe and hose system as well as fire pump was found installed during the inspection. RPO Comments: On 25-Feb-2026, the design documents (SUPS scanned copy) are pending to be submitted to RSC. | Within 3 months | In Progress
Initial Inspection |  | 9 | Fire pump installation requires detailed review to confirm compliance with NFPA 20 and ACCORD standards. | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the ACCORD for review and approval. | Submitted | Aug 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: It was same as it was before. On 08/04/2018: Factory has submitted proposed drawing of standpipe system to Accord for review on 27/02/2018. Note: Factory has already installed negative suction pump. On 16/10/2018: Drawing has been reviewed for positive suction pump by Accord but re-installation work is not started yet. On 03/09/2019: Factory has modified the water reservoir tank and underground fire pump room construction is underway. On 16-Mar-25: Ownership of this factory has been changed from "PRM FASHIONS PVT. LTD" to "Bestec BD Ltd." . Current owner rented this factory from BEPZA in May-2024 and enlisted to RSC as an independent factory on January-2025. Reportedly, they were unable to collect the Accord's approved drawing of SUPS from the previous factory. However, Installation was found almost completed. Angle valve was installed more than 5 feet from the floor finished level. The factory has to prepare the design drawing and submit to RSC for initial review. On 30-Dec-25: The factory has got the rejected SUPS drawing with some observations on 24-Dec-2025. The factory is actively working to address the observations and reportedly, will submit the revised initial drawing within 10-Jan-2026 to RSC for review. The standpipe and hose system as well as fire pump was found installed during the inspection. RPO Comments: On 25-Feb-2026, the design documents (SUPS scanned copy) are pending to be submitted to RSC. | Within 3 months | In Progress
Initial Inspection |  | 10 | Inspection, testing, and maintenance (ITM) for the fire detection system is not in accordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | Submitted | Aug 2 2017 | On 08/08/2017: The factory management shall have to keep written records on-site, in accordance with NFPA 72. On 15/11/2017: The factory management is keeping written records & it will be completed after T&C. On 08/04/2018: The factory management is keeping written records for existing fire alarm system & it will be verified during T&C. On 16/10/2018: Installation work is underway and factory is maintaining ITM record for fire alarm system and it will be verified during T&C. On 03/09/2019: It is an integrated part of fire alarm system. On 16-Mar-25: It is an integrated part of fire alarm system. On 30-Dec-25: It is an integrated part of fire alarm system. RPO Comments: On 25-Feb-2026, the design documents (FADS scanned copy) are pending to be submitted to RSC. | Within 3 months | In Progress
Initial Inspection |  | 11 | Inspection, testing and maintenance (ITM) of the standpipe system is not in accordance with NFPA 25. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 25 and ACCORD standards. | Submitted | Aug 2 2017 | On 08/08/2017: The factory management shall have to keep written records on-site, in accordance with NFPA 25. On 15/11/2017: The factory management is keeping written records & it will be completed after T&C. On 08/04/2018: The factory management is keeping written records for existing standpipe system & it will be verified during T&C. Installed pump takes negative suction. On 16/10/2018: Installation work is underway and factory is maintaining ITM record for standpipe system and it will be verified during T&C. On 03/09/2019: It is an integrated part of standpipe system. On 16-Mar-25: It is an integrated part of standpipe system. On 30-Dec-25: It is an integrated part of standpipe system. RPO Comments: On 25-Feb-2026, the design documents (SUPS scanned copy) are pending to be submitted to RSC. | Within 3 months | In Progress
Initial Inspection |  | 12 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10 and ACCORD standards. | Completed | Aug 2 2017 | On 08/08/2017: The factory management shall have to keep written records on-site, in accordance with NFPA 10 Chapter 7. On 15/11/2017: Corrected. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | The directional signs are not provided where there is a change in direction and where the continuation of the egress path is not obvious. | Install illuminated directional sign where there is a change in the direction of the path of travel. | Completed | Jun 2 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: The factory has started to install illuminated direction sign where is required. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 14 | Manual on-off switch facility available for emergency lights/exit signs. | Remove manual on/off switches from emergency lighting units/ exit signs to prevent them from being switched off. | Completed | Apr 10 2017 | On 08/08/2017: No action has been taken yet. On 15/11/2017: The factory has started to remove manual on-off switch from emergency lights. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 15 | Inspection, testing, and maintenance (ITM) for the emergency lighting system were not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Completed | Aug 2 2017 | On 08/08/2017: Corrected. On 15/11/2017: Corrected. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Refer to issue # 28. | Within 3 months | Corrected
Initial Inspection |  | 16 | Emergency lighting did not function in test mode (burned out, broken, etc.). Several fog light on aisles. | Regularly test the emergency lighting system on each floor and replace/repair lights as needed. | Completed | Jul 2 2017 | On 08/08/2017: Several fog light was not work in test mode. On 15/11/2017: Corrected as per site observations. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 17 | New finding on 08/08/2017: Storage was located in the egress path & in exit stair. Location: most of the stair & floor. | Remove storage from the exit stairs and egress path | Completed | Aug 15 2017 | On 15/11/2017: Corrected as per site observations. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Corrected. On 30-Dec-25: Corrected. Means of egress was found free from any storage materials. | Immediately | Corrected
Follow Up Inspection |  | 18 | New finding on 08/08/2017: Areas used for combustible storage are not separated by fire-rated construction. Dining room & 1st floor-finished goods. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Completed | Sep 7 2017 | On 15/11/2017: Corrected as per site observations. On 08/04/2018: Follow the finding no 20. On 16/10/2018: Follow the finding no 20. On 03/09/2019: Follow the finding no 20. On 16-Mar-25: Follow the finding no 20. On 30-Dec-25: Follow the finding no 20. | Within 1 month | Corrected
Follow Up Inspection |  | 19 | New finding on 08/08/2017: Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | On Going | Sep 7 2017 | On 15/11/2017: Corrected as per site observations. On 08/04/2018: Corrected. On 16/10/2018: Corrected. On 03/09/2019: Corrected. On 16-Mar-25: Issue re-opened. Based on the number and location of emergency lights observed, adequate illumination levels were not anticipated along egress routes at all floor of production building. On 30-Dec-25: The factory has increased the numbers of emergency lights, but based on the number and location of emergency lights observed, adequate illumination levels were not anticipated along egress routes at all the floors of production building. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 20 | New finding (3rd follow-up): Areas used for combustible storage are not separated by fire-rated construction. Location: Finishing section on 1st floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | In Progress | May 10 2018 | On 16/10/2018: Non-compliant storage areas have been found on 1st floor finishing section. On 03/09/2019: Non-compliant storage areas have been found on 1st floor finishing section. On 16-Mar-25: No progress action has been observed since the last inspection. Storage areas were not as per recommendation on 1st floor and 2nd floor with others occupancies during the inspection. On 30-Dec-25: No significant progress has been observed since the last inspection. The combustible storages on 1st and 2nd floor were found neither separated from the adjacent others occupancies by fire rated construction and opening protective, nor provided defined storage area as per recommendations. In-process storage shall not exceeds 10% of floor area. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 21 | New finding (4th follow-up): Door coordinators of all double leaf door are not functional on all floors. | Factory shall have to ensure that all the double leaf doors are closing properly. | In Progress | Nov 20 2018 | On 03/09/2019: No action has been taken yet. On 16-Mar-25: No progress action has been observed since the last inspection. Door coordinators of all double leaf fire doors were found non-functional on all floors during the inspection. On 30-Dec-25: No progressive action has been observed since the last inspection. Door coordinators of all the double leaf fire doors were found non-functional on all floors during the inspection. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 22 | New finding (6th follow-up): The exit stair enclosure is not separated from work areas and other spaces on each floor by fire-rated construction( storage in ramp area, non-functional fire rated doors, unsealed penetrations due to cable tray, glass window opening from wastage godown, lift machine room). Location: Exit stair-1 & 2 on each floor. | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1-hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated fire rated barrier construction for building with 3 or fewer stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Penetrations into and through an exit enclosure shall be prohibited with the exception of required exit doors, sprinkler piping, standpipes, electrical raceway for fire alarm equipment, and electrical conduit serving the exit enclosure. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | In Progress | Jun 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: No significant progress has been observed since the last inspection. Wastage godown has been demolished from the adjacent glass window opening of exit stair-2. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 23 | New finding (6th follow-up): Office (F1) arrangement is found more than 10 percent of main occupancy (Cutting section-G2) at 2nd floor without fire separation. Location: 2nd floor. | Office (F1) shall be separated from the cutting section (G2) by 3 hr. fire rated construction and 3 hr. fire rated doors as per BNBC Table-3.2.1. Or, Reduce the office occupancies within 10 percent to the main occupancy/cutting section that shall be considered accessory occupancy to the main occupancy of the story in which they occur and no fire separation is required in accordance with section 3.4.2 of RSC Technical Guidelines (Standard)¹ V1.0 . | In Progress | Jun 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: No progress has been observed since the last inspection. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 24 | New finding (6th follow-up): Dining (E4 occupancy) area is not separated from production (G2 occupancy) with fire rated assemblies (non-functional fire doors, cable penetration, no direct exit). Location: 3rd floor. | Separate the dining area from other occupancies with 3-hr fire rated construction, provide minimum 3-hr. rated doors for the openings and seal the unprotected penetrations. Provide required exits that lead directly to the street or exit stairwell or leading to a corridor or open space. | In Progress | Jun 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: No progress has been observed since the last inspection. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 25 | New finding (6th follow-up): LPG gas cylinders were found within the factory premise adjacent to main building and gas boiler room Location: Gas Boiler Shed. | LPG/CNG cylinders are permitted to be stored in a separate dedicated building on the factory premises within its boundaries if the building meets the following conditions: 1. The storage building must be at least 3 meters away from any other building and boundaries. 2. The exterior walls of the building must have a fire resistance rating of 3 hours using noncombustible construction. 3. Doors and other openings in the exterior walls must be protected with suitable closing devices having a fire protection rating of 3 hours. 4. The building is to be used for no other purpose than the storage of LPG/CNG cylinders. 5. The building must be mechanically ventilated to control the accumulation of flammable vapors. 6. The installations must be approved and accepted by the requirements of the AHJ, Gas supply company regulations, manufacturers/supplier’s instructions/ guidance, CIOB and all other applicable agencies, codes and standards. | We already applied to BEPZA for gas connection.(In Progress) | Jun 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: No progress has been observed since the last inspection. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 26 | New finding (6th follow-up): Building does not have stair/floor level designation signs at required locations on all floors. Location: Production Building. | Provide stair designation sign at each floor entrance from the stair to the floor in English and Bengali. Signs shall indicate the name of the stair and the floor level. Signs shall be posted adjacent to the door in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.9.3. | Facelity management provided each floor entrance from the stair to the floor in English and Bengali. Signs with indicate the name of the stair and the floor level. Signs shall be posted adjacent to the door in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.9.3.(In Progress) | Apr 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: The factory has provided the stair designation sign at all floors except top floor. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 27 | New finding (6th follow-up): Illumination level of exit signs and directional signs are found inadequate. Exit signs are found missing at storage in ramp area. Also directional signs are not provided adequately where direction of the path of travel to an exit has changed. Location: Production Building and others shed. | Lighted exit signs shall be placed at entrance to an exit. Additionally, directional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated as per standard. | On Going | Jun 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: Exit signs were not provided at storages in ramp area. Directional signs were increased where direction of the path of travel to an exit has changed. But exit sign and directional sign were found less illumination than required as per standard. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 28 | New finding (6th follow-up): Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with the RSC standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC standard. Keep written records on-site. | On Going | Apr 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: Inspection, testing, and maintenance for the exit sign and emergency lighting system was not found. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 29 | New finding (6th follow-up): Unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies due to plumbing pipe in toilet areas. Location: All floor of production building. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's guideline. or, Provide a minimum 2-hr fire rated shaft to separate the plumbing pipe from each floor if required. | On Going | Jun 16 2025 | On 16-Mar-25: New Finding. On 30-Dec-25: The factory has closed some opening in toilet area, but still few penetrations were found which are not sealed as per standard. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Follow Up Inspection |  | 30 | New finding (7th follow-up): Storage areas discharge directly into the exit stair enclosures. The ramp area in exit stair enclosure-1 is currently used as storages at all floors. Location(s): Ground to 5th floor with exit stair-1, and ground to 1st floor with exit stair-2. | Openings from exit enclosure to Storage areas/ basements/ transformer rooms/ generator rooms/ boiler rooms and similar normally unoccupied spaces shall be provided with a vestibule with fire rated construction and openings in accordance with section 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a min 1-hr fire rated door on the exit stair side and a 1.5 hr. fire rated door on the Store, generator, sub-station room side . Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure as per RSC Technical Guidelines (Standard)¹ V1.0. section 6.14.3. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. | On Going | Mar 30 2026 | On 30-Dec-25: New Finding. RPO Comments: On 25-Feb-2026,The corrective action plan should be completed within the accepted timeline. | Within 3 months | In Progress

## Electrical
Date
20-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Bestec BD Ltd. (Previously PRM FASHIONS PVT. LTD.), SS SFB #5, SECTOR # 3, KARNAPHULI EXPORT PROCESSING ZONE, CHITTAGONG-4204, BANGLADESH., Chattogram, Chittagong
Date of Inspection |  | 2017-04-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has less reflection in existing Electrical Single Line Diagram (SLD). | Electrical SLD must be updated properly; all the required information must be mentioned there; and it shall be updated when you do substantial amount of changes of your electrical system. | 25 March-2026 will be completed. | Oct 9 2017 | On 08/08/2017:Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017:SLD implementation work is going on. Not corrected yet. On 08/04/2018 :Not corrected. On 16/10/2018:SLD drawing is not updated properly. Not corrected yet. On 03-Sep-2019: Not Corrected. On 16-Mar-2025: Updated as-built SLD is missing. Factory need to submit updated as-built SLD to RSC for review. On 30/12/2025: SLD was reviewed by RSC on 07-Sep-2025 and status was "Need Modification". Factory has not been submitted the revised SLD yet. Only 15% work progress has been observed. Not corrected. RPO Comments on 25-Feb-2026: the revised design documents (SLD) are pending to be submitted to RSC. | 2 Months | In Progress
Initial Inspection |  | 2 | Lightning Protection System (LPS) drawing is unavailable. | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is more than 40). Once a LPS is designed properly, installation must be done accordingly asap. | Completed | Oct 9 2017 | On 08/08/2017: LPS Drawing is found but not sufficient for the entire factory. Not corrected. Time extension is given till 10/09/2017. On 15/11/2017: Installation works been started. Not corrected yet. On 08/04/2018 : Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record and significantly lower sized cables' record shall be avoided. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Not performed for all required cables. Not corrected yet. On 08/04/2018 : Corrected. | 2 Months | Corrected
Initial Inspection |  | 4 | Earth pits are not identifiable and number of earth pits are inadequate for the factory. | Each earth pit shall be properly identifiable and marked for periodic maintenance. Adequate number of earth pits must be ensured for the factory with proper earth lead and earth electrode size as mentioned in BNBC requirements. mixing all together shall be avoided. | 15 March-2026 will be completed. | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Works been started but not finished yet. Not corrected. On 08/04/2018 : Not corrected. Please maintain test report for all pits as per standard format and provide adequate size. On 16/10/2018: ER test report format is improper. Not corrected yet. On 03-Sep-2019: Not Corrected. On 16-Mar-2025: Earth pit layout is not available and earth pits are not identified yet. On 30/12/2025: Earth pit layout is mismatched with the field condition and SLD. As the earth pits are buried under concrete and soil, it is difficult to identify them. Not corrected. RPO Comments on 25-Feb-2026: the revised design documents (SLD) are pending to be submitted to RSC. | 2 Months | In Progress
Initial Inspection |  | 5 | Electric safety training program has not initiated/ conducted. | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory has to continue to improve the overall electrical safety situation for the staffs. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Corrected. | 1 Months | Corrected
Initial Inspection |  | 6 | Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ busbar. | Each electrical circuit must be terminated at single MCB/ MCCB terminals. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Not corrected yet. On 08/04/2018 : Corrected. | 2 Months | Corrected
Initial Inspection |  | 7 | Cable connected to busbar/ MCCB/ MCB terminal without cable lug. | Each electrical circuit must be terminated at single busbar/ MCB/ MCCB terminals using cable lug. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Works been started but not finished yet. Not corrected yet. On 08/04/2018 : Corrected. | 2 Months | Corrected
Initial Inspection |  | 8 | Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Not corrected yet. On 08/04/2018 : Not corrected. On 16/10/2018: Corrected. | 1 Months | Corrected
Initial Inspection |  | 9 | Inadequate working space around (or in front of) board/ panels and access to the board/ panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/ panel. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Not corrected yet. On 08/04/2018 : Corrected. | 2 Months | Corrected
Initial Inspection |  | 10 | Distribution Board's top/ bottom is left open (typical issue). | Each electrical distribution board/ panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Not corrected yet. On 08/04/2018 : Not corrected. On 16/10/2018: Corrected. | 2 Months | Corrected
Initial Inspection |  | 11 | Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 12 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. | Completed | Feb 6 2017 | On 08/08/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Phase barrier/ separators are missing in MCCBs. | Phases must be separated by insulator ( a rubber type no-flammable materials shall be used for it). | Completed | Oct 4 2017 | On 08/08/2017: Corrected. | 2 Months | Corrected
Initial Inspection |  | 14 | Flexible PVC pipe is used to cover power and signal cable for boiler. | Power and signal cable for boilers shall be distributed using proper type insulator to avoid damage of cables. | Completed | Feb 7 2017 | On 08/08/2017: Corrected. | 2 Months | Corrected
Initial Inspection |  | 15 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Not corrected yet. On 08/04/2018 : Not corrected. On 16/10/2018: Corrected. | 2 Months | Corrected
Initial Inspection |  | 16 | Wooden support used for electrical installation/ element. Electrical rotatory device have been installed unsafely | Replace wooden support and it is preferable to fix each electrical devices with noncombustible support. Adequate and proper safety measures must be taken for all the rotary type installation. | Completed | Oct 4 2017 | On 08/08/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 17 | Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Completed | Feb 6 2017 | On 08/08/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 18 | Panel/ Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/ panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | Completed | Feb 7 2017 | On 08/08/2017: Corrected. | 2 Months | Corrected
Initial Inspection |  | 19 | Meters and other electrical devices (Ammeter, Voltmeter) not operational on the main electrical equipment. | Different type meters and other electrical devices shall be operational in the main electrical distribution board/ panel. | Completed | Feb 7 2017 | On 08/08/2017: Corrected. | 2 Months | Corrected
Initial Inspection |  | 20 | Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 21 | Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Completed | Oct 9 2017 | On 08/08/2017: Not Corrected. Time extension is given till 10/09/2017. On 15/11/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Inadequate earth cable connected to generator frame. | Two separate earth connection & one separate and distinct Neutral connection must be provided over generator. Generator body must have earth connection with half of phase conductor/follow manufacturer/suppliers recommendation. | Completed | Sep 20 2017 | On 15/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Loop connection has been used powering multiple circuits through MCB/ MCCBs. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity). | Completed | Sep 20 2017 | On 15/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Completed | Sep 20 2017 | On 15/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: HT Cable dropping from 11kV OH line wire is used instead of DO Fuse. | Replace the wire with standard DO fuse. | Completed | Dec 31 2017 | On 08/04/2018 : Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Maintenance movement is obstacle due to uneven height of cable trench in utility area (Generator room). | Work place around generator (or other electrical installation) must be on same height. | Completed | Dec 31 2017 | On 08/04/2018 : Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: List of circuit or SLD of existing circuits are not available on each electrical panel/ board (Typical). | List of circuit or SLD of respective circuits shall be available for each electrical panel/ board. | Completed | Dec 31 2017 | On 08/04/2018 : Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record and significantly lower sized cables' record shall be avoided. | 25 April-2026 will be completed. | Nov 30 2018 | On 03-Sep-2019: Document is not found during inspection. Not Corrected. On 16-Mar-2025: Insulation resistance test is not conducted yet. On 30/12/2025: No insulation resistance test report is found. No progress has been observed. Not corrected. RPO Comments on 25-Feb-2026: The factory management is asking for a time extension which is not accepted.The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 29 | New Finding: All meters and other electrical devices (Ammeter, Voltmeter, PFI Auto Controller, etc.) installed on the main electrical equipment are not operational. | Ensure meters and other electrical devices installed on the main electrical equipment are operational. | Completed | Nov 30 2018 | On 03-Sep-2019: Not Corrected. On 16-Mar-2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Inadequate working space around (or in front of) board/ panels and access to the board/ panels is obstacles. | At least 1 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Done | Nov 30 2018 | On 03-Sep-2019: Not Corrected. On 16-Mar-2025: Adequate working clearance is not found in front of electrical board/panel. On 30/12/2025: Same condition found as in the previous follow-up inspection. Working clearance in front of each DB is not maintained. Not corrected. RPO Comments on 25-Feb-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 31 | New Finding: Distribution Board's top/ bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | 15 March-2026 will be completed. | Oct 15 2019 | On 16-Mar-2025: Distribution board's top/ bottom is still left open. On 30/12/2025: This issue still persists in many DBs. Not corrected. RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 32 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | 25 March-2026 will be completed. | Oct 15 2019 | On 16-Mar-2025: Hot Spots are still exist at several points. On 30/12/2025: Hot spots are found in SDB -Compressor. Not corrected. RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 33 | New Finding: Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. | Done | Oct 15 2019 | On 16-Mar-2025: Lint/dust is found inside of the DB. On 30/12/2025: Lint/dust is still persists inside of the DB. Not corrected. RPO Comments on 25-Feb-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 34 | New Finding: Circuit is drawn from bus bar without any protective means. | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). | Completed | Oct 15 2019 | On 16-Mar-2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | For factory buildings with a Risk Index of 40 or higher, a comprehensive Lightning Protection System (LPS) required to be designed as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | Done | Sep 16 2025 | On 30/12/2025: Rolling sphere calculation is shown for compressor room, generator room and fire hydrant pump room in the updated LPS drawing but improper. Moreover, air terminals are found missing. Not corrected. RPO Comments on 25-Feb-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 6 Months | Pending Verification
Follow Up Inspection |  | 36 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Electrical maintenance program shall be developed to include regular inspections and testing of electrical systems, focusing on preventive and proactive measures. | 25 March-2026 will be completed. | Apr 16 2025 | On 30/12/2025: Improper programmed schedule and not matched with field. Not corrected. RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 37 | New Finding: Periodicity of earth Pit resistance test record is not continued. | All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. | 25 March-2026 will be completed. | Apr 16 2025 | On 30/12/2025: No earth pit resistance test report is found. Not corrected. RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 38 | New Finding: Thermography scanning report is not available. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. | 25 March-2026 will be completed. | Apr 16 2025 | On 30/12/2025: No thermography scanning report is found. Not corrected. RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 39 | New Finding: Phase barrier/separators are missing in circuit breaker. | Phases must be separated by insulators made from non-flammable rubber-type materials to prevent electrical short circuits and enhance safety. | 25 March-2026 will be completed. | Apr 16 2025 | On 30/12/2025: Phase separator is missing in many areas. Not corrected. RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 40 | New Finding: Loop connection has been used powering multiple circuits through circuit breakers. | No loop connections are allowed. Each cable must be terminated with a single cable lug at each terminal. Combo bus bars are permitted if the incoming cable size meets the rated capacity. | Completed | May 16 2025 | RPO Comments on 04-Jun-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. On 30/12/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 41 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation, with a thickness of at least 3 mm for rubber mats, must be provided at the working area of each electrical installation. Length of the mat shall be equal to 1 meter or the width of the board/panel, whichever is greater. This includes areas of LT panels, MDBs, DBs, SDBs, and other manually operated machinery to ensure safety and prevent electrical hazards. | Done | Apr 16 2025 | On 30/12/2025: Rubber mat size is inadequate. Not corrected. RPO Comments on 25-Feb-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 42 | New Finding: Water bottle/ combustible/flammable materials are attached with electrical panel board/BBT/cable channel/duct. | All flammable and combustible materials, including water bottles and other items, must be cleared from electrical cable channels, ducts, and BBTs. Separate storage arrangements for these materials should be implemented. | Completed | May 16 2025 | RPO Comments on 04-Jun-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. On 30/12/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: Wooden support used for electrical installation/ element. | Replace wooden support and each electrical devices shall be fixed with non-combustible support. | Completed | Apr 16 2025 | RPO Comments on 04-Jun-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. On 30/12/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Hazardous lights in storeroom / storage areas are uncovered. | Lights in storerooms/storage areas classified as hazardous shall be covered with appropriate materials, or non-hazardous lights shall be installed in these areas. | Completed | Apr 16 2025 | RPO Comments on 04-Jun-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. On 30/12/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Power sockets are kept on floor/hung without support. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200mm above the floor level. | 25 March-2026 will be completed. | May 16 2025 | On 30/12/2025: Power sockets are still kept on floor. Not corrected. RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 46 | New Finding: Lead acid battery terminals are filled left open. | Lead-acid battery terminals must be covered or capped, and any rust must be thoroughly cleaned to ensure safe and efficient operation. | 25 March-2026 will be completed. | Jan 30 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 47 | New Finding: Distribution boards have no clear identification markings. | Clearly mark all distribution boards, switchboards, sub-main boards, and switches for identification. | On Going | Feb 28 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 48 | New Finding: Indicator lights are mounted without disconnecting device. | Indicator lights must be connected through a control device, such as a rated fuse or Circuit Breaker (CB), to ensure they are properly protected and can be safely operated. | On Going | Feb 28 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 49 | New Finding: Panel doors are not connected with earth. | All metal components within the electrical system must be securely connected to the earth. This earthing is essential to mitigate the risk of electrical shock or electrocution by providing a safe path for fault currents to dissipate. | Done | Jan 30 2026 | RPO Comments on 25-Feb-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 50 | New Finding: Multiple cables from different electrical consumers are terminated at circuit breaker terminals or busbars. | Each electrical circuit must be terminated at a single circuit breaker terminal or busbar to ensure distribution and protection within the electrical system. | On Going | Feb 28 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 51 | New Finding: Non rated and non-certified comb bar used for powering multiple MCB. | For connecting multiple MCB use rated and listed comb bar. | On Going | Feb 28 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 52 | New Finding: Earthing bar installed on insulator. Panel body is not connected to earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | 25 March-2026 will be completed. | Jan 30 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 53 | New Finding: Metering devices (ammeter, voltmeter) installed on panel board are not operational. | All indicator lamps and metering devices installed on the panel board must be fully operational to prevent the risk of false or misleading information, which could compromise the safety and proper functioning of the electrical system. Regular checks and maintenance should be conducted to ensure their accuracy and reliability. | On Going | Feb 28 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 54 | New Finding: Cables joint or tapping do not have adequate insulation and mechanical strength. | Cable joints shall be made through porcelain/PVC connectors with PIB tape wound around the joint in respect of conductivity, insulation, and mechanical strength. | 25 March-2026 will be completed. | Jan 30 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress
Follow Up Inspection |  | 55 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Each manually operated machine, accessible to users/operators, must be equipped with an earth connection. Cable selection should be based on the protective device's response and the power demand of the circuit. | 25 March-2026 will be completed. | Jan 30 2026 | RPO Comments on 25-Feb-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 1 Month | In Progress