## Structural
Date
07-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | CORETEX APPARELS LTD., Holding # 160/1, Madhabpur, Kashimpur Metro, Gazipur-1349,, Dhaka
Date of Inspection |  | 2023-11-26
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Columns appear to exceed Euler force. (Main Production Building). | The building engineer is required to update the DEA documents. | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 3, 2026 | Feb 10 2024 | On 18-Sep-2024: This issue has been covered in DEA report. Factory has submitted the DEA documents to RSC. As per the latest review comments, the factory is required to submit a revise DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | Within 6 weeks | In Progress
Initial Inspection |  | 2 | Columns appear to exceed Euler force. (Main Production Building). | Carry out suggested remedial works if required. | This issue related with DEA. After getting DEA approval from RSC all remedial works ( if required ) we'll completed accordingly. | Feb 10 2024 | On 18-Sep-2024: Remedial works required to be carried out after getting acceptance from RSC (if any). RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 months | In Progress
Initial Inspection |  | 3 | Inconsistency in DEA documents and as-built drawing. (Main Production Building). | The building engineer is required to survey the full structure and produce accurate as-built drawings. | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 03, 2026 | Dec 25 2023 | On 18-Sep-2024: Building engineer produced as-built drawings as part of DEA. During inspection, inconsistencies have been found in column schedule drawings. Building engineer is required to update the as-built drawings as per review comments and closing meeting notes and submit to RSC by 26th September, 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | Within 6 weeks | In Progress
Initial Inspection |  | 4 | Inconsistency in DEA documents and as-built drawing. (Main Production Building). | Incorporate all the concrete core test report. | This issue is Corrected by RSC 1st Follow up inspection on 18th Sep-24. | Dec 25 2023 | On 18-Sep-2024: Eigth core layout was verified on-site and all core test was incorporated in DEA. | Within 6 weeks | Corrected
Initial Inspection |  | 5 | Inconsistency in DEA documents and as-built drawing. (Main Production Building). | The building engineer is required to review the DEA documents based on in-situ material strength & software-based analysis and submit the documents to RSC for review. | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 03, 2026 | Feb 10 2024 | On 18-Sep-2024: This issue has been covered in DEA report. Factory has submitted the DEA documents to RSC. As per the latest review comments, the factory is required to submit a revise DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | Within 6 weeks | In Progress
Initial Inspection |  | 6 | Inconsistency in DEA documents and as-built drawing. (Main Production Building). | Produce and manage the load plan as per BNBC. | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 03, 2026 | Feb 10 2024 | On 18-Sep-2024: Factory prepared a load plan (3kPa for production floor) and posted on site. The load plan has been submitted as part of DEA to RSC. As per latest review comments, the factory is required to submit revised DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | Within 6 weeks | In Progress
Initial Inspection |  | 7 | Inconsistency in DEA documents and as-built drawing. (Main Production Building). | Implement the floor loading plan | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 3, 2026 | Feb 10 2024 | On 18-Sep-2024: The load plan has submitted as part of DEA to RSC. The factory shall maintain the final load plan after receiving acceptance from the RSC. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 months | In Progress
Initial Inspection |  | 8 | Non-structural elements not anchored or braced (Main Production Building) | Building engineer is required to adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC | This issue is Corrected by RSC 1st Follow up inspection on 18th Sep-24. | Dec 25 2023 | On 18-Sep-2024: During the inspection, the non-structural elements (racks) were found anchored on the brick wall. | within 6 weeks | Corrected
Initial Inspection |  | 9 | Column susceptible to vehicle impact (Main Production Building) | The factory engineer is required to take necessary measures to prevent the vehicle impact by providing barrier around the columns. | This issue is Corrected by RSC 1st Follow up inspection on 18th Sep-24. | Dec 25 2023 | On 18-Sep-2024: During the inspection, columns have been found protected from vehicle impact by steel angle barrier. | within 6 months | Corrected
Initial Inspection |  | 10 | Discrepancies in as built drawings. (Admin Building) | The building engineer is required to survey the full structure and produce accurate as-built drawings | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March03, 2026 | Feb 10 2024 | On 18-Sep-2024: Building engineer produced as-built drawings as part of DEA and submitted to RSC. As per the latest review comments, the factory is required to submit revised DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 weeks | In Progress
Initial Inspection |  | 11 | Discrepancies in as built drawings. (Admin Building) | The building engineer is required to revise the design documents based on actual site condition. | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 3, 2026 | Apr 20 2024 | On 18-Sep-2024: This issue has been covered in DEA report. Factory has submitted the DEA documents to RSC. As per the latest review comments, the factory is required to submit a revise DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 months | In Progress
Initial Inspection |  | 12 | Lack of edge protection (Admin Building). | Building is required to provide edge protection on the roof and stair to avoid falling hazard. | Already we have provide edge protection on the roof edge protection to avoid falling hazard. | Feb 15 2024 | On 18-Sep-2024: During the inspection, edge of stairs were found to be protected by railing but roof edge not protected. Roof edge protection is required as soon as possible. RPO Comments: On 7-May-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | within 6 weeks | Pending Verification
Initial Inspection |  | 13 | Exposed re-bar at roof. (Admin Building). | All exposed reinforcement is to be protected from corrosion which may cause degradation of the concrete. | This issue is Corrected by RSC 1st Follow up inspection on 18th Sep-24. | Dec 25 2023 | On 18-Sep-2024: During the inspection, exposed reinforcement was protected by anti-corrosive paint. | within 6 weeks | Corrected
Initial Inspection |  | 14 | Discrepancies in as built drawings. (Warehouse Building) | The building engineer is required to survey the full structure and produce accurate as-built drawings. | This issue is Corrected by RSC 1st Follow up inspection on 18th Sep-24. | Dec 25 2023 | On 18-Sep-2024: Building engineer produced as-built drawings as part of DEA and as-built drawing was found satisfactory with on-site condition. | within 6 weeks | Corrected
Initial Inspection |  | 15 | Discrepancies in as built drawings. (Warehouse Building) | The building engineer is required to revise the design documents based on actual site condition. | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 3, 2026 | Apr 15 2024 | On 18-Sep-2024: This issue has been covered in DEA report. Factory has submitted the DEA documents to RSC. As per the latest review comments, the factory is required to submit a revise DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 months | In Progress
Initial Inspection |  | 16 | Lack of edge protection (Warehouse Building). | Building is required to provide edge protection on the roof and stair to avoid falling hazard. | This issue is Corrected by RSC 1st Follow up inspection on 18th Sep-24. | Feb 15 2024 | .On 18-Sep-2024: During the inspection, edge of stairs were found to be protected by railing. | within 6 weeks | Corrected
Initial Inspection |  | 17 | Exposed re-bar at roof. (Warehouse Building). | All exposed reinforcement is to be protected from corrosion which may cause degradation of the concrete. | This issue is Corrected by RSC 1st Follow up inspection on 18th Sep-24. | Dec 25 2023 | .On 18-Sep-2024: During the inspection, exposed reinforcement was protected by anti-corrosive paint. | within 6 weeks | Corrected
Initial Inspection |  | 18 | Lack of Design Report. (Utility Building) | The building engineer is required to prepare a set of design documents including as built drawings and a design report as per BNBC | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 3, 2026 | Feb 15 2024 | On 18-Sep-2024: Building engineer prepared DEA documents. Factory has submitted the DEA documents to RSC. As per the latest review comments, the factory is required to submit revised DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 weeks | In Progress
Initial Inspection |  | 19 | Lack of Design Report. (Utility Building) | Carry out remedial works if required. | This issue related with DEA. After getting DEA approval from RSC all remedial works ( if required ) we'll completed accordingly. | Apr 20 2024 | On 18-Sep-2024: Remedial works required to be carried out after getting acceptance from RSC (if any). RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 months | In Progress
Initial Inspection |  | 20 | Non-engineered shed. (Wastage Shed) | The building engineer is required to check the member, connection & stability system of the roof shed and suggest proper alternatives accordingly. | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 03, 2026 | Feb 15 2024 | On 18-Sep-2024: This issue has been covered in DEA report. Factory has submitted the DEA documents to RSC. As per the latest review comments, the factory is required to submit a revise DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 weeks | In Progress
Initial Inspection |  | 21 | Non-engineered shed. (Wastage Shed) | Carry out remedial works if required. | This issue related with DEA. After getting DEA approval from RSC all remedial works ( if required ) we'll completed accordingly. | Apr 20 2024 | On 18-Sep-2024: Remedial works required to be carried out after getting acceptance from RSC (if any). RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 months | In Progress
Initial Inspection |  | 22 | Lack of Design Report. (Gate House) | The building engineer is required to prepare a set of design documents including as built drawings and a design report as per BNBC | This issue related with DEA which is already submited to RSC on 10th April-24 and we got 1st review comments from RSC on 30th April-24. According to the review comments of RSC our Consultant team are work on it and hope all required documents we'll submited within March 3, 2026 | Feb 15 2024 | On 18-Sep-2024: Building engineer prepared DEA documents. This issue has been covered in the DEA report. Factory has submitted the DEA documents to RSC. As per latest review comments, the factory is required to submit revised DEA by 26th September 2024. RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 weeks | In Progress
Initial Inspection |  | 23 | Lack of Design Report. (Gate House) | Carry out remedial works if required. | This issue related with DEA. After getting DEA approval from RSC all remedial works ( if required ) we'll completed accordingly. | Apr 20 2024 | On 18-Sep-2024: Remedial works required to be carried out after getting acceptance from RSC (if any). RPO Comments: On 22-Apr-2026: the design documents are currently under the RSC’s review. | within 6 months | In Progress

## Fire
Date
07-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | CORETEX APPARELS LTD., Holding # 160/1, Madhabpur, Kashimpur Metro, Gazipur-1349,, Dhaka
Date of Inspection |  | 2023-11-26
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stair enclosures are not separated from work areas and other spaces on each floor by fire-rated construction. | The exit stair enclosure shall be provided with a minimum of 2-hr. fire resistance rating for buildings 4 or more stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2hr. fire rated fire rated barrier construction for building with 4 or more stories Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | This issue relates to the requirement to complete the fire Exit stair openings. We will proceed with the necessary actions and complete the task accordingly by 30 Oct 2026. | Feb 25 2024 | On 17-Dec-25: The factory has installed fire doors at the exit stair enclosures. However, due to non-functional fire doors (fire doors were kept open with external objects), the exit stair enclosures are not yet separated from the floor area. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 2 | Areas & rooms used for combustible storage open to the factory are not separated by fire rated construction. | Separate the dedicated storage rooms by minimum 1-hr fire-rated construction. Provide 0.75 hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated barrier construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.45m (8ft.) , maximum area of 23m2 (250 ft2) and 3m (10ft.) clear distance from adjacent another unenclosed combustible storage. - If the building/floor is sprinkler protected: maximum height of 3.66m (12ft.) and maximum area of 93m2 (1000 ft2). - In-process storage shall not exceed 10 percent of the building area of the story in which they occur. | Done | Dec 30 2023 | On 17-Dec-25: Corrected. In-process storage within the production area was maintained in accordance with the recommendations. | Within 3 months | Corrected
Initial Inspection |  | 3 | Catwalk has been constructed on High rack storage and the area of the intermediate deck creates a full floor where the size of the deck is more than 33% of the total floor area and requires fire rated separation. Location: Wearhouse Building (Ground Floor.) | Remove the catwalk of the intermediate deck. Or, Maintain fire separation (3hr for type 1) between floor to floor as per BNBC 2006 Table 3.3.1. Provide required fire rating on the structural elements by following Table?3.2.4, 3.1.9 & Table 4.4.1 of the RSC Technical Guidelines Standard or Table 3.3.1 of BNBC-2006. Consult a qualified fire protection engineer to design the rated construction barriers in between two floors and in structural members. Factory shall submit all required product datasheet, installation design along with design philosophy to RSC for review prior to installation on site. | Following the guidance provided by RSC, we are planning to rearrange our storage area in order to facilitate the removal of the existing catwalk. This restructuring is intended to enhance safety and optimize the use of available space. We have scheduled the work to be carried out over the coming weeks, and we aim to complete the entire process by 30st August 2026. | Apr 30 2024 | On 17-Dec-25: No action has been taken yet. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 6 months | In Progress
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in the fire rated floor/ceiling assemblies. Location: BBT Riser & Sanitary Pipe. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3- hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's guideline. (Type-1 Construction). or, Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. (Type-1 Construction) | This issue relates to the requirement to complete the fire Unsealed penetrations. We will proceed with the necessary actions and complete the task accordingly by 30 Sep 2026. | Feb 20 2024 | On 17-Dec-25: The factory has installed fire doors at the BBT riser rooms and toilet areas. However, the fire doors were non-functional (non-functional fire door accessories and the gap from the floor level was more than 19 mm), and BBT penetration from the riser room to the production floors is not yet sealed completely. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 5 | Room used for combustible storage are not separated by fire rated construction from Boiler Room. | Separate the storage room by a minimum 1- hr fire rated construction. Seal and/or protected all openings to maintain the required fire separations. | Done | Feb 10 2024 | On 17-Dec-25: Corrected. The storage area has been separated from the boiler room and surrounding occupancies with fire-rated constructions. | Within 2 months | Corrected
Initial Inspection |  | 6 | The structural elements of Main Building 3rd Floor Partial roof is constructed by steel which is non-rated and were found in exposed condition without any fire protection. | The building shall be type-I or II construction. So, provide require rating in the structural elements of the building. Consult with a qualified fire protection engineer. BNBC 2006-Table 3.2.4 | This issue relates to the requirement to complete the fire protection work. We will proceed with the necessary actions and complete the task accordingly by 25 September 2026. | May 20 2024 | On 17-Dec-25: No action has been taken yet. The factory shall prepare a design philosophy of require rating in the structural elements in accordance with BNBC 2020 and submit it to RSC for review. Note: As per the resolution issued by The "Ministry of Housing and Public Works” based on the recommendations from the House Building Research Institute (HBRI) and the Public Works Department (PWD) to assess structural fire protection requirements of steel buildings (unprotected non-combustible construction type) according to BNBC 2020. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 6 months | In Progress
Initial Inspection |  | 7 | Adequate aisles found in the Main Production Building. | Provide minimum aisle widths of 36 inch with proper marking & update on evacuation map. | Done | Dec 30 2023 | On 17-Dec-25: Corrected. Adequate aisles have been provided throughout the Main Production Building. | Within 1 month | Corrected
Initial Inspection |  | 8 | Sliding & inside swing doors found in several areas throughout the factory | Replace all gates and doors along the means of egress with side-hinged, swinging egress doors in accordance with RSC Standard. | Done | Feb 10 2024 | On 17-Dec-25: Corrected. Sliding doors have been removed from the egress routes and the inside swing doors have been used for the toilet areas where the occupant load is less than 50 of the Main Production Building. | Within 2 months | Corrected
Initial Inspection |  | 9 | A single means of egress is provided from (3rd & Occupied Roof) where the occupant load exceeds 49 person. | Provide at least two means of exits leading directly to the street or leading to a corridor or open space having access to exits in two independent and different directions. Dining (E3) is not permitted with moderate hazard occupancies (G2) as per BNBC 2006. | Done | Jan 30 2024 | On 17-Dec-25: Corrected. The Stair-2 (N-E) has been extended up to the occupied roof of the Main Production Building. | Within 3 months | Corrected
Initial Inspection |  | 10 | Compliant Exit Stair not provided at Utility Building 1st Floor. | Provide compliant exits and stairs for this building from top floor to ground floor as per RSC Technical Guidelines (Standard) 6.5.6.2. | This task has already been completed according to the instructions of RSC. | Jan 30 2024 | On 17-Dec-25: The factory has provided a stair for the 1st floor of the Utility Building. However, the width of the exit stair is less than 60 inches. RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 11 | Inadequate emergency lighting units. (Emergency Light, Exit Sign, Directional Exit Light etc.) | Test the emergency lighting system on each floor and provide additional emergency fixtures to supply adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and along exit discharge paths and a minimum 2.5 lux along exit access aisles. Provide exit signs above all building exits to the exterior, all doors to the exit stairs and along all paths of travel where a change of direction is not obvious. | Done | Jan 17 2024 | On 17-Dec-25: Corrected. Adequate illumination of the emergency lighting has been observed in the floor areas along the means of egress. | Within 1 month | Corrected
Initial Inspection |  | 12 | Common path of travel exceeds the permitted limit (23m/ 75ft) at Ground Floor Finishing Section (Main Building). | Reconfigure the egress arrangement to reduce the maximum common path of travel to not more than 23 meter. | Done | Jan 16 2024 | On 17-Dec-25: Corrected. The floor layout has been rearranged, and glass partitions have been removed on the ground floor. The common path of travel was found within the limit during the inspection. | Within 1 month | Corrected
Initial Inspection |  | 13 | Parapets or guards are not provided in occupied/occupiable roof. OR Parapets or guards are provided in occupied roof which is less than 1067mm (42 inch.). | Provide parapets or guards with a minimum height of 1067mm (42 inch.) | Done | Feb 15 2024 | On 17-Dec-25: Corrected. Parapets of adequate height have been provided on the occupiable roof of the Main Factory building. | Within 3 months | Corrected
Initial Inspection |  | 14 | Building did not have stair designation signs and occupant load signs at required locations at all floors. | Provide stair designation signs and occupant load signs at required locations. | This task has already been completed according to the instructions of RSC. | Dec 30 2023 | On 17-Dec-25: The stair designation signs have not yet been provided. RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 months | Pending Verification
Initial Inspection |  | 15 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The RSC standard. | Inspect, test and maintain the emergency lighting system in the accordance with NFPA/RSC. Keep written records on-site. | Done | Dec 30 2023 | On 17-Dec-25: Corrected. The factory is maintaining the ITM of emergency lighting system. | Within 1 months | Corrected
Initial Inspection |  | 16 | The factory has installed Fire alarm and detection system which requires detailed review to confirm compliance with NFPA 72 and RSC Technical Guidelines (Standard). | Submit the proposed design of Addressable fire alarm system to RSC in accordance with NFPA 72. Installation shall be as per the reviewed design with a listed Addressable Fire Alarm System | This issue relates to the requirement to complete the Fire Alarm Detection System (FADS). We will proceed with the necessary actions and complete the task accordingly by 30 August 2026. | Feb 10 2024 | On 17-Dec-25: The fire alarm and detection system initial design has been reviewed by the RSC on 1st Dec 2024. Reportedly, “installation is going on and will be completed by February 2026. The Pre-T&CVI documents will be submitted by February 2026 as well”. The fire alarm and detection system were found active during the inspection. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Design within 2 months and installation within 3 months | In Progress
Initial Inspection |  | 17 | Inspection, testing, and maintenance for the fire detection system is not found in accordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | This task has already been completed according to the instructions of RSC. | Dec 30 2023 | On 17-Dec-25: Integrated with Fire Alarm and Detection System. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month after installation. | In Progress
Initial Inspection |  | 18 | The factory building has an occupied floor greater than 10 meter (33 feet) and installed a standpipe protection system which requires detailed review to confirm compliance with NFPA 14 & 20 and RSC Technical Guidelines (Standard). | Submit the proposed design of Standpipe Protection System to RSC in accordance with NFPA 14 & 20. Installation shall be as per the reviewed design with a listed Standpipe & Fire Pump System. | This issue relates to the requirement to complete the Sprinkler System (SUPS). We will proceed with the necessary actions and complete the task accordingly by 30 August 2026. | Feb 10 2024 | On 17-Dec-25: The fire suppression system initial design has been reviewed by the RSC on 1st Dec 2024. Reportedly, “installation is going on and will be completed by February 2026. The Pre-T&CVI documents will be submitted by February 2026 as well”. The fire suppression system was found active during the inspection. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Design within 2 months, Installation within 3 months | In Progress
Initial Inspection |  | 19 | Inspection, testing and maintenance of the standpipe system is not found in accordance with NFPA 25. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 25. | This task has already been completed according to the instructions of RSC. | Dec 30 2023 | On 17-Dec-25: Integrated with Fire Suppression System. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month after installation | In Progress
Initial Inspection |  | 20 | Inspection, testing, and maintenance for the fire pump is not found in accordance with NFPA 25 or as per Accord standard. | Inspect, test and maintain the fire pump, and keep written records on-site, in accordance with NFPA 25 or as per Accord standard. | This task has already been completed according to the instructions of RSC. | Dec 30 2023 | On 17-Dec-25: Integrated with Fire Suppression System. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month after installation. | In Progress
Initial Inspection |  | 21 | Inspection, testing and maintenance of portable fire extinguishers is not found in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Done | Dec 30 2023 | On 17-Dec-25: Corrected. The factory is maintaining the ITM of portable fire extinguisher. | Within 1 month. | Corrected
Follow Up Inspection |  | 22 | New Finding (1st FUI): Fire evacuation maps are not updated as per site condition. Location: Main Factory Building and Utility Building. | Update the fire evacuation map and shall be posted at the entrance to each exit stair in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 13.3. | This issue relates to the requirement to complete the Evacuation plan. We will proceed with the necessary actions and complete the task accordingly by 10 June 2026 | Jan 17 2026 | On 17-Dec-25: New Finding. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month. | In Progress
Follow Up Inspection |  | 23 | New Finding (1st FUI): Building does not have occupant load signs at required locations on all floors. Location: Main Factory Building and Utility Building. | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.4.4 . | This task has already been completed according to the instructions of RSC. | Jan 17 2026 | On 17-Dec-25: New Finding. RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month. | Pending Verification
Follow Up Inspection |  | 24 | New Finding (1st FUI): Changes in level was found 24 in. where RSC Technical Guidelines (Standard)¹ V1.0 Section 6.9 or 6.10 doesn't meet. Location: Discharge of Stair-1 (South-East) of the Main Factory Building and Admin Building. | Changes in level exceeding 535 mm (21 in.) in elevation shall meet the requirements for stairs in 6.9 or ramps in 6.10. The change in level shall be readily apparent and if not, marked with additional signage or floor markings. | This issue relates to the requirement to complete the Exit Adquacy. We will proceed with the necessary actions and complete the task accordingly by 20 June 2026 | Mar 17 2026 | On 17-Dec-25: New Finding. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months. | In Progress
Follow Up Inspection |  | 25 | New Finding (1st FUI): No guard rail provided for exit discharge. Location: Ground Floor, Admin Building. | Guards shall be provided at all open sides of means of egress that exceed 760 mm (30 in.) above the floor or finished ground below. Guards shall have a minimum height of 1067 mm (42 in.). Open guards shall have intermediate rails or pattern such that a sphere 200 mm (8 in.) in diameter cannot pass through any opening up to a height of 865 mm (34 in.). Guard shall construct in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.12. | This issue relates to the requirement to complete the Exit Adquacy. We will proceed with the necessary actions and complete the task accordingly by 25 June 2026 | Mar 17 2026 | On 17-Dec-25: New Finding. RPO Comments on 22-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months. | In Progress

## Electrical
Date
07-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | CORETEX APPARELS LTD., Holding # 160/1, Madhabpur, Kashimpur Metro, Gazipur-1349,, Dhaka
Date of Inspection |  | 2023-11-26
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | The submitted SLD was reviewed and approved by RSC on 16 May 2024, and it is being maintained in accordance with the approved requirements. | Feb 20 2024 | On 16/05/2024: Not Corrected. Factory have got accepted SLD on 16/05/2024. Need to do some more work to make it as built, load identification and individual overcurrent protection and load identification. On 14/12/2025: Not Corrected. No significant progress has been observed since the last follow-up. As built drawing missing. Mismatches are found between the approved SLD and the actual installation, including load identification, oversized breakers, earthing layout, busbar/cable information, and missing individual protection. RPO Comments: On 22-Apr-2026: There is no pictorial evidence has been received. This items now is in progress. | 3 Months | In Progress
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC). | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Feb 20 2024 | On 16/05/2024: Corrected. | 4 Months | Corrected
Initial Inspection |  | 3 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 30 2024 | On 16/05/2024: Corrected. | 1 Months | Corrected
Initial Inspection |  | 4 | Safety program is initiated but training document is not adequate. | Electrical safety training and awareness program for the electrical personnel must be initiated by qualified Electrical personnel and documented following recognized standards. It is a periodic task which factory must continue to improve the overall electrical safety situation for the staffs. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 30 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 5 | No LOTO (Lock-Out-Tag-Out) register is available for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 30 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 6 | Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Feb 15 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 7 | Buchholz relay not connected to HT panel protection system. | Buchholz relay needs to be connected to HT panel protection system. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 30 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 8 | Transformer body earthing (equipment earthing) cable size is inadequate. | Equipment earthing cable size must be increased. The earth cable size shall be determined according to BNBC or Adiabatic method (if possible). Number of earth pits shall be determined by the size of connected earth cable. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 15 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 9 | Equipment earth cable (for generator) size is inadequate. | At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Feb 25 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 10 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 7 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 11 | Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 7 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 12 | No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Inadequate working space around (or in front of) board/ panels and access to the board/ panels is obstacles. | At least 1 meter (or equal to the width of board/ panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 14 | Indicator lamps installed on panel board are not operational. | All indicator lamps and metering devices installed on panel board shall be operational. Otherwise, it may provide false information. | Already we have installed indicator lamps at every electrical panel boards. | Dec 30 2023 | On 16/05/2024: Not Corrected. Factory will remove some panels and install fuses in some other panels. RPO Comments: On 28-Aug-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 14/12/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 15 | Distribution Board's top/bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 16 | Panel body is not connected to earth. | All metal installations which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 17 | Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 18 | Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 19 | MCCBs/MCBs are not installed/adjusted per load demand. | All the MCCBs/MCBs must be installed/ adjusted as per connected load current; if adjustment is not possible, replacement will be the only way. | In accordance with RSC's instructions, the MCCB has been adjusted to match the cable's ampere capacity. | Dec 30 2023 | On 16/05/2024: Not Corrected. This work will be done along with SLD work. On 14/12/2025: Not Corrected. No significant progress has been observed since the last follow-up. RPO Comments: On 22-Apr-2026: There is no pictorial evidence has been received. This items now is in progress. | 2 Months | In Progress
Initial Inspection |  | 20 | Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Feb 20 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 21 | Cable connected to busbar/ MCCB/MCB terminal without cable lug. | Each electrical circuit must be terminated at single busbar/MCB/ MCCB terminal using cable proper sized cable lug (where applicable). | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Feb 28 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 22 | Unterminated live wire is kept inside the electrical panel. | All the unterminated live power cables must be removed as soon as possible. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 30 2023 | On 16/05/2024: Corrected. | 1 Month | Corrected
Initial Inspection |  | 23 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Feb 28 2024 | On 16/05/2024: Not Corrected. Found in some old panels which will be removed. On 14/12/2025: Not Corrected. Significant progress has been observed, but this issue still remains in the cutting floor. RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 Months | Pending Verification
Initial Inspection |  | 24 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | This task already completed according to the instruction of RSC. | Jan 20 2024 | On 16/05/2024: Not Corrected. Found in one old panel which will also be removed. RPO Comments: On 03-Dec-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 14/12/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 25 | HT and LT cables are laid together inside same cable trench. | Conductors having non-shielded insulation and operating at different voltage levels shall not occupy the same enclosure, cable, or raceway. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 7 2024 | On 16/05/2024: Corrected. | 3 Months | Corrected
Initial Inspection |  | 26 | Power cables are buried in the concrete floor. | Power cable must be distributed through cable trench. Cable trench must be covered properly. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 3 Months | Corrected
Initial Inspection |  | 27 | 11kV power cable dropping from overhead line is not properly supported with pole and unprotected at the bottom of pole. | 11kV distribution power cable must be fixed with pole properly and protected at the bottom avoiding any kind of physical injury. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 28 | Wiring or extensions to connect equipment/ devices are laid on floors unprotected in flexible PVC. | The cable connection to machines/equipment may be run under the checkered plates (existing) and in trenches or rigid conduits/cable trays and supports to protect from external damages. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 29 | Cables are laid on floor inside cable trench haphazardly. | Cables inside cable trench have to be guided and routed properly. A cable tray shall be installed in the trench to ensure proper support and dressing for cables. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 30 | Combustible material attached with BBT. | Cable channels/ducts/ BBT must be kept neat and clean; these must be free from combustible material and water pot. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 31 | BBT end terminal left open. | Unused BBT end terminal must be sealed/covered by BBT end cap or by insulating material. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 27 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 32 | Cables are hanging without proper support and protection. | Cable tray/ladder must be used to support cables at anywhere to keep cable out of tension. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 27 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 33 | Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Manually operated each machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 17 2024 | On 16/05/2024: Corrected. | 1 Month | Corrected
Initial Inspection |  | 34 | Tap Off Box (TOB) left open to allow cable entry. | Cables entering tap off box must be firmly fixed with cable gland. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 27 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 35 | Uncovered/Perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 36 | Power socket is kept on floor unsafely. | Power socket shall be installed at minimum 200mm above the floor with a rigid support. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 37 | Inconvenient access to compressor room (fall hazard). | Provide proper stairs with handrail to eliminate fall/ tripping hazard. Factory may provide portable stair with adequate locking/ fixing capabilities for no movement during access (for operation & maintenance). | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Jan 31 2024 | On 16/05/2024: Corrected. | 2 Months | Corrected
Initial Inspection |  | 38 | Panel base plates are removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. | This issue is Corrected by RSC 1st Follow up inspection on 16th May-24. | Dec 30 2023 | On 16/05/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Lightning Protection System (LPS) is not maintained properly. Issues include missing air terminals, loose or disconnected conductors etc. | Regularly scheduled maintenance procedures must be conducted to ensure the continued effectiveness and reliability of the Lightning Protection System (LPS), preserving its ability to protect against lightning strikes. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 40 | New Finding: Electric safety training program is not initiated by qualified electrical personnel. | Electrical safety training and awareness programs for electrical personnel must be conducted regularly by qualified personnel and documented. This periodic task is crucial for continuously improving overall electrical safety for factory staff. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 41 | New Finding: No policies for PPE/ LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE (Personal Protective Equipment) and LOTO (Lock-Out-Tag-Out) policy using LOTO devices to ensure personnel safety during maintenance activities. All LOTO usage records must be maintained for compliance and safety monitoring. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 42 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Electrical maintenance program shall be developed to include regular inspections and testing of electrical systems, focusing on preventive and proactive measures. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 43 | New Finding: Multiple cables from different electrical consumers are terminated at circuit breaker terminals or busbars. | Each electrical circuit must be terminated at a single circuit breaker terminal or busbar to ensure distribution and protection within the electrical system. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 44 | New Finding: Multiple cables connected /terminated at the bus bar using single cable lug. | Each power cable must be terminated at any connection point using single cable lug. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 45 | New Finding: Loop connection has been used powering multiple circuits through circuit breakers. | No loop connections are allowed. Each cable must be terminated with a single cable lug at each terminal. Combo bus bars are permitted if the incoming cable size meets the rated capacity. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 46 | New Finding: Uncovered/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | This task has already been completed in accordance with the instructions of RSC, and the requirement has been fulfilled accordingly. | Jan 14 2026 | RPO Comments: On 22-Apr-2026: the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification

## Boiler
Date
07-May-2026 | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address
Date of Inspection
Finance Plan Agreed | Yes