## Structural
Date
04-Jul-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Century Apparels Ltd, Holding No. 01, Block-B. D.N. Road; West Masdair, Fatullah, Narayanganj., Narayanganj, Dhaka
Date of Inspection |  | 2014-09-18
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The AS-built drawing need to be revised to more accurately reflect the actual existing construction | The factory's Structural Engineer is to survey the actual conditions and revise the As-built drawings as early as possible | Corrected | Oct 22 2014 | On 27/07/15: A set of as-built drawing was shown during inspection, additional cantilever was shown on drawing. On 02/10/16: Found corrected from previous inspection. On 17/10/17: This issue was corrected from previous inspection. During inspection, as build drawing matches with actual condition. On 19/04/2018: Corrected previously. During inspection, As built drawing matches with actual condition. On 20th December 2018: Corrected previously. On 18-Apr-2022: Corrected from previous inspection. As-built drawing was produced as a part of EA which was accepted from ACCORD on 9th October 2017. On 17-Aug-2022: Corrected from previous follow up inspection. As built drawings were prepared as a part of EA. Factory management got EA acceptance from ACCORD on 09-October-2017. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. On 16-Sep-2025: Previously corrected. | within 6 months | Corrected
Initial Inspection |  | 2 | The existing extra cantilevered slabs and beams needs to be checked and reviewed against what was originally designed for. | The factory's Structural Engineer is to survey the actual conditions, revised the drawings and designs and carry a new structural analysis to confirm the structural safety of the slab system with the new site modifications. | Corrected | Oct 22 2014 | On 27/07/15: During inspection factory showed few pages attached to the as-built drawing which indicated the code parameters for wind and seismic loading but no analysis or calculation was shown. Factory is advised to do as per the recommendation of the initial inspection report and submit to Accord office as soon as possible. On 02/10/16: During follow up visit it was found that factory management have done as built drawing but no analysis has been done yet. Also no EA report has been submitted to ACCORD yet. On 17/10/17: Factory produced drawing as a part of EA and EA was accepted by ACCORD on 9th Oct 2017. On 19/04/2018: Factory prepared As-Built drawings along with EA report which was accepted by ACCORD on 9th October, 2017. On 20th December 2018: Corrected previously. Factory prepared As-Built drawings along with EA report which was accepted by ACCORD on 9th October, 2017. On 18-Apr-2022: Corrected from previous inspection. As-built drawing was produced as a part of EA which was accepted from ACCORD on 9th October 2017. On 17-Aug-2022: Corrected from previous follow up inspection. This issue had been covered in EA report. As built drawings were prepared as a part of EA. Factory management got EA acceptance from ACCORD on 09-October-2017. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. On 16-Sep-2025: Previously corrected. | within 6 months | Corrected
Initial Inspection |  | 3 | The roof needs to be protected with a water proofing layer if the construction does not proceed in the near future | Provide a proper waterproofing layer at the roof level if construction is not to proceed. | Corrected | Jan 30 2015 | On 27/07/15: No such layer has been provided, though a layer of cement finishing has been provided under the water tanks. On 02/10/16: During follow up visit no water proofing layer has been found. On 17/10/17 : During inspection, no water proofing layer and drainage system was found. Signage of water ponding was observed. Factory management is required to provide adequate drainage system and water proofing on roof slab to discharge the water. On 19/04/2018: Factory has provided a water proofing membrane on roof and improved the drainage system to avoid water ingress. On 20th December 2018: Corrected previously. No water ponding was observed during inspection. On 18-Apr-2022: Corrected from previous inspection. On 17-Aug-2022: Corrected from previous follow up inspection. Factory management had provided water proofing layer on roof top and during inspection, water ponding was not found on roof top. On 09-Dec-2024: Corrected previously. During inspection, waterproofing layer was found applied on the roof. On 14-May-2025: Corrected previously. Water proofing layer has been applied. On 16-Sep-2025: Previously corrected. | within 6 months | Corrected
Initial Inspection |  | 4 | The starter bars of the columns and shear walls on the 5th floor level need to be painted to prevent the corrosion of steel for future use. | Provide a proper painting layer to prevent steel corrosion | Corrected | Oct 22 2014 | On 27/07/15: Done. On 02/10/16: During follow up visit it was found that painting layer to prevent steel corrosion have been provided. Found corrected from previous inspection. On 17/10/17: This issue was corrected from previous inspection. During inspection, painting in starter rebar was observed to prevent corrosion. On 19/04/2018: Corrected previously. During inspection, starter rebar was found painted. On 20th December 2018: Corrected previously. On 18-Apr-2022: Corrected from previous inspection. During inspection all exposed rebar were found painted. On 17-Aug-2022: Corrected from previous follow up inspection. During inspection, exposed rebars were found painted. On 09-Dec-2024: Corrected previously. The factory has applied anti-corrosive coating on exposed rebar. On 14-May-2025: Corrected previously. Anti-corrosive coating has been applied on the exposed re-bar. On 16-Sep-2025: Previously corrected. | within 6 months | Corrected
Initial Inspection |  | 5 | A Structural Engineer is to review and check the building stability under wind and seismic loads. | The factory's Structural Engineer is to analyse and check the overall structural system under lateral wind and seismic loading to verify all compliance with BNBC codes. Based on the analysis results, consider whether any strengthening or modification work needs to be taken | Corrected | Oct 22 2014 | On 27/07/15: During inspection factory showed few pages attached to the as-built drawing which indicated the code parameters for wind and seismic loading but no analysis or calculation was shown. Factory is advised to do as per the recommendation of the initial inspection report and submit to Accord office as soon as possible. On 02/10/16: During follow up visit it was found that factory management have done as built drawing but no analysis has been done yet. Also no EA report has been submitted to ACCORD yet. On 17/10/17 : Factory completed Engineering Assessment (EA) and EA got acceptance on 9th Oct 2017. No remediation was recommended in EA report. On 19/04/2018: Factory prepared EA and submitted to ACCORD which was accepted on 9th October, 2017. As per EA recommendation, no retrofitting was required for the factory building. On 20th December 2018: Corrected previously. Factory prepared EA and submitted to ACCORD which was accepted on 9th October, 2017. As per EA recommendation, no retrofitting was required for the factory building. On 18-Apr-2022: Corrected from previous inspection. Factory got EA acceptance from ACCORD on 9th October 2017. As per accepted EA no remediation work is required. On 17-Aug-2022: Corrected from previous follow up inspection. Factory management got EA acceptance from ACCORD on 09-October-2017. As per accepted EA recommendation, no remediation work is required. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. On 16-Sep-2025: Previously corrected. | within 6 months | Corrected
Follow Up Inspection |  | 6 | New Findings -1: Columns susceptible to vehicle impact | Provide vehicle protection around the columns to avoid vehicle impact. | Corrected | May 31 2018 | On 19/04/2018: During inspection, the columns on loading -unloading areas on ground floor found prone to vehicle impact. Factory is required to provide vehicle protection around the columns to avoid vehicle impact. On 20th December 2018: Factory has provided vehicle impact protection on the columns of loading-unloading area. On 18-Apr-2022: Corrected from previous inspection. Factory provided protection for vehicle impact. On 17-Aug-2022: Corrected from previous follow up inspection. Factory management had provided vehicle impact protection around columns. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. Column guard was observed. On 16-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 7 | New Findings -2: Railing at stair on top floor found loose | Factory is required to replace the railing with a well engineered sections. | Corrected | May 31 2018 | On 19/04/2018: During inspection, railing at stair(from 5th floor to roof) found too loose to provide fall protection. Factory is required to improve the railing by proper engineered sections. On 20th December 2018: Factory has strengthened the railing at stair(from 5th floor to roof). On 18-Apr-2022: Corrected from previous inspection. Factory had strengthened the stair railing. On 17-Aug-2022: Corrected from previous follow up inspection. Factory management had strengthened the stair railing. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. On 16-Sep-2025: Previously corrected. | (within 6 – weeks) | Corrected
Follow Up Inspection |  | 8 | New finding-3: Apparently inadequate connection of steel members to brick wall for steel roof over both staircases | Check the connection adequacy for uplift forces for all connections and implement remedial works where required. | Corrected | May 30 2022 | On 18-Apr-2022: During inspection connection of steel members to brick wall were appeared to be inadequate for steel roof over both staircases. Factory engineer is required to check the connection adequacy for uplift forces for all connections and implement remedial works where required. On 17-Aug-2022: No action had been taken regarding this issue. Factory engineer is required to check the connection adequacy for uplift forces for all connections and submit it to RSC for review. On 09-Dec-2024: The factory demolished the steel shed above the staircase and constructed a new RC roof slab over the staircase. On 14-May-2025: Corrected previously. Roof shed was demolished. On 16-Sep-2025: Previously corrected. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 9 | New finding-4: New structure in the factory premises Pump Room - 500 sft Observation: -Lack of as-built drawing. | The factory is required to keep as-built drawing on-site for further verification. | The as built drwing ready for further verification | Jun 25 2025 | On 14-May-2025: During the inspection, single-storied basement structure RC Pump Room (500 sft) was observed in the factory premises. The as-built drawing was not available on-site. The factory is required to keep as-built drawing on-site for further verification. On 16-Sep-2025: The as-built drawing was not available on-site at the time of inspection. Progress Status: 0% RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification
Follow Up Inspection |  | 10 | New finding-5: Single storied ancillary structure in the factory premises adjacent to the Main Production Building Security Room - 121 sft Boiler Room - 160 sft Lack of as-built drawing. | The factory is required to prepare full set of as-built drawings and keep as-built drawing on-site for further verification. | We have contact our consultant. They are work on it. It will cmpleted within 31/12/2025 | Nov 9 2025 | On 16-Sep-2025: During the inspection, two single-storied ancillary structures were found in the factory premises. The as-built drawing was not available on-site. The factory is required to prepare full set of as-built drawings and keep the as-built drawing on-site for further verification. RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | (within 6 weeks) | Pending Verification

## Fire
Date
04-Jul-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Century Apparels Ltd, Holding No. 01, Block-B. D.N. Road; West Masdair, Fatullah, Narayanganj., Narayanganj, Dhaka
Date of Inspection |  | 2014-06-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boiler and generator room is not separated by fire-rated construction (openings, non-rated doors, penetrations) | Separate the boiler and generator room by a minimum 2-hr fire-rated construction. Seal and protected all openings to maintain the required fire separations. | Corrected | Jul 25 2015 | On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow ups. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 2 | The exit stairs are not separated from work areas and other spaces on each floor by fire rated construction. | Provide minimum 1.5 hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floor. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Corrected | Apr 30 2016 | On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow up. Door closer and coordinator does not working properly, shall be remediated immediately. On 12/08/2018: Corrected. On 06/01/2019: Corrected as per previous follow up. Note: Coordinators have been found missing at several locations. Doors have been found open by unapproved means. On 09/09/2019: Corrected. On 05/10/2021: Corrected. Fire rated doors shall be ensured functional all the time. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected as per previous FU. Fire rated doors & accessories shall be ensured functional all the time. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 3 | unsealed penetrations and openings are located in the fire-rated floor/ceiling assemblies. | Provide a minimum 2hr fire rated shaft to separate the utility risers from each floor level or seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation | Corrected | Apr 14 2016 | On 07/05/2017: It has been found same as the last follow up. On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow up. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located NW exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation | Corrected | Jul 25 2015 | On 07/05/2017: Corrected. On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow ups. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 5 | The storage on ground floor are not separated by fire rated construction | Provide dedicated storage rooms separated by minimum 1 hr fire rated construction (Fire door) | Corrected | Mar 14 2016 | For Previous Comments See Previous Report. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 6 | Areas used for combustible storage on the 1st floor are not separated by fire rated construction | Where separate storage rooms are not feasible provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.4m and maximum area of 23m2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m | Corrected | Apr 14 2016 | For Previous Comments See Previous Report On 21/01/2018: Corrected as on previous follow up only for 1st floor. On 12/08/2018: Issue has been cover on point no 40. On 06/01/2019: Refer to issue no 40. On 09/09/2019: Refer to issue no 40. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Refer to the issue no. # 40 On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Refer to the issue no. # 40. | 3 months | Corrected
Initial Inspection |  | 7 | Egress doors with locking features are provided at building exits, exit stairs and exit discharge. | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA-101 | Corrected | Oct 15 2014 | On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow ups. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Collapsible sliding doors are provided at building exits and exit stairs. | Replace all gates and sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 | Corrected | Oct 15 2014 | For Previous Comments See Previous Report On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 1 month | Corrected
Initial Inspection |  | 9 | NW exit stair door does not swing in the direction of egress travel. | Modify the egress door to swing in the direction of egress travel. | Corrected | Aug 31 2015 | On 07/05/2017: Corrected. On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow up. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 10 | SE exit stairs discharge inside the building. | Modify stair to discharge directly outside or provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage area) or provide sprinkler protection for discharge floor in accordance with NFPA 13. | Corrected | Aug 31 2015 | On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow ups. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected as per fu. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 6 months | Corrected
Initial Inspection |  | 11 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | We have submited pre T&cv documents on 16/09/2025 and RSC Accepted on 30/11/2025. Now We are awaiting for pre T&cv audit. | Jun 14 2016 | For Previous Comments See Previous Report On 05/03/2023: Pre-T&CVI found that FADS is not ready for full T&C. See the detail Pre-T&CVI report. On 09/05/2024: Factory has submitted the documents of Pre T&C VI for Fire Alarm & Detection system on dated 30 August 2023. During the inspection the panel was found active with remarkable fault ( General Trouble, NAC trouble, Supervisory alarm, devices bypass). Also the modification work was ongoing. However, after completing the modification work factory will informed to RSC for further processed. On 14-May-25: The factory has submitted the as-built design & other related documents (3rd time) to the RSC for Pre-T&CVI on 22-Jan-2025 (both ID-11059 & ID-12654 share single fire alarm panel) which is under review. However, during the inspection the fire alarm control panel was found active with some trouble. The factory is required to ensure that the FACP remains active and in normal operating condition at all times. On 16-Sep-25: Factory has submitted as-built design and drawing of Fire Alarm Detection System (4th time) on 19th August, 2025 which is currently under RSC review. FACP was found active but 18 numbers of troubles found during the visit. RPO Comments on 22 Feb 2026- As per the email dated 30 Nov 2025, the captioned factory is ready for Pre-T&C VI (FADS). On 08-June-2026: T&C has been conducted. The system is not approved, Again Testing and Commissioning Verification Inspection is Required. Refer to the full-T&C report for details. | Design within 4 month install within 9 month | In Progress
Initial Inspection |  | 12 | Inspection, testing, and maintenance of the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Jun 14 2016 | For Previous Comments See Previous Report On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. The factory shall maintain the fire alarm and detection system ITM as per NFPA-72, Table-14.3.1 On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 13 | Inspection, testing, and maintenance records for the fire detection system was not in accordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Jun 14 2016 | For Previous Comments See Previous Report On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. The factory shall maintain the fire alarm and detection system ITM as per NFPA-72, Table-14.3.1 On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 14 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the building, tied into the fire alarm system, in accordance with NFPA 72. | Corrected | Jun 14 2016 | For Previous Comments See Previous Report On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 6 months | Corrected
Initial Inspection |  | 15 | All exit signage not illuminated (burned out, broken, etc.) | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 1 month | Corrected
Initial Inspection |  | 16 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 17 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes at all floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Apr 14 2016 | For Previous Comments See Previous Report On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 18 | The corridor was not separated from work areas and other spaces on 1st floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the corridor from work areas and other building spaces on 1st floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 21/01/2018: Corrected as on previous follow ups. This building is now occupied by other factory (Afilion Tex at ground floor, Century Fashion & Fabric at 1st floor and Century Knit & Print at 2nd floor). On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 3 months | Corrected
Initial Inspection |  | 19 | The boiler and generator room is not separated by fire-rated construction (openings, non-rated doors, penetrations). | Separate the boiler and generator room by a minimum 2-hr fire-rated construction. Seal and protected all openings to maintain the required fire separations | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 3 months | Corrected
Initial Inspection |  | 20 | The storage room are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Refer to the issue no.# 43 On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 3 months | Corrected
Initial Inspection |  | 21 | The NW exit stairs are not separated from work areas and other spaces on each floor by fire rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | 3 months | Corrected
Initial Inspection |  | 22 | Unsealed penetrations and openings are located in NW exit stair enclosures. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 3 months | Corrected
Initial Inspection |  | 23 | Egress doors and gates with locking features are provided at building exits, exit stairs, along egress routes and exit discharge. | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | Immediate | Corrected
Initial Inspection |  | 24 | Storage was located in the NW exit stair. | Remove all storage from exit stairs and egress paths. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | Immediate | Corrected
Initial Inspection |  | 25 | Collapsible gates and sliding doors are provided at building exits, exit stairs, along egress routes and exit discharge. | Replace all gates and sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 1 month | Corrected
Initial Inspection |  | 26 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected as per previous. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | Design within 4 months install within 9 months | Corrected
Initial Inspection |  | 27 | Activation of the fire alarm system by a manual fire alarm station provides automatic occupant notification only on the floor of alarm and not throughout the building. | Configure the fire alarm system to initiate automatic occupant notification on all floor levels to facilitate whole building evacuation upon any manual fire alarm station activation. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 1 month | Corrected
Initial Inspection |  | 28 | Inspection, testing, and maintenance of the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 3 months | Corrected
Initial Inspection |  | 29 | Inspection, testing, and maintenance records for the fire detection system was not in accordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 3 months | Corrected
Initial Inspection |  | 30 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the building, tied into the fire alarm system, in accordance with NFPA 72. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 6 months | Corrected
Initial Inspection |  | 31 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected | Jul 25 2015 | For Previous Comments See Previous Report On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Not Applicable) | 3 months | Corrected
Follow Up Inspection |  | 32 | New Finding: The building has an occupied floor greater than 10 meter (33 feet) and its not provided with standpipe system as per NFPA 14. | Provide standpipe and hose system as per NFPA 14. | We have submited document with pictorial eveidance on 27/01/2026 for RSC Review. | Jul 14 2016 | For Previous Comments See Previous Report On 09/05/2024: Factory has submitted the documents of Pre T&C VI for Fire protection system on dated 30 August 2023. Factory has completed the modification work. During the inspection the pump was found active and functional. On 16-Jul-2024: Pre-T&CVI found that SUPS is not ready for full T&CVI. Pre-T&C closure verification inspection is required. See details on Pre-T&C report. On 14-May-25: The factory has submitted the as-built design & relevant documents to the RSC on 17-Mar-2025 for Pre-T&CVI closure verification inspection after completing all installation and modification work as per the last Pre-T&CVI recommendation. However, during the inspection fire pumps were found active. On 22-Jul-2025: An additional Pre-T&C closure verification is required on-site for the Fire Protection System (SUPS) following the completion of the recommended modifications to the system, drawings, and documentation, as outlined in the report. On 16-Sep-25: Installation and modification work is on-going as per the last Pre-T&CVI recommendation. Reportedly, the factory will submit as-built design and drawing as soon as modification work is completed. However, during the inspection fire pump set was found in active condition. RPO Comments on 03 Mar 2026- The design documents have be reviewed and as per email dated 03 Mar 2026 Century Apparels Ltd (ID-11059) is now considered ready for the Full T&CVI of SUPS. On 08-June-2026: T&C has been conducted. The system is not approved, Again Testing and Commissioning Verification Inspection is Required. Refer to the full-T&C report for details. | Design within 2 months install within 4 months | In Progress
Follow Up Inspection |  | 33 | New Finding (2nd Follow-up): Manual on-off switch is provided for emergency lighting units in all stair landing. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Corrected | Mar 31 2016 | For Previous Comments See Previous Report On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 34 | New Finding (4th follow up): Parapets or guards are not provide in occupiable roof with standard height. | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | Corrected | Oct 31 2016 | For Previous Comments See Previous Report On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 01 months | Corrected
Follow Up Inspection |  | 35 | New Finding (4th follow up): Handrails are not provided on both sides of the exit stairs. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | Corrected | Nov 30 2016 | For Previous Comments See Previous Report On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 01 months | Corrected
Follow Up Inspection |  | 36 | New Finding (4th follow up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on-site, in accordance with NFPA 10. | Corrected | Oct 31 2016 | For Previous Comments See Previous Report On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 01 months | Corrected
Follow Up Inspection |  | 37 | New Finding (4th follow up): Width of aisles is less than 0.9m (36-in.)/ aisles marking is not provided on 3rd floor dining and 4th floor. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.). | Corrected | Oct 10 2016 | For Previous Comments See Previous Report On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 38 | New Finding (4th follow up): Building did not have stair designation signs and occupant load signs at required locations. | Provide stair designation signs and occupant load signs at required locations. | We have already posted Occupant load plan sign. | Oct 10 2016 | On 08/10/2017: Corrected. Need some modifications. On 21/01/2018: Corrected as on previous follow ups. Shall be updated daily. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Issue is Re-opened. Occupant load sign are not provided in proper way and stair designation sign is also missing on roof level. RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | Immediate | Pending Verification
Follow Up Inspection |  | 39 | New Finding (4th follow up): The boiler room is not separated by fire-rated construction (openings, non-rated doors, penetrations) | Separate the boiler room by a minimum 2-hr fire-rated construction. Seal and protected all openings to maintain the required fire separations. | Corrected | Nov 30 2016 | On 07/05/2017: Factory has installed fire door and door has been found manually open. On 08/10/2017: Corrected. On 21/01/2018: Corrected as on previous follow up. On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 01 months | Corrected
Follow Up Inspection |  | 40 | New Finding: Areas used for in-process storage of combustible materials are open to the surrounding occupancy. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Now we are not used for in-process storage of combustible materials are open to the surrounding occupancy. | Mar 30 2018 | Factory asked for time extension till 30/03/2018. Timeline extended from 20/02/2018 to 30/03/2018 On 12/08/2018: Not corrected. On 06/01/2019: Not corrected. On 09/09/2019: Corrected. On 05/10/2021: Improper storage was noted on 2 floors during inspection. On 18/04/2022: Corrected. On 17/08/2022: Re-Open, In process storage observed on some location of the production floor. On 05/03/2023: Corrected. Maintaining as per recommendation. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Issue is Re-opened. In-process storages has been exceeded the allowable limit at 3rd and 4th floor of Main Building. RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 01 month | Pending Verification
Follow Up Inspection |  | 41 | New Finding: Storage was located in the N-W exit stair. | Remove all storage from exit stairs, aisles and egress paths. | Corrected | Jan 28 2018 | On 12/08/2018: Corrected. On 06/01/2019: Corrected. On 09/09/2019: Corrected. On 05/10/2021: Corrected. On 18/04/2022: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 1 week | Corrected
Follow Up Inspection |  | 42 | New Finding 13th FUI: The storage room are not separated by fire-rated construction. Location: 3rd floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | We have changed store room. Now the storage room are separeted. | Sep 17 2022 | On 17/08/2022: New Finding On 05/03/2023: Corrected. Maintaining. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Issue is Re-opened. Open storages (covered more than 20% area) has been observed at production area on 1st floor without any fire protection barrier. (note- For in-process storage less 10% of floor area need to be maintained.) RPO Comments on 22 Feb 2026- The factory management reported the remediation completion. But pictorial evidence is not credible enough to mark the CAP item as “Pending Verification”. | within 1 month | In Progress
Follow Up Inspection |  | 43 | New Finding 13th FUI: There were some aisle blocked by cartoon and cloths. Combustible Diesel store under the stair. | Remove the all storage from mentioned location immediately. | Corrected | Aug 20 2022 | On 17/08/2022: New Finding On 05/03/2023: Corrected. On 09/05/2024: Corrected. On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 44 | New Finding (15th FU): Factory Building is interim and new lift installation work is ongoing which is open directly in exit stair without fire separation. | An exit stairway shall not be built around a lift shaft unless both of them are located in a smoke proof enclosure and made of a material with fire resistance rating required for the type of construction of smoke proof enclosure. (As per 6.14.3 of RSC Technical Guidelines (Standard) V1.0) Elevator shaft shall be 2-hr fire rated opening protection from factory floor. Recommended to follow "SUPPLEMENTARY PAPER ON REMEDIATION GUIDANCE ELEVATOR OR LIFT SHAFT OPENING IN EXIT ENCLOSURES" for remediation. | We have submited document for RSC Review. | Aug 19 2024 | New Finding: On 14-May-25: In progress. The factory submitted the fire-rated curtain documents (second submission) to the RSC for review on 13 May 2025. The documents are currently under review. On 16-Sep-25: Factory has submitted design philosophy, drawing and documents (3rd submission) of fire curtain to RSC on 15th July, 2025 which is under review. RPO Comments on 22 Feb 2026- The captioned factory submitted the documents on 10 Dec 2025 which are under RSC review. | Within 3 months | In Progress
Follow Up Inspection |  | 45 | New Finding (15th FU): Sliding door are found at 4th floor and 1st floor packing and sampling section. | Replace all collapsible gates/ sliding doors/ rolling shutter doors along the means of egress with side hinged, swinging egress doors. If locks are required for security reasons, utilize specialized door locking features complying with NFPA101. | We have remove sliding door. | Jun 19 2024 | New Finding: On 14-May-25: Corrected. Sliding doors has been removed from the mentioned areas. On 16-Sep-25: Issue is Re-opened. Sliding doors need to be removed from main building office, sample section and childcare area. RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 46 | New Finding (15th FU): Penetration are found due to pvc pipe at bonded warehouse and production toilet area. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. If fire stopping materials with proprietary design are used for seal, then it shall be classified for the purpose it is used for. Also the installation shall be as per the proprietary design it has been tested with. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | We have resubmited the document for RSC review on 25/11/2025. | Jul 19 2024 | New Finding: On 14-May-25: In progress. The factory submitted the fire-rated collar documents (second submission) to the RSC for review on 13 May 2025. The documents are currently under review. Moreover, all unsealed penetration is required to be seal by fire rated materials. On 16-Sep-25: Factory has submitted design philosophy, drawing and documents of fire rated collar to RSC on 15th July, 2025 (2nd time) which is under review. Unsealed plumbing penetration was still found on 1st floor office area and ground floor ware house. RPO Comments on 22 Feb 2026- the captioned factory submitted the documents on 25 Nov 2025 which are under RSC review. | Within 2 months | In Progress
Follow Up Inspection |  | 47 | New Finding(16th FUI): Fire doors has been installed in the openings of required fire rated assemblies such as exit stairs, storage rooms separations etc. However, fire door were found with following issues- 1. Some fire door coordinators were missing on the 1st & 4th floor of stair-1 & 2. 2. Doors were not proper positive latching. 3. Door holders were found non functional during fire alarm condition. 4. Fire doors and frames were found with holes that could impact the fire protection rating. Location: Five storied main production building. | Factory shall have to ensure that the maintenance work shall be done for the fire door hardware and accessories on a regular basis as per NFPA 80 and manufacturer's published guideline. Repair/ replace the unworkable accessories with listed one. Ensure that the fire doors are self closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. Any modification of fire doors beyond the job site preparation shall be approved by the door manufacturer. | We have maintence all fire door. | Aug 14 2025 | On 14-May-2025: New finding On 16-Sep-25: No progress has been observed. RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 48 | Unsealed electrical line penetrations are found in different floor levels. Location: Main Production Building. | Seal all penetrations and openings in floor/ceiling assemblies by a listed through-penetration fire stop system tested in accordance with ASTM E814 or approved alternative standard to maintain minimum 3-hr. fire resistance rating. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating in accordance with section 4.7 of RSC Technical Guideline (Standard) | We have sealed all electrical penetration. | Dec 16 2025 | On 16-Sep-25: New Finding. RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 49 | Storage area discharge is staircase without vestibule at main building. Location(s): Ground floor (Both Stairs). | Openings from exit enclosure to Storage areas/ basements/ transformer rooms/ generator rooms/ boiler rooms and similar normally unoccupied spaces shall be provided with a vestibule with fire rated construction and openings in accordance with section 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a min 1-hr fire rated door on the exit stair side and a 1.5 hr. fire rated door on the Store, generator, sub-station room side . Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure as per RSC Technical Guidelines (Standard)¹ V1.0. section 6.14.3. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. | We have remove all storge on audit day. | Dec 16 2025 | On 16-Sep-25: New Finding. RPO Comments on 14 Dec 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification

## Electrical
Date
04-Jul-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Century Apparels Ltd, Holding No. 01, Block-B. D.N. Road; West Masdair, Fatullah, Narayanganj., Narayanganj, Dhaka
Date of Inspection |  | 2014-07-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Change over Switch used in place of isolator and not mounted on the wall/foundation. | Use proper rated switch gears as isolator. Mount the panel board on wall/foundation as recommended. | Corrected | Jul 20 2015 | On 14/03/16: Already verified in Accord first follow up inspection. | 1 Month | Corrected
Initial Inspection |  | 2 | Cables terminating to generator output terminal box are laid on floor. | Cables terminating at generator output terminal box must be supported on riser and protected. Existing cables laid on floor may be supported in cable trench or on trays. | Corrected | Apr 30 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is till 30/04/16. On 12/06/16: Not corrected. On 02/10/16: Not Corrected. On 07/05/2017: Not corrected. On 08/10/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 3 | Phase barrier/ separators between different phases are not installed. Typical). | Phase barriers between different phases must be installed to avoid arc flash over. | Corrected | Jul 20 2015 | On 14/03/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 4 | Incoming and outgoing cables are not supported properly. | Cables terminating at control panel must be supported on ladders and cables below switch board laid towards to floor must be protected. | Corrected | Apr 30 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is 30/04/16. On 12/06/16: Not corrected. Factory is behind schedule. Factory asked for time extension till 30.08.2016.Time extension request is not accepted. On 02/10/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Panel doors not connected with earth bond (Typical). | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at Zero potential all the time. | Corrected | Jul 20 2015 | On 14/03/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 6 | Cable glands not installed for cables. | Provide cable glands according to the respective cable size for incoming & outgoing cables. So that the cables are not stressed on the sharp edge of the hole of panels. | Corrected | Apr 30 2016 | On 14/03/2016: This issue is not corrected yet. New committed timeline is 30/04/16. On 12/06/2016: Not Corrected. On 02/10/2016: Not Corrected. On 07/05/2017: Not Corrected. On 08/10/2017: Not Corrected. On 21/01/2018: Corrected. | 1 Month | Corrected
Initial Inspection |  | 7 | Porcelain fuse unit mounted on wooden board. Copper wires uses in place of fuse wire. | Electrical devices must be protected and installed in non-combustible protective enclosure. Porcelain fuse unit should be replaced with MCCB. Proper rated fuse wires must be used for protection for re-wire able fuses. | Corrected | Jul 20 2015 | On 14/03/16: Already verified in Accord first follow up inspection. | 1 Month | Corrected
Initial Inspection |  | 8 | Haphazard cables inside the panel. | Redesign and rewiring required. Use cable duct wiring channels. | Corrected | May 11 2014 | On 14/03/16: Already verified in Accord first follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 9 | Service cable laid directly on concrete floor. | Service cable on concrete floor must be supported in cable trays or laid in cable trenches. The cable must be protected against physical damage. | Corrected | May 11 2014 | On 14/03/16: Already verified in Accord first follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 10 | Cables terminating at panel not supported. | Install the cable tray/ ladder/ duct up to the cable entry of the panel in order to support the cables. Ensure the cables are tightly latched with the ladder and provide covers made of non-combustible material. | Corrected | May 11 2014 | On 14/03/16: Already verified in Accord first follow up inspection. | 3 Months | Corrected
Initial Inspection |  | 11 | Excessive lint deposit at cable duct. | Disconnect the power source of the cable laid into channel and clean dust and debris of all interior components. Provide cover made of non-combustible material on the channel for preventing ingress of dust and debris in future. | Corrected | Sep 15 2015 | On 14/03/16: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 12 | New Finding: Battery terminals are not covered. | Use insulated rubber cap to cover all the battery terminals. | Corrected | Apr 30 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is 30/04/16. On 12/06/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 13 | New Finding: Earth Continuity Conductor (ECC) in the distribution box is improper size. Nevertheless there is no Earth bar. | Increase ECC size for whole factory according to BNBC 2006 Part 8 Chapter 2 section 2.8 (Usually ECC should be equal to the half of the respective phase cable). | Corrected | Apr 30 2016 | On 14/03/16: Proper size ECC & earth bar didn’t found. So, this issue is not corrected yet. New committed timeline is 30/04/16. On 12/06/2016: Not Corrected. On 02/10/2016: Not Corrected. On 07/05/2017: Not Corrected. On 08/10/2017: Not Corrected. On 21/01/2018: Not Corrected. On 12/08/2018: Not Corrected. On 06/01/2019: Corrected. Factory asked for time extension till 30/09/2018. Not accepted by Accord. | 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Multiple cables connected in the bus bar through single lugs. | Each cable must be connected in the bus bar through single lugs. | Corrected | Apr 30 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is 30/04/16. On 12/06/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Loop connection has used powering multiple MCBs. | Eliminate loop cables; use single cable for each MCBs. You may use bus bar to avoid multiple termination. | Corrected | Apr 30 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is 30/04/16. On 12/06/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 16 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Corrected | Apr 30 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is 30/04/16. On 12/06/2016: Not Corrected. On 02/10/2016: Not Corrected. On 07/05/2017: Not Corrected. On 08/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 17 | New Finding: Insulation resistance test of electrical equipment is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Corrected | May 31 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is 31/05/16. On 12/06/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Thermography scanning report is unavailable. | Keep a thermography scanning record of your electrical system at lease twice a year. | Corrected | Sep 30 2015 | On 14/03/16: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Corrected | May 31 2016 | On 14/03/16: Single line diagram is not complete for the factory. This issue is not corrected yet. New committed timeline is 31/05/16. On 12/06/16: Not Corrected. Factory has submit the SLD to ACCORD to review. On 02/10/16: Not Corrected. On 07/05/2017: Not corrected. On 08/10/2017: Not Corrected. On 21/01/2018: Not Corrected. Factory has reviewed drawing but still not amended properly. On 12/08/2018: Not Corrected. Factory asked for time extension till 30/09/2018. Not accepted by Accord. On 06/01/2019: Not Corrected. On 09/09/2019: Not Corrected. Factory asked for time extension till 20-Sep-2020. Not accepted. On 24/02/2021: Not Corrected. SLD is under review of the RSC.On 24/04/2022: Not Corrected. Some progress has been observed. SLD is under review of RSC. On 17/08/2022: Not Corrected. Some progress has been observed. SLD is accepted from RSC. But SLD is not as-built (Cable mismatch, load mismatch, circuit identification etc.) On 05/03/2023: Not Corrected. SLD is not as-built. No progress has been observed. On 24/01/2024: Not Corrected. Significant progress has been observed. Individual protection missing, cable identification missing, protection missing from transformer to manual COS, transformer & generator ecc cable mismatch, earthing layout shall be updated. On 09/05/2024: Not Corrected. The factory has implemented SLD on the 3rd and 4th floor. Mismatch (Cable, Circuit and load info, Comb busbar, circuit breaker, earthing layout, individual protection) has been observed with accepted SLD. Almost 70% progress has been observed. On 29/10/2024: Not Corrected. No progress has been observed from last follow-up inspection. Mismatches (cable and load identification, individual protection, ECC of panel board, mccbs adjustment) have been observed. On 14/05/2025: Not Corrected. Significant progress has been observed, with approximately 80% of the work completed. However, a few areas still require modification, such as oversized individual protection, missing or mismatched load identification in some areas, load reference mismatches, discrepancies in fault clearing time, and the omission of a few consumer boxes in the SLD. RPO Comments on 14 Aug 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. On 16/09/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Lightning Protection System (LPS) has not installed yet. | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | Corrected | May 31 2016 | On 14/03/16: This issue is not corrected yet. New committed timeline is 31/05/16. On 12/06/16: Not corrected. Factory is behind schedule. On 02/10/16: Not Corrected. Factory did not install LPS yet. On 07/05/2017: Not corrected. On 08/10/2017: Not Corrected. On 21/01/2018: Not Corrected. exposed metal parts aren't bonded properly. On 12/08/2018: Not Corrected. On 06/01/2019: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Transformer Breather oil cup is empty. | Fill the transformer breather oil cup by transformer oil. | Corrected | Apr 30 2016 | On 12/06/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 22 | New Finding: Oil leakage has been observed from transformer. Also Lint and dust deposited on transformer top. | Stop oil leakage from transformer and keep clean top of transformer. | Corrected | Apr 30 2016 | On 12/06/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Hot spots at terminations inside panel. | Find the cause of excessive heat-rise which may be the overloading, loose connection, unbalanced load and others and take action immediately. | Corrected | Jul 15 2016 | On 12/06/16: Corrected. No hot spot found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Periodicity of Thermography survey is not continued. | Thermography survey must be done and recorded at least twice in a year. | Corrected | Nov 8 2017 | Factory asked for time extension till 30/07/2017. Not Accepted. On 08/10/2017: Not Corrected. New committed time line is given till 08/11/2017 to close this issue. On 21/01/2018: Corrected. Thermography survey date: 31/08/2017. | 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: Flexible PVC pipe is used to cover power and signal cable for boiler. | Power and signal cable for boilers shall be distributed using proper type insulator to avoid damage of cables. | Corrected | Jul 30 2017 | Factory asked for time extension till 30/07/2017. Not Accepted. On 08/10/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Transformer top and around it shall be kept neat and clean. | Lint and dust deposited on and around the transformer. | Corrected | Nov 8 2017 | Factory asked for time extension till 30/07/2017. Not Accepted. On 08/10/2017: Not Corrected. New committed time line is given till 08/11/2017 to close this issue. On 21/01/2018: Not Corrected. On 12/08/2018: Not Corrected. On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Generator body earthing (equipment earthing) cable is inadequate. | Equipment earthing cable size must be increased. The earth cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. | Corrected | Nov 8 2017 | Factory asked for time extension till 30/11/2017. Not Accepted. On 21/01/2018: Not Corrected. On 12/08/2018: Not Corrected. On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Electric safety training program has not initiated/ conducted yet. | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory has to continue to improve overall safety situation for the staffs. | Corrected | Nov 8 2017 | On 21/01/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/ MCCB terminals. | Corrected | Feb 28 2018 | On 12/08/2018: Not Corrected. On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Cable duct/ channels are filled with fluffs (Lint/ dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | Feb 14 2018 | On 12/08/2018: Not Corrected. On 06/01/2019: Not Corrected. On 09/09/2019: Corrected. | 2 Weeks | Corrected
Follow Up Inspection |  | 31 | New Finding: Insulation Resistance Test is generated without conducting any physical survey. Latest report is a copy of previous report except the changes of date and page number. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Corrected | Mar 30 2018 | Factory asked for time extension till 30/03/2018. Timeline extended from 29/02/2018 to 30/03/3018. On 12/08/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Indicator lights are mounted without disconnecting device. | Indicator lights should be connected by control device such as rated fuse or MCB. | Corrected | Apr 28 2018 | Factory asked for time extension till 30/05/2018. Timeline extended from 28/03/2018 to 18/04/3018. On 12/08/2018: Not Corrected. On 06/01/2019: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | Corrected | Apr 28 2018 | Factory asked for time extension till 30/05/2018. Timeline extended from 28/03/2018 to 18/04/3018. On 12/08/2018: Not Corrected. Factory asked for time extension till 30/09/2018. Not accepted by Accord. On 06/01/2019: Not Corrected. On 09/09/2019: Not Corrected. On 24/02/2021: Not Corrected. Circuit breaker is needed to be adjusted per load demand. On 24/04/2022: Not Corrected. Some progress has been observed. On 17/08/2022: Not Corrected. Some progress has been observed. On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Transformer Oil Test (dielectric strength test) report is available but not accurate. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Corrected | Sep 13 2018 | On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Generator exhaust pipe is uninsulated. | Generator Exhaust pipe need to be covered by proper and adequate insulator. | Corrected | Sep 13 2018 | On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Burning sign is seen at the terminal. | Need to check the connected load, Check the thermal issue. But need to replace the burnt cable and lugs immediately. | Corrected | Sep 13 2018 | On 06/01/2019: Not Corrected. On 09/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Sep 13 2018 | On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/ DB/SDB/ other manual operated machineries) must be ensured. | Corrected | Sep 13 2018 | On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Transformer Breather oil cup is empty. | Transformer breather oil cup must be filled not more than 70% of its capacity. | Corrected | Sep 13 2018 | On 06/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Lights in the store room / storage areas are uncovered/ unprotected. | Lights in the store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. And a secure cabling shall be ensured. | Corrected | Sep 13 2018 | On 06/01/2019: Not Corrected. On 09/09/2019: Not Corrected. On 24/02/2021: Not Corrected. Unprotected lights were found in the warehouse and above stack of stored combustible goods. On 24/04/2022: Not Corrected. Some progress has been observed. PVC pipe used for wiring in storage area. Store room electrical connection shall be done through secure path e.g. GI steel pipe. On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected | Sep 13 2018 | On 06/01/2019: Not Corrected. On 09/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Corrected | May 15 2021 | On 24/04/2022: Not Corrected. Some progress has been observed. On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Not Corrected. The factory is working on it. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Corrected | Apr 15 2021 | On 24/04/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Oil leakage from transformer has been observed. | Oil leakage from transformer must be stopped and top of transformer must also be kept clean. | Corrected | Apr 15 2021 | On 24/04/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Panel/Distribution boxes are inaccessible. | Each electrical distribution board/panel must be easily accessible and no obstacles shall be made to access it. | Corrected | Apr 15 2021 | On 24/04/2022: Not Corrected. No progress observed. On 17/08/2022: Not Corrected. Some progress has been observed. Observed at few points. On 05/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Apr 15 2021 | On 24/04/2022: Not Corrected. No progress observed. Exposed steam line tied with combustible material. On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Cable duct/ channels are filled with fluffs (Lint/dust). | Cable channels/ ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | Apr 15 2021 | On 24/04/2022: Not Corrected. No progress observed. On 17/08/2022: Not Corrected. Some progress has been observed. On 05/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables must be removed as soon as possible. | Corrected | Apr 15 2021 | On 24/04/2022: Corrected. No unterminated live wire observed. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected | Apr 15 2021 | On 24/04/2022: Not Corrected. Some progress has been observed. On 17/08/2022: Not Corrected. Some progress has been observed. Still found at few places. On 05/03/2023: Not Corrected. Progress has been observed. On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Lightning Protection System (LPS) is not maintained properly. (loose connection/joints are rusted.) | Periodic maintenance shall be done to maintain LPS. Rusted/ damaged conductors & Air terminal shall be cleaned & replaced where necessary. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Not Corrected. No Progress has been observed. Disconnected conductor found, Joints are rusted, LPS drawing needs to be modified. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 51 | New Finding: No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/ DB/SDB/other manual operated machineries) must be ensured. | Corrected | Jul 8 2022 | On 17/08/2022: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 52 | New Finding: Distribution Board's top/bottom is left open (typical issue). | Each electrical distribution board/panel shall be properly sealed to avoid ingression of fluffs; but an adequate ventilation system shall also be ensured. Gland shall be used, where required. | Corrected | Jun 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Not Corrected. Progress has been observed. But few panels are not sealed properly. On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Multiple cables (came from different electrical consumers) terminated at same plug. | Each electrical circuit must be terminated at single terminals. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. Some progress observed. On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 54 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Not Corrected. Significant progress has been observed. Still found in a few places. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 55 | New Finding: Cable tray is overloaded with excessive cables; eventually top cover has no effectiveness. | Proper sized cable tray must be installed; a perforated one is better and 20-25% space in cable tray/duct shall be kept free. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: Surrounding area of panel is full of combustible material. | In front of each distribution board should have at least 1.07 m clearance. For stacking combustible materials this clearance shall not be less than 10 feet. | Corrected | Jun 8 2022 | On 17/08/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Hot spots have been observed at some points. (above 30ºC of ambient). | Hot spots must be eliminated from entire electrical system. | Corrected | Jun 8 2022 | On 17/08/2022: Corrected. No hotspot was observed during the inspection. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Wiring or extensions to connect equipment/ devices are laid on floors unprotected. | The cable connection to machines/equipment may be run under the checkered plates (existing) and in trenches or rigid conduits/ cable trays and supports to protect from external damages. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 59 | New Finding: Electric boiler has no earthing connection. | Each electrical installation must have proper earth connection. | Corrected | Nov 8 2022 | On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 60 | New Finding: Improper terminations are available at panel boards. | Cables needs to be terminated in busbar with proper sized cable lugs, washer, nut-bolts with direct contact to the buses. No busbar tubes shall be in between the contacts. | Corrected | Nov 8 2022 | On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 61 | New Finding: Panel door lock broken. | Provide proper type lock on panel door and keep the panel door close. | Corrected | Nov 8 2022 | On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 62 | New Finding: Panel room has inadequate illumination. | Adequate illumination must be ensured in the sub station room thus any maintenance can be done comfortably (150 lux should be maintained). | Corrected | Nov 8 2022 | On 05/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Corrected | Nov 8 2022 | On 05/03/2023: Not Corrected. No progress has been observed. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 64 | New Finding: Non rated and non-certified comb bar used for powering multiple MCB. | For connecting multiple MCB use rated and listed comb bar. | Corrected | Nov 8 2022 | On 05/03/2023: Not Corrected. No Progress observed. On 24/01/2024: Corrected. Removed comb busbar. | 2 Months | Corrected
Follow Up Inspection |  | 65 | New Finding: Outdoor Cable are not covered to protect from weather effect. | Outdoor cable tray/ ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Corrected | Apr 15 2023 | On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Thermographic survey is not performed for all panel board. | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | Corrected | Feb 29 2024 | On 09/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Hot spots have been observed at some points. (above 40ºC of ambient). | Hot spots must be eliminated from entire electrical system. | Corrected | Feb 7 2024 | On 09/05/2024: Not Corrected. Hot spot has been observed at several panels. On 29/10/2024: Not Corrected. Significant progress has been observed but still hotspots found in DB-2, DB-4 and few other panels. RPO Comments On 31 Dec 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 14/05/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels and ducts must be kept clean and sealed to prevent any ingress of dust and debris. | Corrected | Dec 8 2024 | RPO Comments On 31 Dec 2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 14/05/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Uncovered/Perforated type cable tray used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected | Aug 14 2025 | On 16/09/2025: Corrected. | 3 Months | Corrected

## Boiler
Date
04-Jul-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Century Apparels Ltd, Holding No. 01, Block-B. D.N. Road; West Masdair, Fatullah, Narayanganj., Narayanganj, Dhaka
Date of Inspection |  | 2022-05-12
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 11986 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. |  | Dec 15 2024 | Comments on 05-Nov-24: The remediation work shall be done following provided guideline and applicable standard within the committed timeline. RPO Comments on 14 Jan 2025- The factory management reported the remediation completion. This item will be verified in the next inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. All required documents were not available during the inspection. On 2-Feb-26: Not Corrected. Documentation including Piping and Instrumentation diagram, commissioning documents, flue gas analysis report, water treatment design and calculation, and water treatment report were not available to verify the present condition of the boiler. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 2 | BB 11986 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. |  | Dec 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-25: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Not Corrected. Emergency stop switch at panel found defective. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 3 | BB 11986 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Corrected | Dec 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Corrected. LLWL marked properly. | 2 MONTHS | Corrected
Initial Inspection | External visual inspection | 4 | BB 11986 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | Corrected | Nov 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. Boiler was not Operational So inspection was not Completed. On 2-Feb-26: Corrected. Safety valves outlet line installed. | 1 MONTH | Corrected
Initial Inspection | External visual inspection | 5 | BB 11986 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. |  | Dec 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Not Corrected. Still Direct groundwater was used as feed water for the boiler. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 6 | BB 11986 | The steam pressure gauge range is insufficient. | The boiler pressure gauge range should be at least twice the boiler's maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. |  | Nov 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Not Corrected. Steam pressure gauge range insufficient | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 7 | BB 11986 | Inconsistency was observed between the construction drawing and the actual construction of the boiler | Construction drawing should be consistent with the actual construction of the boiler |  | Dec 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Not Corrected. Inconsistency still persists. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 8 | BB 11986 | Leakage was observed from the water level gauge glass. | The water level gauge glass must be tightened or replaced if necessary. | Corrected | Nov 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Corrected. No leakage observed. | 1 MONTH | Corrected
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 9 | BB 11986 | Thin salt & scale formation was observed on the water side throughout the water chamber | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Corrected | Nov 15 2024 | On 07-Jan-26: Corrected De-scaling has been done and waterside found in cleaned condition during inspection | 1 MONTH | Corrected
Initial Inspection | Functional test inspection | 10 | BB 11986 | There was no Low Low Water (LLWL) level trip with an interlock for the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. |  | Oct 22 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Not Corrected. There was no interlock for the Low Low Water (LLWL) level trip of the boiler | 1 WEEK | In Progress
Initial Inspection | Functional test inspection | 11 | BB 11986 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. |  | Nov 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Not Corrected. The Steam Pressure Limiter was missing | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 12 | BB 11986 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. |  | Nov 15 2024 | Comments on 05-Nov-24: Will be verified during the next follow up inspection. On 14-Jan-26: Not Corrected. The boiler was not operational. Therefore, the inspection was not completed. On 2-Feb-26: Not Corrected. The Air Pressure Limiter was missing | 1 MONTH | In Progress
Followup Inspection | External visual inspection | 13 | BB 11986 | New Finding: Boiler condensate return pipelines were found with improper insulation. | Proper insulation to exposed parts of the boiler condensate and steam distribution pipelines should be provided. |  | Feb 7 2026 |  | 1 MONTH | In Progress
Followup Inspection | External visual inspection | 14 | BB 11986 | New Finding: Rotating equipment was found without mechanical guard in the boiler room. | Mechanical guard must be provided to rotating shaft and driving system. |  | Jan 28 2026 |  | 2 WEEKS | In Progress
Followup Inspection | External visual inspection | 15 | BB 11986 | New Finding: Inconsistent values were observed between steam pressure gauges. | Appropriate pressure gauge(s) shall be provided according to Bangladesh Boiler Regulation (BBR)/manufacturing standard/any standard recognized by the CIoB with consistent functionality. |  | Apr 2 2026 |  | 2 MONTHS | In Progress
Followup Inspection | External visual inspection | 16 | BB 11986 | New Finding: Discharge of safety valve was not free from danger of scalding. | Safety valve outlet line shall not affect emergency discharge path or discharge of safety valve shall be free from danger of scalding. |  | Mar 2 2026 |  | 1 MONTH | In Progress
Followup Inspection | External visual inspection | 17 | BB 11986 | New Finding: Drainage arrangement was not installed for one or more safety valves. | Drainage arrangement must be installed for all safety valves as per manufacturer published guideline or at the lowest point of outlet line. |  | Apr 2 2026 |  | 2 MONTHS | In Progress
Followup Inspection | Functional test inspection | 18 | BB 11986 | New Finding: There was no acoustic or optical alarm when the limiter was activated. | An acoustic with optical alarm should be installed. |  | Mar 2 2026 |  | 1 MONTH | In Progress
Followup Inspection | External visual inspection | 19 | BB 11986 | New Finding: There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve |  | Apr 2 2026 |  | 2 MONTHS | In Progress
Followup Inspection | External visual inspection | 20 | BB 11986 | New Finding: Exhaust gas is re-entering the boiler room from the chimney | Chimney height should be increased so that no exhaust gas re-enter the boiler room |  | Apr 2 2026 |  | 2 MONTHS | In Progress