## Structural
Date
04-Jul-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Century Apparels Ltd - Unit 2, Holding # 01, Block-B D.N. Road, West Masdair Fatullah, Narayanganj-1400, Narayanganj, Dhaka
Date of Inspection |  | 2017-03-19
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Apparently no obvious lateral stability of any sheds. | Building engineer is required to check the stability system, connection adequancy of all sheds against lateral loading. | Corrected | Jun 30 2021 | On 16-Jul-2017: Factory authority has not appointed any consultancy firm yet. Factory is required to appoint a consultancy firm to carry out engineering assessment as soon as possible. On 22-02-2018:This issue is required to cover in Engineering Assessment (EA). Factory has submitted revised EA to Accord on 25th February 2018. EA is under Accord review. On 9th-Sept-2018: This issue is required to be covered in EA. Factory submitted EA of the sheds on 13th May 2018 and meeting minutes sent from Accord on 5th Sept 2018. Factory is required to submit revised EA. On 24th-Nov-2018: This issue has been cover in EA. EA of factory building was accepted by ACCORD on 22nd November 2018. During verification inspection, some mismatch was found in between as-built drawing and actual site condition. Mismatches are; diagonal and vertical members of truss was found 50mmX50mm at Knitting & Utility shed, Diagonal members of truss was found 38mmX38mm at dinning shed & truss height was found 4'-7" at Boiler & steel washing shed. Factory is required to submit updated drawing and FEM analysis model to ACCORD within 7 days from receiving the report. On 23-Apr-2019: Resubmission of EA documents is required. Last review comment was sent on 22-Apr-2019. On 07- October- 2019: Factory submitted revised documents to Accord on 26th February 2019 as per verification report. Later review comment was sent from Accord on 22nd April 2019 and factory was required to submit the revised documents to Accord within 6th May 2019. Finally factory submitted the revised documents to Accord on 13-October-2019 which is under review. On 14-Sep-2021: This issue is covered in EA. EA was accepted from ACCORD on 22-N0v-2018. However, during verification inspection on 24-Nov-2018, some mismatches were found between as built drawings and on-site condition. Later, the factory submitted the revised EA documents to RSC which was re-accepted on 14-Jan-2021. On 31-May-2022: Corrected previously. Factory has got EA acceptance from ACCORD on 22-Nov-2018. Due to discrepancies, factory has re-submitted the revised EA to RSC and got re-acceptance of Shed-1 (Knitting & Utility Shed), Shed-2 (Boiler & Washing), Shed-3 (Wastage storage) & Shed-4 (Dinning Shed) on 14-Jan-2021. On 17-Aug-2022: Corrected from previous follow up inspection. This issue had been covered in EA report. Factory management got EA re-acceptance from RSC on 14-January-2021. On 16-Oct-2022: This issue was corrected from previous inspection. This issue had been covered in EA which was re-accepted by RSC on 14-January-2021. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. On 16-Sep-2025: Previously corrected. | Within 6 Weeks | Corrected
Initial Inspection |  | 2 | Apparently no obvious lateral stability of any sheds. | Carry out Engineering Assessment for all sheds. Carry out remedial works arise from engineering Assessment. | Corrected | Jun 30 2021 | On 16-Jul-2017: Engineering assessment has not been carried out yet since factory authority has not appointed any consultancy firm On 22-02-2018:This issue is required to cover in Engineering Assessment (EA) .Factory has submitted revised EA to Accord on 25th February 2018 .EA is under Accord review. On 9th-Sept-2018: This issue is required to be covered in EA. Factory submitted EA of the sheds on 13th May 2018 and meeting minutes sent from Accord on 5th Sept 2018. Factory is required to submit revised EA. On 24th-Nov-2018: This issue has been cover in EA. EA of factory building was accepted by ACCORD on 22nd November 2018. During verification inspection, some mismatch was found in between as-built drawing and actual site condition. Mismatches are; diagonal and vertical members of truss was found 50mmX50mm at Knitting & Utility shed, Diagonal members of truss was found 38mmX38mm at dinning shed & truss height was found 4'-7" at Boiler & steel washing shed. Factory is required to submit updated drawing and FEM analysis model to ACCORD within 7 days from receiving the report. As per accepted EA factory is required to complete retrofitting works within 28th February 2019. On 23-Apr-2019: Resubmission of EA documents is required . Last review comment was sent on 22-Apr-2019. On 07- October- 2019: Factory submitted revised documents to Accord on 26th February 2019 as per verification report. Later review comment was sent from Accord on 22nd April 2019 and factory was required to submit the revised documents to Accord within 6th May 2019. Finally factory submitted the revised documents to Accord on 13-October-2019 which is under review. Factory is required to follow the recommendation of accepted EA report for the remedial works. On 14-Sep-2021: This issue is covered in EA. This issue is covered in EA. EA was accepted from ACCORD on 22-N0v-2018. However, during verification inspection on 24-Nov-2018, some mismatches were found between as built drawings and on-site condition. Later, the factory submitted the revised EA documents to RSC which was re-accepted on 14-Jan-2021. As per EA recommendation, remediation is required for all the sheds. The factory has started remediation works for Dinning shed and Knitting & Utility shed. During inspection, retrofitting work was found on-going. However, the factory has demolished boiler & washing shed partially. External & internal walls were still found in place. The timeline for remediation works is 30-Oct-2021. In addition, as per factory management, also the wastage storage shed will be demolished. The factory is required to complete all the remediation works within the mentioned timeline. On 31-May-2022: This issue was covered in EA. Factory has got EA acceptance from ACCORD on 22-Nov-2018. Due to discrepancies, factory has re-submitted the revised EA to RSC and got re-acceptance of Shed-1 (Knitting & Utility Shed), Shed-2 (Boiler & Washing), Shed-3 (Wastage storage) & Shed-4 (Dinning Shed) on 14-Jan-2021. During inspection, it was found that factory has completed the retrofitting works of Shed-1 and Shed-4. Work completion certificate and material test report was found on-site. However, some mismatch was observed (column layout) in the Shed-1. No change was observed in FEM model while column layout revised according to site condition. Factory management has sent the updated drawing via email on 01-June-2022 as a supporting document which was found satisfactory. On the other hand, Shed-2 was demolished by factory management, but Shed-3 was not either demolished or retrofitted by the factory till the date of inspection. However, later factory has submitted a copy of rental agreement to RSC via email on 12-June-2022. After that RSC has replied to separate the structure from the premises of the factory permanently and not to use the shed anymore in future. Now, factory is required to separate the shed by installing fence between the Shed-1 & Shed-3 and to stop the all access of shed-3 from the premises of the Century Apparels Ltd. On 17-Aug-2022: This issue had been covered under EA report. Factory management got EA re-acceptance from RSC on 14-January-2021. During inspection, it was found that factory had completed the retrofitting works of Shed-1 and Shed-4. Work completion certificate and material test report was found on-site. On the other hand, Shed-2 was demolished by factory management, but Shed-3 was not either demolished or retrofitted by the factory till the date of inspection. However, later factory has submitted a copy of rental agreement to RSC via email on 12-June-2022. After that RSC has replied to separate the structure from the premises of the factory permanently and not to use the shed anymore in future. Now, factory is required to separate the shed by installing fence between the Shed-1 & Shed-3 and to stop the all access of shed-3 from the premises of the Century Apparels Ltd. On 16-Oct-2022: EA of the factory was re-accepted by RSC on 14-Jan-2021. As per the recommendation of the EA, the factory completed the retrofitting works for the Shed-1 & Shed-4 which was verified in previous inspection and found satisfactory. And Shed-2 has been demolished. Lastly, no retrofitting has been done for the Shed-3 as the factory rented the Shed-3 to another factory. As per recommendation from RSC, the factory was required to separate the Shed-3 by providing the fence to restrict all access from the premises of Century Apparels Ltd. During inspection, it was found that the Shed-3 is no longer being used by Century Apparels Ltd. Unit-2. The entry of the Shed-3 has been restricted by blocking the gate at the side of the factory premises of Century Apparels Ltd. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. Shed-1 and Shed-4 were retrofitted. Shed-2 has been demolished. Shed-3 is not in use & restricted. On 16-Sep-2025: Previously corrected. | Within 6 Weeks | Corrected
Initial Inspection |  | 3 | Apparently no obvious lateral stability of any sheds. | Carry out remedial works arise from engineering Assessment. | Corrected | Jun 30 2021 | On 16-Jul-2017: Remedial works will be carried out after completion of engineering assessment if required. On 22-02-2018:This issue is required to cover in Engineering Assessment (EA) .Factory has submitted revised EA to Accord on 25th February 2018 .EA is under Accord review. On 9th-Sept-2018: This issue is required to be covered in EA. Factory submitted EA of the sheds on 13th May 2018 and meeting minutes sent from Accord on 5th Sept 2018. Factory is required to submit revised EA. On 24th-Nov-2018: This issue has been cover in EA. EA of factory building was accepted by ACCORD on 22nd November 2018. During verification inspection, some mismatch was found in between as-built drawing and actual site condition. Mismatches are; diagonal and vertical members of truss was found 50mmX50mm at Knitting & Utility shed, Diagonal members of truss was found 38mmX38mm at dinning shed & truss height was found 4'-7" at Boiler & steel washing shed. Factory is required to submit updated drawing and FEM analysis model to ACCORD within 7 days from receiving the report. As per accepted EA factory is required to complete retrofitting works within 28th February 2019. On 23-Apr-2019: Resubmission of EA documents is required . Last review comment was sent on 22-Apr-2019. Remedial works has not been started yet. On 07- October- 2019: Factory submitted revised documents to Accord on 26th February 2019 as per verification report. Later review comment was sent from Accord on 22nd April 2019 and factory was required to submit the revised documents to Accord within 6th May 2019. Finally factory submitted the revised documents to Accord on 13-October-2019 which is under review. Factory is required to follow the recommendation of accepted EA report for the remedial works. On 14-Sep-2021: This issue is covered in EA. This issue is covered in EA. EA was accepted from ACCORD on 22-N0v-2018. However, during verification inspection on 24-Nov-2018, some mismatches were found between as built drawings and on-site condition. Later, the factory submitted the revised EA documents to RSC which was re-accepted on 14-Jan-2021. As per EA recommendation, remediation is required for all the sheds. The factory has started remediation works for Dinning shed and Knitting & Utility shed. During inspection, retrofitting work was found on-going. However, the factory has demolished boiler & washing shed partially. External & internal walls were still found in place. The timeline for remediation works is 30-Oct-2021. In addition, as per factory management, also the wastage storage shed will be demolished. The factory is required to complete all the remediation works within the mentioned timeline. On 31-May-2022: This issue was covered in EA. Factory has got EA acceptance from ACCORD on 22-Nov-2018. Due to discrepancies, factory has re-submitted the revised EA to RSC and got re-acceptance of Shed-1 (Knitting & Utility Shed), Shed-2 (Boiler & Washing), Shed-3 (Wastage storage) & Shed-4 (Dinning Shed) on 14-Jan-2021. During inspection, it was found that factory has completed the retrofitting works of Shed-1 and Shed-4. Work completion certificate and material test report was found on-site. However, some mismatch was observed (column layout) in the Shed-1. No change was observed in FEM model while column layout revised according to site condition. Factory management has sent the updated drawing via email on 01-June-2022 as a supporting document which was found satisfactory. On the other hand, Shed-2 was demolished by factory management, but Shed-3 was not either demolished or retrofitted by the factory till the date of inspection. However, later factory has submitted a copy of rental agreement to RSC via email on 12-June-2022. After that RSC has replied to separate the structure from the premises of the factory permanently and not to use the shed anymore in future. Now, factory is required to separate the shed by installing fence between the Shed-1 & Shed-3 and to stop the all access of shed-3 from the premises of the Century Apparels Ltd. On 17-Aug-2022: This issue had been covered under EA report. Factory management got EA re-acceptance from RSC on 14-January-2021. During inspection, it was found that factory had completed the retrofitting works of Shed-1 and Shed-4. Work completion certificate and material test report was found on-site. On the other hand, Shed-2 was demolished by factory management, but Shed-3 was not either demolished or retrofitted by the factory till the date of inspection. However, later factory has submitted a copy of rental agreement to RSC via email on 12-June-2022. After that RSC has replied to separate the structure from the premises of the factory permanently and not to use the shed anymore in future. Now, factory is required to separate the shed by installing fence between the Shed-1 & Shed-3 and to stop the all access of shed-3 from the premises of the Century Apparels Ltd. On 16-Oct-2022: EA of the factory was re-accepted by RSC on 14-Jan-2021. As per the recommendation of the EA, the factory completed the retrofitting works for the Shed-1 & Shed-4 which was verified in previous inspection and found satisfactory. And Shed-2 has been demolished. Lastly, no retrofitting has been done for the Shed-3 as the factory rented the Shed-3 to another factory. As per recommendation from RSC, the factory was required to separate the Shed-3 by providing the fence to restrict all access from the premises of Century Apparels Ltd. During inspection, it was found that the Shed-3 is no longer being used by Century Apparels Ltd. Unit-2. The entry of the Shed-3 has been restricted by blocking the gate at the side of the factory premises of Century Apparels Ltd. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. On 16-Sep-2025: Previously corrected. | Within 6 months | Corrected
Initial Inspection |  | 4 | No drawings were available on site. | Building engineer is required to produce the as built drawings for all sheds as part of engineering assessment. | Corrected | Jun 30 2021 | On 16-Jul-2017: As-built drawings have not been produced for all sheds as part of EA since factory authority has not appointed any consultancy firm. On 22-02-2018:Fcatory authority has produced as built drawing for all the sheds as a part of EA .Drawings were available on site .Factory has submitted revised EA to Accord on 25th February 2018 .EA is under Accord review. On 9th-Sept-2018: This issue is required to be covered in EA. Factory submitted EA of the sheds on 13th May 2018 and meeting minutes sent from Accord on 5th Sept 2018. Factory is required to submit revised EA. On 24th-Nov-2018: As built drawing was produced as part of EA. EA of factory building was accepted by ACCORD on 22nd November 2018. During verification inspection, some mismatch was found in between as-built drawing and actual site condition. Mismatches are; diagonal and vertical members of truss was found 50mmX50mm at Knitting & Utility shed, Diagonal members of truss was found 38mmX38mm at dinning shed & truss height was found 4'-7" at Boiler & steel washing shed. Factory is required to submit updated drawing and FEM analysis model to ACCORD within 7 days from receiving the report. On 23-Apr-2019: Resubmission of EA documents is required . Last review comment was sent on 22-Apr-2019. As-built drawing matched with site condition. On 07- October- 2019: As built drawing was produced as part of EA. Factory submitted revised documents to Accord on 26th February 2019 as per verification report. Later review comment was sent from Accord on 22nd April 2019 and factory was required to submit the revised documents to Accord within 6th May 2019. Finally factory submitted the revised documents to Accord on 13-October-2019 which is under review. On 14-Jan-2021: EA has been re-accepted on 14-jan-2021. All retrofitting work is required to be completed by 30 June 2021. On 14-Sep-2021: This issue is covered in EA. EA was accepted from ACCORD on 22-N0v-2018. However, during verification inspection on 24-Nov-2018, some mismatches were found between as built drawings and on-site condition. Later, the factory submitted the revised EA documents to RSC which was re-accepted on 14-Jan-2021. During inspection, no major mismatch was found between as built drawings and on-site condition. On 31-May-2022: Corrected previously. As-built drawing was produced by factory management as a part of EA. Factory has got EA acceptance from ACCORD on 22-Nov-2018. Due to discrepancies, factory has re-submitted the revised EA to RSC and got re-acceptance of Shed-1 (Knitting & Utility Shed), Shed-2 (Boiler & Washing), Shed-3 (Wastage storage) & Shed-4 (Dinning Shed) on 14-Jan-2021. During inspection, no mismatch was observed in Shed-1 and Shed-2. However, Shed-2 was found demolished and Shed-3 was not used by factory management. On 17-Aug-2022: Corrected from previous follow up inspection. This issue had been covered in EA report. As built drawings were prepared as a part of EA report. Factory management got EA re-acceptance from RSC on 14-January-2021. On 16-Oct-2022: This issue was corrected from previous inspection. As built drawings were prepared as part of EA which was re-accepted by RSC on 14-January-2021. On 09-Dec-2024: Corrected previously. On 14-May-2025: Corrected previously. On 16-Sep-2025: Previously corrected. | Within 6 Weeks | Corrected

## Fire
Date
04-Jul-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Century Apparels Ltd - Unit 2, Holding # 01, Block-B D.N. Road, West Masdair Fatullah, Narayanganj-1400, Narayanganj, Dhaka
Date of Inspection |  | 2017-03-19
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Production area is not separated from adjacent utility facilities (Boiler, Generator & sub-station) at Shed-01 & Shed-02. | Separate the Generator & Sub-station facilities from production area by 2- hr. fire rated construction & boiler room by 1-hr. fire rated construction. Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr fire rated materials to maintain the fire separation for generator & sub-station room & 0.75 hr. fire rated materials to maintain the fire separation for boiler room if required. All exhaust systems shall discharge to the exterior of the building in a safe location. | Corrected | Aug 16 2017 | On 10/12/2019: No listing mark could be detected on installed gypsum board or evidence was not provided regarding installation of board. However, certificate has been provided. Factory shall ensure authenticity of gypsum board. On 24-02-2020 (Special Inspection): Listing mark has been found in installed gypsum board. Certification documents has been found. However factory shall ask the installer for design philosophy and shall open up a portion of installed area to check the installation. On 16/03/2020: Factory shall follow comments from special inspection & shall open up a portion of installed area during inspection to verify the installation. On 10/12/2020 (Special Inspection): Corrected. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected as per previous follow up. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. (Note: Gypsum board installed covering steel beam. Documents and listed design related to gypsum board should be kept on-site.) | 3 months | Corrected
Initial Inspection |  | 2 | Areas used for in-process storage of combustible materials are open to surrounding production area at North side of Shed-01. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Aug 16 2017 | On 07.10.2019: Corrected. On 10/12/2019: Corrected as per previous follow-up. Note: Defined storage area shall maintain as per recommendation. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected as per previous follow-up. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Refer to issue no.# 13 On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. The factory has maintain the in-process storage area as per recommendation. On 16-Sep-25: Corrected. | 1 month | Corrected
Initial Inspection |  | 3 | CNG cylinders storage area is not separated by fire-rated construction & was open to exit discharge path of Shed-04 (Dining Shed). | Separate the CNG Cylinder storage by providing a dedicated storage facilities with 2-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. | Corrected | May 18 2017 | On 23/04/2019: Corrected as per previous follow up. On 07.10.2019: Corrected. On 10/12/2019: Corrected. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected as per previous follow-up. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. CNG cylinders sore not found during inspection. On 09/05/2024: Corrected On 14-May-25: Corrected. CNG cylinder storage was not found during the inspection. On 16-Sep-25: Corrected. | 1 month | Corrected
Initial Inspection |  | 4 | Doors along means of egress are provided with non compliant locking system at Shed-01 & Shed-02 | 1. Remove all non compliant locking features from egress doors. 2. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. 3. Doors may be locked where the latch and lock are disengaged with one motion where the occupant load does not exceed 49 persons. 4. Doors may be provided with locking hardware from the ingress side provided that a panic bar is installed on any door with an occupant load exceeding 49 persons. | Corrected | May 18 2017 | On 23/04/2019: Corrected. On 07.10.2019: Corrected. On 10/12/2019: Corrected. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected. On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 5 | Sliding doors have provided along means of egress at Shed-01 & Shed-02 | Replace all sliding type doors by the side‐hinged swinging type doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | May 18 2017 | On 23/04/2019: Corrected as per previous follow up. On 07.10.2019: Corrected. On 10/12/2019: Corrected. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 6 | Building did not have occupant load signs at the required locations. | Provide occupant load signs at the required locations. | Corrected | Apr 30 2017 | On 17/11/2018: Corrected as per previous follow up. On 23/04/2019: Corrected as per previous follow up. Note: No occupant load sign has been observed. On 07.10.2019: Corrected. On 10/12/2019: Corrected. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Refer to the issue no. # 14 On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | The fire detection system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire detection system with a new, listed addressable fire detection system in accordance with NFPA 72. | We have submited pre T&cv documents on 16/09/2025 and RSC Accepted on 30/11/2025. Now We are awaiting for pre T&cv audit. | Oct 18 2017 | For Previous Comments See Previous Report On 05/10/2021: The system is not corrected where major modifications are required, for details please see T&CVI report. On 17/08/2022: Request to see full on site pre-T&C report. On 05/03/2023: Pre-T&CVI found that FADS is not ready for full T&C. See the details pre-T&CVI report. On 09/05/2024: Factory has submitted the documents of Pre T&C VI for Fire Alarm & Detection system on dated 30 August 2023. During the inspection the panel was found active with remarkable fault ( General Trouble, NAC trouble, Supervisory alarm, devices bypass). Also the modification work was ongoing. However, after completing the modification work factory will informed to RSC for further processed. On 14-May-25: The factory has submitted the as-built design & other related documents (3rd time) to the RSC for Pre-T&CVI on 22-Jan-2025 (both ID-11059 & ID-12654 share single fire alarm panel) which is under review. However, during the inspection the fire alarm control panel was found active with some trouble. The factory is required to ensure that the FACP remains active and in normal operating condition at all times. On 16-Sep-25: Factory has submitted as-built design and drawing of Fire Alarm Detection System (4th time) on 19th August, 2025 which is currently under RSC review. FACP was found active but 18 numbers of troubles found during the visit. RPO Comments on 22 Jan 2026-As per the email dated 30 Nov 2025, Century Apparels Ltd. Unit-2 (ID - 12654) is ready for Pre-T&C VI (FADS). On 08-June-2026: T&C has been conducted. The system is not approved, Again Testing and Commissioning Verification Inspection is Required. Refer to the full-T&C report for details. | Design within 3 months, Install within 6 months | In Progress
Initial Inspection |  | 8 | Inspection, testing, and maintenance for the fire detection system is not in accordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Oct 18 2017 | On 23/04/2019: Corrected. On 07.10.2019: Corrected. On 10/12/2019: Corrected as per previous follow-up. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected as per previous follow-up. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. The factory shall maintain the fire alarm and detection system ITM as per NFPA-72, Table-14.3.1 On 16-Sep-25: Corrected. The factory shall maintain the fire alarm and detection system ITM as per NFPA-72, Table-14.3.1. | Within 3 months | Corrected
Initial Inspection |  | 9 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10 and ACCORD standards. | Corrected | Jul 18 2017 | On 17/11/2018: Corrected as per previous follow up. On 23/04/2019: Corrected. On 07.10.2019: Corrected. On 10/12/2019: Corrected. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: All exit stairs, egress paths and aisles. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Jul 18 2017 | On 17/11/2018: Corrected as per previous follow up. On 23/04/2019: Corrected as per previous follow up. Note: During inspection emergency light was not functional in Shed-1. Factory shall ensure proper maintenance. On 07.10.2019: Corrected. On 10/12/2019: Corrected as per previous follow-up. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | Inspection, testing, and maintenance for the emergency lighting system were not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | Corrected | Jul 18 2017 | On 27/12/2017: Corrected. On 23/07/2018: Corrected. On 17/11/2018: Corrected as per previous follow up. On 23/04/2019: Corrected as per previous follow up. On 07.10.2019: Corrected. On 10/12/2019: Corrected. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: Corrected. On 10/12/2020 (Special Inspection): Not checked during special inspection. On 31/08/2021 (Special Inspection): Not verified. On 05/10/2021: Corrected. On 17/08/2022: Corrected. On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 12 | New Findings (4th Follow Up): CNG cylinders storage area is not separated by fire-rated construction from other occupancy adjacent to dinning shed & boiler shed. | Separate the CNG Cylinder storage by providing a dedicated storage facilities with 2-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations & provide proper ventilation system. | Corrected | Dec 17 2018 | On 10/12/2019: Corrected. Not found. On 24-02-2020 (Special Inspection): Not checked during special inspection. On 16/03/2020: During inspection, CNG cylinder was found using as a fuel of boiler. Factory shall remove CNG & ancillary equipment from factory building. On 10/12/2020 (Special Inspection): CNG cylinder has been found. Reportedly, factory shall remove CNG cylinder from factory building. On 31/08/2021 (Special Inspection): Not corrected yet. Condition is the same as it was before. CNG/Storage cylinder van & CNG high pressure ancillary equipment are using as a fuel of boiler at the very risky & unsafe way in a open place just beside the main production building and staff dining areas. Factory shall complete the remediation as per recommendation without any further delay. On 05/10/2021: Corrected. Removed the facility now gas boiler changed to diesel boiler. On 17/08/2022: Corrected. On 05/03/2023: Corrected. CNG cylinder store not found during inspection. On 09/05/2024: Corrected On 14-May-25: Corrected. CNG Cylinder storage was not found during the inspection. On 16-Sep-25: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 13 | New Findings: Areas used for in-process storage of combustible materials are open to surrounding production area at North side of Shed. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Sep 17 2022 | On 17/08/2022: New Finding On 05/03/2023: Corrected. Maintaining. On 09/05/2024: Corrected On 14-May-25: Corrected. In-process storage was found within limit. On 16-Sep-25: Corrected. (Note-Unenclosed combustible storage is maintained maximum height of 2.4m and maximum area of 23m2 and separate by a minimum clear distance of 3m. Need to ensure that in-process storage area do not exceed 10% of floor area.) | Within 1 months | Corrected
Follow Up Inspection |  | 14 | New Findings: Building did not have occupant load signs at the required locations. | Provide occupant load signs at the required locations. | Corrected | Sep 1 2022 | On 17/08/2022: New Finding On 05/03/2023: Corrected. On 09/05/2024: Corrected On 14-May-25: Corrected. On 16-Sep-25: Corrected. | Within 15 days | Corrected
Follow Up Inspection |  | 15 | New Findings (15th FUI): The fire pump room is not provided with adequate fire separation due to unprotected exterior wall of dining shed-4 within 10 ft distance. Location: Fire pump room. | Provide fire pump room with 2 hr. rated fire separation when building is not fully sprinklered and 1 hr. rated fire separation when the building is provided with automatic sprinklers in accordance with NFPA 13. Or, Physically separate the pump room from the protected building by a minimum of 50 ft. (15.3 m) in accordance with NFPA 20. Provide direct access from the outside or provide a 2-hr enclosed passageway from an enclosed stairway or exterior exit. | We have already install fire door. | Dec 16 2025 | On 16-Sep-25: New Findings. RPO Comments on 22 Jan 2026- The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 Months | Pending Verification
Follow Up Inspection |  | 16 | New Findings (15th FUI): Abrupt changes in the elevation of walking surfaces were observed, not meeting the RSC Technical Guidelines (Standard)¹ V1.0 Section 6.3.4. Location: Shed-1 second exit discharge. | Abrupt changes in elevation of walking surfaces shall not exceed ¼ in. unless provided with a beveled slope of 1 in 2 that do not exceed ½ in. Changes greater than ½ in. shall meet the requirements for RSC Technical Guidelines (Standard)¹ V1.0 Section 6.3.5. | The walking surfaces are now clear. | Nov 16 2025 | On 16-Sep-25: New Findings. RPO Comments on 22 Jan 2026- The factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 Months | Pending Verification

## Electrical
Date
04-Jul-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Century Apparels Ltd - Unit 2, Holding # 01, Block-B D.N. Road, West Masdair Fatullah, Narayanganj-1400, Narayanganj, Dhaka
Date of Inspection |  | 2017-03-19
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/ less reflection in existing SLD. | Electrical SLD must be updated properly; all the required information must be mentioned there; and it shall be updated when you do substantial amount of changes of your electrical system. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: SLD is not available yet. On 23/07/2018: Prepare as-built SLD. Do circuit marking accordingly. On 17/11/2018: Need to work on this issue. On 23/04/2019: Not Corrected. On 07/10/2019: Factory is working on the issue. On 10/12/2019: SLD needs modification as per the last review. On 24/02/2020 (Special Inspection):Not Corrected. Still need modification as per review. On 16/03/2020: The identification shall include an approved degree of detail that allows each circuit to be distinguished from all others. On 14/09/2021: Not Corrected. SLD has submitted to RSC. On 22/04/2022: Not Corrected. Some progress has been observed. SLD is under review of the RSC. On 17/08/2022: Not Corrected. Some progress has been observed. SLD is accepted from RSC. But SLD is not as-built (Cable mismatch, load mismatch, circuit identification etc.) On 05/03/2023: Not Corrected. SLD is not as-built. No progress has been observed. On 24/01/2024: Not corrected. Significant progress has been observed. Individual protection missing, cable identification missing, protection missing from transformer to manual COS, transformer & generator ecc cable mismatch, earthing layout shall be updated. On 09/05/2024: Not Corrected. The factory has implemented SLD on the 3rd and 4th floor. Mismatch (Cable, Circuit and load info, Comb busbar, circuit breaker, earthing layout, individual protection) has been observed with accepted SLD. Almost 70% progress has been observed. On 01/07/2024: Corrected. | 3 Months | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed. | Factory has to design lightning protection system (LPS) for the whole factory (where the Risk index is more than 40), Once a LPS is designed properly, installation must be done accordingly asap. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Drawing information is inadequate. On 23/07/2018: Prepare drawing with relevant contents. Calculate zone of protection accurately. On 17/11/2018: No of Two shed's LPS installation is stilling missing. On 23/04/2019: Need to re-calculate the slope calculation for sheds On 07/10/2019: Mark earth pit accordingly. On 10/12/2019: Down conductor for knitting shed need to recalculate. Down conductor size shall be 12.7mm. On 24/02/2020 (Special Inspection): Not Corrected. Still some pit need to change. On 16/03/2020: Corrected. | 2 Months | Corrected
Initial Inspection |  | 3 | Maintenance record doesn't reflect with housekeeping. | Periodic maintenance must be done in the facility; proper and relevant documentation shall be kept. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Corrected. | 2 Months | Corrected
Initial Inspection |  | 4 | Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. Safety program is initiated but no influences at field. On 23/07/2018: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables must be removed as soon as possible. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Corrected. | 1 Month | Corrected
Initial Inspection |  | 6 | MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load and the cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. Factory asked for time extension till 30/05/2018. Not accepted. On 23/07/2018: Corrected. | 2 Months | Corrected
Initial Inspection |  | 7 | Cables in service are joined (splicing) between terminations. | Cables in service are joined (splicing) between terminations. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Corrected. Not found this time. | 2 Months | Corrected
Initial Inspection |  | 8 | Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized according to the BNBC 2006, article 2.8, table 8.2.11. Cable size shall be selected depending on the CB's response time and phase cables' size. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Not corrected. No remarkable progress observed. On 17/11/2018: Not Corrected. Factory people working on this issue. On 23/04/2019:Not Corrected. On 07/10/2019: Not corrected. On 10/12/2019: Corrected. | 2 Months | Corrected
Initial Inspection |  | 9 | Cable connected to bus-bar terminal without cable lug. | Each electrical circuit must be terminated at single bus-bar terminals using proper sized cable lug. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 10 | Distribution Board's top/ bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used where required. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Corrected. | 2 Months | Corrected
Initial Inspection |  | 11 | Indicator lights are mounted without disconnecting device. | Indicator lights should be connected by control device such as rated fuse or MCB. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Not corrected. The issue still exists in utility room. On 17/11/2018: Corrected. | 2 Months | Corrected
Initial Inspection |  | 12 | Panel doors are not connected with earth. | All metal installations which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Not corrected. On 17/11/2018: Not Corrected. On 23/04/2019: Corrected. | 1 Month | Corrected
Initial Inspection |  | 14 | Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Corrected. Not found this time. | Immediate | Corrected
Initial Inspection |  | 15 | Earth connections for different electrical installation are not segregated. | All the earth connections (transformer, generator and electrical systems) must be segregated and clearly marked (for TT earthing system). | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. Factory asked for time extension till 03/10/2018. Not accepted. On 23/07/2018: Not corrected. Factory is working on the issue. On 17/11/2018: Corrected. | 3 Months | Corrected
Initial Inspection |  | 16 | Electrical distribution box/panels are full of fluffs (lint/dirt). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Corrected. | 1 Month | Corrected
Initial Inspection |  | 17 | Transformer room is used as store (or used as temporary storage). The storages make obstacle for entry/exits. Fall hazard may happen. | Transformer room must be kept neat and clean and entrance/exit shall be kept cleaned for obstacle free movement. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 18 | Electrical earth cables and earth pits are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on all cables used in the system. These shall be according to SLD or earth pit drawing/layout.. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Not corrected. Pits are marked. Earth cables are needed to be identified accordingly. On 17/11/2018: Corrected. | 1 Month | Corrected
Initial Inspection |  | 19 | Light fixtures are not fixed properly (Typical). The joint box is also kept open. | Ensure fixation of all light from ceiling using proper support. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Not corrected. The issue still exists in utility room. On 17/11/2018: Corrected. At inspection time not observe this type of issue. | 1 Month | Corrected
Initial Inspection |  | 20 | Earth Pit resistance test record doesn't match with field. | Adequate number of earth pits must be ensured (if it's lower in numbers) and record must be made accordingly. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Not corrected. Test is done. But the report is needed to be prepared in adequate manner. On 17/11/2018: Corrected. | 1 Month | Corrected
Initial Inspection |  | 21 | Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record and significantly lower sized cables' record shall be avoided. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Not Corrected. On 23/07/2018: Not corrected. The test is done. But the report is needed to be prepared in adequate manner. On 17/11/2018: Corrected. On 10/12/2019: Insulation resistance need to test again with pictorial evidence. | 1 Month | Corrected
Initial Inspection |  | 22 | Thermography scanning report is unavailable. | Thermography survey must be done and recorded at least twice in a year. | Corrected | Sep 15 2017 | On 16/07/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 23 | Maintenance movement is making obstacle due to improper cable tray on floor in the boiler room. | Cable tray shall be laid properly. Covered cable trench must be equal to working floor height. If not, extended area must be slopped at both sides to avoid obstacle. | Corrected | Sep 15 2017 | On 16/07/2017: Not Corrected. New committed time line is given till 15/09/2017 to close this issue. On 27/12/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Cable trench is left open. | Cable trench must be covered properly. cover shall not be permanent type for doing periodic checking. | Corrected | Aug 30 2017 | On 27/12/2017: Not Corrected. Covered not done properly. On 23/07/2018: Not corrected. On 17/11/2018: Not Corrected. On 23/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: Periodicity of Transformer Oil Test (dielectric strength, moisture content and flash point) survey is not continued. | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year. If the operation of transformer is 24/7 in the facility twice in a year is a better practice. | Corrected | Mar 10 2018 | Factory asked for time extension till 03/10/2018. Time extended from 10/02/2018 to 10/03/2018. On 23/07/2018: Not corrected. Ambiguity found in report. On 17/11/2018: Not Corrected. On 23/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Panel/distribution board is not firmly fixed with the foundation. | Each electrical installation in the facility shall be grouted properly. | Corrected | Sep 30 2018 | Factory asked for time extension till 30/09/2018. Time extended from 10/09/2018 to 30/09/2018. On 17/11/2018: Not Corrected. On 23/04/2019: Not Corrected. On 07/10/2019: Not corrected as not completed yet. On 10/12/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. | Corrected | Sep 30 2018 | Factory asked for time extension till 30/09/2018. Time extended from 10/09/2018 to 30/09/2018. On 17/11/2018: Not Corrected. On 23/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Panel's top/bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. | Corrected | Sep 30 2018 | Factory asked for time extension till 30/09/2018. Time extended from 10/09/2018 to 30/09/2018. On 17/11/2018: Not Corrected. On 23/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Corrected | Feb 15 2019 | On 23/04/2019: Not Corrected. Factory is asking for time extension 14-Sep-2019. Not Accepted. On 07/10/2019: Not corrected By CH: Factory asked for time extension till 31-Jan-2020.Not accepted. On 10/12/2019: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 30 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. | Corrected | Jan 15 2019 | On 23/04/2019: Not Corrected. On 07/10/2019: Not corrected On 10/12/2019: Cable are not sized as per cumulative circuit breaker rating. Remove multiple cable from circuit breaker terminal. On 24/02/2020 (Special Inspection): Not Corrected. Found in few places. On 16/03/2020: This issue is found within a panel board. On 14/09/2021: Not Corrected. Found in few places. On 24/04/2022: Not Corrected. Some progress has been observed. But still found in few panels. On 17/08/2022: Not Corrected. Factory has started working on it. Some progress has been observed. On 05/03/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Oct 30 2019 | On 10/12/2019: Corrected. | 1 Week | Corrected
Follow Up Inspection |  | 32 | New Finding Periodicity of Transformer Oil Test (dielectric strength test) survey is not continued. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Corrected | Apr 20 2020 | Factory asked for time extension till 30-Sep-2020. Not accepted. On 14/09/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Not Corrected. Significant progress has been observed. Still found in few places. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Lightning Protection System (LPS) is not maintained properly. (loose connection/ junction box, conductors & joints are rusted.) | Periodic maintenance shall be done to maintain LPS. Rusted/ damaged junction box, conductors & air terminal shall be cleaned & replaced where necessary. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. Disconnected conductor found. Joints are rusted as before. No progress observed. On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Earthing busbar size is inadequate. | Earth bus bar sized shall be determined according to main earthing cable (if those are according to BNBC or designed according to Adiabatic method). | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Not Corrected. Progress has been observed. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected | Jun 8 2022 | On 17/08/2022: Not Corrected. Observed at few points. On 05/03/2023: Not Corrected. Progress has been observed. On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Distribution boards have no clear identification markings. Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. | Corrected | Jul 8 2022 | On 17/08/2022: Not Corrected. No progress observed. On 05/03/2023: Not Corrected. Progress has been observed. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Corrected | Nov 8 2022 | On 05/03/2023: Not Corrected. No progress has been observed. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Panel base plates are removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. | Corrected | Nov 8 2022 | On 05/03/2023: Not Corrected. Progress has been observed. But panels are not sealed properly. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Electrical devices are not fixed at base (Kept on table). | All electrical component must be fixed at base with proper arrangement. | Corrected | Nov 8 2022 | On 05/03/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 41 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Corrected | Nov 8 2022 | On 05/03/2023: Not Corrected. The factory is working on it. On 24/01/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Lint and dust deposited on and around the transformer. | Transformer top and around it shall be kept neat and clean. | Corrected | Apr 15 2023 | On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Compressor machine mounted on wheel & is not locked. | Compressor machine mounted on wheel must be anchored or the wheels must be locked to prevent from trolling. | Corrected | Apr 15 2023 | On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Nut-bolt, bus-bar & washer are rusted in the sub/distribution board. | Rusted nut-bolt, bus-bar & washer must be replaced with new one. | Corrected | Apr 15 2023 | On 24/01/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Panel body is not connected to earth. Earthing bar installed on insulator. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Corrected | Feb 29 2024 | On 09/05/2024: Not Corrected. Earth lead conductor size is inadequate for few panels. On 01/07/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Inadequate working space around transformer for performing maintenance work. | Adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. Access needs to be restricted to qualified personnel wearing appropriate PPE (Personal Protective Equipment). | We have made as-built layout plan for transformer room. We will check with RSC engineer then it will be completed. | Sep 14 2025 | On 16/09/2025: Not corrected. No progress has been observed. The factory needs to submit the as-built and proposed layout plan to RSC for review. RPO Comments on 04 Mar 2026- The factory must complete the remediation work as per given recommendation. As per factory action plan, the remediation work is ongoing. Please contact the RPO if meeting is required to get technical assistance from RSC Engineers. | 4 Months | In Progress
Follow Up Inspection |  | 47 | New Finding: Transformer oil test (dielectric strength test) report is unavailable. | Testing of transformer oil, specifically the dielectric strength test needs to be conducted at least once in a year from government-authorized entities such as BPDB, BREB, PGCB, EGCB, DESCO, DPDC, or any other designated govt. authority. This ensures adherence to an unaltered, verifiable, standardized format, thereby maintaining the integrity and reliability of the transformer's insulation system. | We will appaly for transformer Oill test within 10/03/2026. | Oct 16 2025 | RPO Comments on 04 Mar 2026- The factory must complete the remediation work as per given recommendation. As per factory action plan, the remediation work is ongoing. Please contact the RPO if meeting is required to get technical assistance from RSC Engineers. | 1 Month | In Progress