## Structural
Date
08-Nov-2025 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | FUTURE CLOTHING LTD., DURGAPUR, MONDOLBARI, ZIRABO, ASHULIA, SAVAR, DHAKA, Dhaka, Dhaka
Date of Inspection |  | 2022-07-18
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Absence of design documents and as-built drawing (Building-01: Office Building) | Factory engineer is required to be prepare a design report in compliance with section 1.9.1.1 (part-6, BNBC). | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 2 | Absence of design documents and as-built drawing (Building-01: Office Building) | Factory engineer is required to be prepare a set of as-built drawing in compliance with section 1.9.1.2 (part-6, BNBC). | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. On 22-Jul-2025: As part last review comment, factory needs to submit the revised as-built drawings as part of design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 3 | Absence of design documents and as-built drawing (Building-01: Office Building) | Implement remediation work if required. | After revised EA, if any remediation require then the work will be done accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 4 | Falling Hazard at roof level and stair area (Building-01: Office Building) | Factory is required to provide parapet/railing at all locations of roof and staircase to avoid possible falling hazard. | The building is under construction prohibited upward & downward movement to this building for all. We have closed the stair also. | Sep 14 2022 | On 27-Feb-2023: Factory was required to provide parapet/railing at all locations of the roof and staircase to avoid possible falling hazards. During verification inspection, the entrance of the staircase was found sealed. Whenever the factory will open the entrance, the factory will be required to provide parapet/railing at all locations of the roof and staircase to avoid the possible falling hazard. On 22-Jul-2025: Corrected previously. During inspection, the entrance o the stair was found sealed. | 6 weeks | Corrected
Initial Inspection |  | 5 | Exposed reinforcement left at roof level (Building-01: Office Building) | Factory is required to provide rust proof paint on exposed reinforcement to protect from corrosion. | Anti corrosion paint work is done. | Sep 14 2022 | On 27-Feb-2023: During verification inspection rust proof paint was found on exposed reinforcement. On 22-Jul-2025: Corrected previously. | 6 weeks | Corrected
Initial Inspection |  | 6 | Crack on brick wall (Building-02: Guard Room) | Factory engineer is required to investigate the reason of crack and repair with a suitable method. | We are taking steps accordingly. | Sep 14 2022 | On 27-Feb-2023: The factory has submitted the crack investigation report along with EA report to RSC, which is now under review. Factory need to complete the remediation work as per accepted Crack investigation report from RSC. On 22-Jul-2025: Factory is currently no using Building 2. As part last review comment, factory needs to submit crack investigation report to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 7 | Absence of design documents (Shed-01: Sewing) | Factory engineer is required to be prepare a design report in compliance with section 1.9.1.1 (part-6, BNBC). | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory has prepared design report and submitted it to the RSC which is currently under review process. However, during this verification inspection, few discrepancies were observed in between the submitted as-built drawing and the on-site condition. Detailed comments on discrepancies will be shared with the factory along with review comments on the submitted design report. The factory will be required to revised the design report and drawing based on the requirements of review comments. On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 8 | Absence of design documents (Shed-01: Sewing) | Implement remediation work if required. | After EA, will be done the work accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory has prepared design report and submitted it to the RSC which is currently under review process. However, during this verification inspection, few discrepancies were observed in between the submitted as-built drawing and the on-site condition. Detailed comments on discrepancies will be shared with the factory along with review comments on the submitted design report. The factory will be required to revised the design report and drawing based on the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 9 | Discrepancy and missing information as-built drawing (Shed-01: Sewing) | Factory engineer is required to be prepare a set of as-built drawing in compliance with section 1.9.1.2 (part-6, BNBC). | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory has prepared design report and submitted it to the RSC which is currently under review process. However, during this verification inspection, few discrepancies were observed in between the submitted as-built drawing and the on-site condition. Detailed comments on discrepancies will be shared with the factory along with review comments on the submitted design report. The factory will be required to revised the design report and drawing based on the requirements of review comments. On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 10 | Non-structural elements found unbraced/not anchored (Shed-01: Sewing) | Factory is required to brace/anchor all non-structural elements. | Relevant work is processing. | Feb 3 2023 | On 27-Feb-2023: Factory did not take any initiative regarding this issue. The non-structural elements were found not anchored. Factory is required to brace/anchor the non structural elements properly. On 22-Jul-2025: Factory has anchored all non structural elements. | 6 months | Corrected
Initial Inspection |  | 11 | Absence of design documents (Shed-03: Finishing) | Factory engineer is required to be prepare a design report in compliance with section 1.9.1.1 (part-6, BNBC). | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory has prepared design report and submitted it to the RSC which is currently under review process. However, during this verification inspection, few discrepancies were observed in between the submitted as-built drawing and the on-site condition. Detailed comments on discrepancies will be shared with the factory along with review comments on the submitted design report. The factory will be required to revised the design report and drawing based on the requirements of review comments. On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 12 | Absence of design documents (Shed-03: Finishing) | Implement remediation work if required. | We have submitted the document for your review based on your review comments and guidelines. | Feb 3 2023 | On 27-Feb-2023: The factory has prepared design report and submitted it to the RSC which is currently under review process. However, during this verification inspection, few discrepancies were observed in between the submitted as-built drawing and the on-site condition. Detailed comments on discrepancies will be shared with the factory along with review comments on the submitted design report. The factory will be required to revised the design report and drawing based on the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 13 | Absence of design documents (Shed-04: Wash Sent & Receive) | Factory engineer is required to be prepare a design report in compliance with section 1.9.1.1 (part-6, BNBC). | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 14 | Absence of design documents (Shed-04: Wash Sent & Receive) | Implement remediation work if required. | After EA, if any remediation require then the work will be done accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 15 | Apparently lack of lateral stability (Shed-05: Medical-Daycare) | Factory engineer is required to check the lateral stability of the shed. | After EA, if any remediation require then the work will be done accordingly. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 16 | Apparently lack of lateral stability (Shed-05: Medical-Daycare) | Implement remediation work if required. | After EA, if any remediation require then the work will be done accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 17 | Corrosion on steel members (Shed-05: Medical-Daycare) | Factory is required to identify the locations and apply rust proof paint on steel members to prevent corrosion. | Work is done. | Sep 14 2022 | On 27-Feb-2023:The factory has identified the location and applied rust proof paint on steel member. On 22-Jul-2025: Corrected previously. | 6 weeks | Corrected
Initial Inspection |  | 18 | Apparently lack of lateral stability (Shed-06: Utility) | Factory engineer is required to check the lateral stability of the shed. | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 19 | Apparently lack of lateral stability (Shed-06: Utility) | Implement remediation work if required. | After EA, if any remediation require then the work will be done accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory has prepared design report and submitted to RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 20 | Absence of design documents (Shed-06: Utility) | Factory engineer is required to be prepare a design report in compliance with section 1.9.1.1 (part-6, BNBC). | After EA, if any remediation require then the work will be done accordingly. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 21 | Absence of design documents (Shed-06: Utility) | Implement remediation work if required. | After EA, if any remediation require then the work will be done accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 22 | Crack on brick wall (Shed-06: Utility) | Factory engineer is required to investigate the reason of crack and repair with a suitable method. | We have already engaged a third party for this work. | Sep 14 2022 | On 27-Feb-2023: During inspection it was found that at few locations cracks were repaired but still in few locations there were cracks. The factory is required to prepare the crack investigation report incorporating the actual reason of cause & suggest proper remedial measures and repair the cracks accordingly. On 22-Jul-2025: Factory has repaired the cracks and no visible cracks were observed. | 6 weeks | Corrected
Initial Inspection |  | 23 | Loose bracing (Shed-06: Utility) | Factory is required to identify the locations and tighten all the bracings accordingly. | Work is done. | Sep 14 2022 | On 27-Feb-2023: During inspection it was found that the factory has tightened all the loose bracings. On 22-Jul-2025: Factory has tightened all the loose bracings. | 6 weeks | Corrected
Initial Inspection |  | 24 | Absence of as-built drawings and apparently inadequate connection (Shed-07: Compressor Room) | Factory engineer is required to prepare full set of as-built drawing as per 1.9.1.2 (BNBC) | After EA, if any remediation require then the work will be done accordingly. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 25 | Absence of as-built drawings and apparently inadequate connection (Shed-07: Compressor Room) | Factory engineer is required to check the connection adequacy for uplift forces as a part of EA and implement remediation work where required. | After EA, if any remediation require then the work will be done accordingly. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 26 | Absence of as-built drawings and apparently inadequate connection (Shed-07: Compressor Room) | Implement remediation work if required. | After EA, if any remediation require then the work will be done accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 27 | Absence of as-built drawings and apparently inadequate connection (Shed-08: Inspection Room) | Factory engineer is required to prepare full set of as-built drawing as per 1.9.1.2 (BNBC) | After EA, if any remediation require then the work will be done accordingly. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 28 | Absence of as-built drawings and apparently inadequate connection (Shed-08: Inspection Room) | Factory engineer is required to check the connection adequacy for uplift forces as a part of EA and implement remediation work where required. | After EA, if any remediation require then the work will be done accordingly. | Sep 14 2022 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments. Also, factory is required to implement the remedial works (if any) as per the recommendation of the design report (after accepted by the RSC). On 22-Jul-2025: As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 29 | Absence of as-built drawings and apparently inadequate connection (Shed-08: Inspection Room) | Implement remediation work if required. | After EA, if any remediation require then the work will be done accordingly. | Feb 3 2023 | On 27-Feb-2023: The factory prepared design report and submitted it to the RSC for review. During this verification inspection, few discrepancies were observed between the as-built drawing and the on-site condition. Detailed comments on discrepancies will be provided to the factory along with review comments against the design report. The factory will be required to address the requirements of review comments On 22-Jul-2025: After the EA acceptance, factory needs to complete all the remediation works if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 months | In Progress
Initial Inspection |  | 30 | Lack of as-built drawing (Shed-09: Prayer Room) | Factory engineer is required to prepare full set of as-built drawing as per 1.9.1.2 (BNBC) | We have submitted the document for your review based on your review comments and guidelines. | Sep 14 2022 | On 27-Feb-2023: The factory has prepared the as-built drawings, but no connection details of the member has been found. The factory is required to prepare an as-built drawing showing all the connection details. On 22-Jul-2025: As part last review comment, factory needs to submit the revised as-built drawings as part of design documents to RSC within 15 Sep 2025. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Initial Inspection |  | 31 | Crack on brick wall (Shed-11: Toilet -2 & Shed-12: Toilet -2) | Engage a Consultant immediately to provide adequate restraint to the cracked external masonry. | We have done dismantled the cracked wall. | Aug 9 2022 | On 27-Feb-2023: Factory has demolished the Shed-11: Toilet-2 along with the cracked wall. But during inspection the cracks on the wall of Shed-12: Toilet-3 were observed. However, after the inspection, factory has demolished the cracked wall of shed-12 and sent pictorial evidence to RSC. On 22-Jul-2025: Corrected previously. Factory has demolished the cracked wall of shed-11 and 12 and no visible cracks were observed. | (Immediate - Now) | Corrected
Initial Inspection |  | 32 | Crack on brick wall (Shed-11: Toilet -2 & Shed-12: Toilet -2) | Provide adequate support for the roof shed. | We have done dismantled the cracked wall. | Aug 9 2022 | On 27-Feb-2023: Factory has demolished the Shed-11: Toilet-2 along with the cracked wall. But during inspection the cracks on the wall of Shed-12: Toilet-3 were observed. However, after the inspection, factory has demolished the cracked wall of shed-12 and sent pictorial evidence to RSC. On 22-Jul-2025: Corrected previously. Factory has demolished the cracked wall of shed-11 and 12 and no visible cracks were observed. | (Immediate - Now) | Corrected
Initial Inspection |  | 33 | Crack on brick wall (Shed-11: Toilet -2 & Shed-12: Toilet -2) | The factory must immediately engage a consultant to investigate the wall cracks, develop a remediation plan and submit to RSC for review. | We have done dismantled the cracked wall. | Aug 9 2022 | On 27-Feb-2023: Factory has demolished the Shed-11: Toilet-2 along with the cracked wall. But during inspection the cracks on the wall of Shed-12: Toilet-3 were observed. However, after the inspection, factory has demolished the cracked wall of shed-12 and sent pictorial evidence to RSC. On 22-Jul-2025: Corrected previously. Factory has demolished the cracked wall of shed-11 and 12 and no visible cracks were observed. | (Immediate - Now) | Corrected
Initial Inspection |  | 34 | Crack on brick wall (Shed-11: Toilet -2 & Shed-12: Toilet -2) | Complete remediation work as per investigation report. | We have done dismantled the cracked wall. | Sep 14 2022 | On 27-Feb-2023: Factory has demolished the Shed-11: Toilet-2 along with the cracked wall. But during inspection the cracks on the wall of Shed-12: Toilet-3 were observed. However, after the inspection, factory has demolished the cracked wall of shed-12 and sent pictorial evidence to RSC. On 22-Jul-2025: Corrected previously. Factory has demolished the cracked wall of shed-11 and 12 and no visible cracks were observed. | 6 weeks | Corrected
Follow Up Inspection |  | 35 | New findings 1: Distorted steel columns of Shed 03 (Finishing) | Factory engineer is required investigate the reason of the distortion of the column flange and check the adequacy of the distorted columns. | We are taking steps accordingly. | Apr 25 2023 | On 27-Feb-2023: During the inspection distorted flange was observed in several locations of Shed 3. Factory engineer is required investigate the reason of the distortion of the column flange and check the adequacy of the distorted columns. On 22-Jul-2025: This issue is required to cover under EA. As part last review comment, factory needs to submit the revised design documents to RSC within 15 Sep 2025. During inspection, distorted flange was still observed in several locations of Shed 3. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress
Follow Up Inspection |  | 36 | New findings 2: Distorted steel columns of Shed 03 (Finishing) | Implement remediation according to the recommendation of the investigation report. | We are taking steps accordingly. | Apr 25 2023 | On 27-Feb-2023: During the inspection distorted flange was observed in several locations of Shed 3. Factory engineer is required investigate the reason of the distortion of the column flange and Implement remediation according to the recommendation of the investigation report. On 22-Jul-2025: The factory is required to complete the remedial works after getting acceptance from RSC if required. RPO Comments on 14-Sep-2025: Factory got time extension to submit the document till 30 Sep 2025. | 6 weeks | In Progress

## Fire
Date
08-Nov-2025 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | FUTURE CLOTHING LTD., DURGAPUR, MONDOLBARI, ZIRABO, ASHULIA, SAVAR, DHAKA, Dhaka, Dhaka
Date of Inspection |  | 2022-07-18
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Transformer and generator room are not properly separated from each others by fire rated construction. Location: Utility Shed-6. | Separate the transformer and generator room by a minimum 2-hr fire rated constructions. Seal and/or protect all opening to maintain the required fire separation. Provide proper ventilation system with consult a qualified engineer. Follow the RSC Technical Guidelines (Standard)-3.4.2.1 | Done | Nov 30 2022 | On 26-Nov-24: Separation is provided between generator and the transformer. | Within 3 months | Corrected
Initial Inspection |  | 2 | The Sheds have been found steel composite type and the steel columns and girders has been found in exposed condition without any fire protection. Location : Shed-1 and Shed-3 | Construction of interim non-high-rise factories containing G and/or H2 occupancies(factories) shall be Type 1 or Type 2 construction as required in BNBC 2006 Part 3 Table 3.2.4.The fire resistance of structural members for interim and existing building shall be in compliance with BNBC 2006 Part 3 Chapter 3 and Table 3.3.1. Chemical store shed shall be type-1 construction. Provide required fire rating on the structural elements by following Table-3.2.4, 3.1.9 & Table 4.4.1 of the RSC Technical Guidelines (Standard) or Table 3.3.1 of BNBC-2006. Consult a qualified fire protection engineer to design the rated construction barriers in between two floors and in structural members. | We are working on it. | Feb 28 2023 | On 26-Nov-24: No significant progress has been observed. The remediation is required to be performed according to BNBC 2020, Part 1, Chapter 1, Section 4. Fire resistance rating of the exterior wall is required to be ensured according to BNBC 2020 Table 3.3.1 (a). Factory is required to submit proposed remediation plan to the RSC for review. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 6 months | In Progress
Initial Inspection |  | 3 | Storage rooms are not properly separated by fire rated construction. Location: Shed-1 and Shed-3 ( non-rated door) | Provide dedicated storage rooms separated by minimum 1-hr fire rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23 m² - If sprinkler protected: maximum height of 3.66m and maximum area of 93 m² Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | As per your guidelines, we will separate the dedicated storage room by a minimum 1-hour fire rated door. Hopefully it will be complete very soon. | Nov 30 2022 | On 26-Nov-24: Stores are not properly separated at the shed 1 and shed 3 due to non rated door and unprotected opening. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 4 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location: Shed?3 | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | We have already removed all combustible materials that were exposed in the surrounding area. | Sep 30 2022 | On 26-Nov-24: In-process goods are not kept maintaining the recommendation at shed 01 and 03. RPO Comments: On 06-Mar-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 months | Pending Verification
Initial Inspection |  | 5 | The exit discharge path is less than 10 ft. wide and is not separated from the building interior from Shed-1 at exit-5 and Shed-3 at exit-3. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way (only include this if feasible) | We have a plan to separate the exit route. Hope it will be complete very soon. | Feb 28 2023 | On 26-Nov-24: The exit 5 at shed 1 and the exit 3 at shed 3 are not protected from the building interior. RPO Comments: On 10-JUN-2025: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 6 months | Pending Verification
Initial Inspection |  | 6 | Occupant load sign was not present in the exits. | Provide present occupant load sign in every floors. | Based on your drawings and design review comments, we will recruit a consulate for an addressable fire detection system listed in accordance with NFPA 72 very soon. | Sep 30 2022 | On 26-Nov-24: Provided. | Within 1 months | Corrected
Initial Inspection |  | 7 | The fire detection system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire detection system with a new, listed addressable fire detection system in accordance with NFPA 72. | Based on your drawings and design review comments, we will recruit a consulate for an addressable fire detection system listed in accordance with NFPA 72 very soon. | Feb 28 2023 | On 26-Nov-24: Review drawing by the RSC has been received by the factory. The factory is required to start the installation work according to the review drawing. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | Design within 3 months and installation with 6 months | In Progress
Initial Inspection |  | 8 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with The RSC Technical Guidelines (Standard). | Based on your drawings and design review comments, we will recruit a consulate for an addressable fire detection system listed in accordance with NFPA 72 very soon | Feb 28 2023 | On 26-Nov-24: It is an integrated part of the fire detection and alarm system. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 9 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10 ,and in accordance with The RSC Technical Guidelines (Standard). | Done | Nov 30 2022 | On 26-Nov-24: Inspection test record is found adequate for the fire extinguisher system. | Within 3 months | Corrected
Initial Inspection |  | 10 | Directional signs are not provided where direction of the path of travel to an exit has changed. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | Done | Nov 30 2022 | On 26-Nov-24: Directional signs were Provided. | Within 3 months | Corrected
Initial Inspection |  | 11 | Exit signage not illuminated/missing (burned out, broken, etc.). Locations: Shed-4 and Shed-8 | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs | Done | Sep 30 2022 | On 26-Nov-24: Exit signage is provided. | Within 1 months | Corrected
Initial Inspection |  | 12 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location-Shed-1 and Shed-3. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Done | Nov 30 2022 | On 26-Nov-24: Adequate illumination is provided at the shed 1 and shed 03. | Within 3 months | Corrected
Initial Inspection |  | 13 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The RSC Technical Guidelines (Standard) | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The RSC Technical Guidelines (Standard). Keep written records on-site. | Done | Nov 30 2022 | On 26-Nov-24: Provided. | Within 3 months | Corrected
Follow Up Inspection |  | 14 | New Finding (1st Follow Up): The dining area (occupant is 295) is not separated from accessories store and finishing section by fire rated construction. Location: Shed 3 (Packing, Finishing, Dining & Finished Goods) | Separate the dedicated storage room (H2) and Finishing section (G2) by a minimum 3-hr fire-rated construction from dining (E4). It is necessary to limit the occupant load to 300 or below. Provide 3 hr. fire rated door and seal all penetrations and openings by 3 hr. fire rated fire rated barrier construction. Additionally, ensure that there are required safe and direct exits available for the dining facilities, or consider relocating them to a dedicated building. | As per your guidelines, we will Separate the dedicated storage room (H2) and Finishing section (G2) by a minimum 3-hr fire-rated construction from dining E4).Hopefully it will be complete very soon. | Mar 12 2025 | On 26-Nov-24: New Finding RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress

## Electrical
Date
08-Nov-2025 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | FUTURE CLOTHING LTD., DURGAPUR, MONDOLBARI, ZIRABO, ASHULIA, SAVAR, DHAKA, Dhaka, Dhaka
Date of Inspection |  | 2022-07-18
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | In Progress | Nov 30 2022 | On 06/03/2024: Not Corrected. SLD reviewed on 18th-July 2023, factory is working on filed as per reviewed SLD. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/10/2025: Not Corrected. No significant progress has been observed. Mismatches were found between the accepted SLD and the actual installation, including load identification, oversized breaker, earthing layout, and busbar/cable information. | 3 MONTHS | In Progress
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed. | Factory must design Lightning Protection System (LPS) for the whole factory (where the Risk index is more than 40). Once a LPS is designed properly, installation must be done accordingly. | In Progress | Nov 30 2022 | On 06/03/2024: Not Corrected. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/10/2025: Not Corrected. No progress has been observed. | 3 MONTHS | In Progress
Initial Inspection |  | 3 | Insulation resistance test of electrical power cables is not performed. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | We have already completed the insulation resistance test. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 4 | Earth Pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made, and the result shall be kept for not less than two years and shall be available to the Inspector when required. | In Progress | Oct 31 2022 | On 06/03/2024: Not Corrected. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/10/2025: Not Corrected. The test report mismatches with field information. | 2 MONTHS | In Progress
Initial Inspection |  | 5 | Thermography scanning report is unavailable. RECOMMENDATION: Thermography survey must be done and recorded at least twice in a year. | Thermography survey must be done and recorded at least twice in a year. | We have already completed the thermography scanning on 19 September 2022. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 6 | Transformer Oil Test (dielectric strength test) report is unavailable. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Done | Sep 30 2022 | On 06/03/2024: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 7 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). |  | Sep 30 2022 | On 06/03/2024: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 8 | Electric safety training program has not initiated/conducted. | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory should continue to improve overall electrical safety situation for the staffs. |  | Sep 30 2022 | On 06/03/2024: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 9 | No policies for PPE & LOTO (Lock-Out-Tag Out) are introduced for safety of the personnel during any kind of the personnel during any kind of maintenance work. | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 10 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. | We have already hung CPR guidelines near all electrical LT panels, MDB, FDB, DB, SDB. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 11 | Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | In Progress | Nov 30 2022 | On 06/03/2024: Not Corrected. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/10/2025: Not Corrected. No progress has been observed. | 3 MONTHS | In Progress
Initial Inspection |  | 12 | Transformer earthing (equipment earthing) cable size is inadequate. | Equipment earthing cable size must be increased. The earth cable size shall be determined according to BNBC or Adiabatic method (if possible). Number of earth pits shall be determined by the size of connected earth cable. | In Progress | Oct 31 2022 | On 06/03/2024: Not Corrected. Still inadequate. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/10/2025: Not Corrected. No progress has been observed. | 2 MONTHS | In Progress
Initial Inspection |  | 13 | Transformer Breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil mark on the cup. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 14 | Oil level in transformer conservator oil tank is below minimum level. | Minimum oil level in transformer conservator oil tank must be maintained, and it shall be checked periodically. | Done | Nov 30 2022 | On 06/03/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 15 | Equipment earth cable (for generator) size is inadequate. | At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. | In Progress | Oct 31 2022 | On 06/03/2024: Not Corrected. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/10/2025: Not Corrected. No progress has been observed. | 2 MONTHS | In Progress
Initial Inspection |  | 16 | Generator terminal box left open to allow cable entry. | Base plate for generator terminal box must be installed and cables entering terminal box must be firmly fixed with cable gland. | We have already completed the generator terminal box work and we used the cable glands. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 17 | Generator output cables (laid on floor) are not protected and supported. | Service cables from generator must be supported at its own breaker's terminal and with cable tray. | We have provided trays and support for cable protection. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 18 | Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped, and rust must be cleaned. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 19 | Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | We have already done identification marking on all distribution boards, and switches will be clearly marked for proper identification after completion of SLD. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 20 | No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. | We have already supplied enough rubber mats of the distribution board. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 21 | Electrical power cables and circuit breakers are not identified properly. | Proper identification shall be done on power cables circuit breakers used in the system according to SLD. | According to SLD, we will try to complete the work very soon. | Oct 31 2022 | RPO Comments on 28-Feb-2024: The corrective action plan should be completed as per the given recommendation with immediate concern. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 22 | Panel base plates are removed to allow cable entry. | Panel base plates must be installed, at all times, and cables entering panel must be firmly fixed with cable gland. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 23 | Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Panel door have already connected with earth. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 24 | Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 25 | Power cables entering or exiting from Distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel must be fixed through panel base/top plate using proper sized cable glands (metal/PVC). | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 26 | MCCBs/MCBs are not installed/adjusted per load demand. | All the MCCBs/MCBs must be installed/adjusted as per connected load current; if adjustment is not possible, replacement will be the only way. | In Progress | Oct 31 2022 | On 06/03/2024: Not Corrected. This issue related to SLD. RPO Comments on 15-Sep-2025: The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/10/2025: Not Corrected. No progress has been observed. | 2 MONTHS | In Progress
Initial Inspection |  | 27 | Earth lead cable/Earth Continuity Conductor size is inadequate/not available. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | The earthing wire size of the equipment will be increased. Earth wire size will be done according to BNBC or Adiabatic method. | Oct 31 2022 | RPO Comments on 28-Feb-2024: The corrective action plan should be completed as per the given recommendation with immediate concern. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 28 | Distribution Board's top/bottom/back cover/front door is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. |  | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 29 | Multiple cables (came from different electrical consumers) terminated at MCCB terminals/Busbar. | Each electrical circuit must be terminated at single MCB/MCCB/busbar terminals. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 30 | Loop connection has been used powering multiple circuits through MCB/MCCBs. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity). | According to SLD, we will try to complete the work very soon. | Oct 31 2022 | RPO Comments on 28-Feb-2024: The corrective action plan should be completed as per the given recommendation with immediate concern. On 06/03/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 31 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 32 | Cable connected to busbar/MCCB/MCB terminal without cable lug. | Each electrical circuit must be terminated at single busbar/MCB/MCCB terminal using cable proper sized cable lug (where applicable). | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 33 | Circuit is drawn from bus bar without any protective means. | Each electrical circuit must be drawn from distribution board busbar using a proper type of protection arrangement (MCCB/MCB). | We have used proper type of protection for MCCB/MCB. | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 34 | Nonrated and non-certified comb bar used for powering multiple MCB. | For connecting multiple MCB use rated and listed comb bar. | According to SLD, we will try to complete the work very soon. | Oct 31 2022 | RPO Comments on 28-Feb-2024: The corrective action plan should be completed as per the given recommendation with immediate concern. On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 35 | Burnt sign visible at connector terminals. | Check the connections and circuit breaker. Find out the exact reason of burning. If required, replace the burned terminal. Assign an engineer to take necessary action depending on the problem. | It has been checked and done. There is now burn sign | Sep 30 2022 | On 06/03/2024: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 36 | MCB is installed without any enclosure. | Each MCCB/MCB must be enclosed by proper type material. the material must not be more than 18 SWG graded. | Done | Sep 30 2022 | On 06/03/2024: Corrected. Remediation of this issue have done not Found during inspection. | 1 MONTHS | Corrected
Initial Inspection |  | 37 | Unterminated and exposed live wire is kept inside the electrical panel/floor. | All the unterminated live power cables must be removed as soon as possible. | Done | Sep 30 2022 | On 06/03/2024: Corrected. Remediation of this issue have done not Found during inspection. | 1 MONTHS | Corrected
Initial Inspection |  | 38 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Done | Oct 31 2022 | On 06/03/2024: Corrected. Remediation of this issue have done not Found during inspection. | 2 MONTHS | Corrected
Initial Inspection |  | 39 | Non-metallic sheathed (Types NM, NMC, and NMS) cable is run exposed within suspended ceiling, and Suspended ceiling has been used for cable support. | Use metallic sheathed cable or provide enclosed cable raceway to run cable over suspended ceiling. | Done | Oct 31 2022 | On 06/03/2024: Corrected. Remediation of this issue have done not Found during inspection. | 2 MONTHS | Corrected
Initial Inspection |  | 40 | Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 41 | Wiring or extensions to connect equipment/ devices are laid on floors unprotected. | The cable connection to machines/equipment may be run under the checkered plates (existing) and in trenches or rigid conduits/ cable trays and supports to protect from external damages. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 42 | Cables are laid on floor inside cable trench haphazardly. | Cables inside cable trench must be guided and routed properly. A cable tray shall be installed in the trench to ensure proper support and dressing for cables. | Done | Nov 30 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 43 | BBT plug point left open. | Unused BBT plug point must be sealed/covered by BBT plug cap or by insulating material. | Done | Sep 30 2022 | On 06/03/2024: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 44 | Tap Off Boxes (TOB) has openings (typical issue). | Each Tap Off Boxes (TOB) must be properly sealed to avoid ingression of fluffs. Gland shall be used, where required. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 45 | Power socket is kept on floor unsafely. | Power socket shall be installed at minimum 200mm above the floor with a rigid support. | Done | Oct 31 2022 | On 06/03/2024: Corrected. Removed from mentioned location. | 2 MONTHS | Corrected
Initial Inspection |  | 46 | Hazardous lights in storeroom / storage areas are uncovered. | Hazardous lights in storeroom /storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 47 | Uncovered/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 48 | Cable directly connected with motor coil without terminal box. | Cable must be connected through motor terminal box as manufacturer guideline. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 49 | Electrical devices (pump motor) are not fixed at base. | All electrical components must be fixed at base with proper arrangement. | We have already fixed the proper arrangement and foundation of electrical equipment (pump motor). | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 50 | Electrical installations (motor, boiler, compressor, cable channel, etc.) has no earth connection. | All electrical installations shall have proper earth connection. Cable selection shall be made per CB response and circuit's power demand. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 51 | Compressor machine mounted on wheel & is not locked. | Compressor machine mounted on wheel must be anchored or the wheels must be locked to prevent from trolling. | Done | Oct 31 2022 | On 06/03/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 52 | Earth pits are not identifiable. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Done | Nov 30 2022 | On 06/03/2024: Corrected. | 3 MONTHS | Corrected
Follow Up Inspection |  | 53 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be accurately reflected in the record. Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years and documented. This testing may require power shutdown to ensure accurate results and safety. | In Progress | Nov 26 2025 |  | 1 Month | In Progress
Follow Up Inspection |  | 54 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. | In Progress | Nov 26 2025 |  | 1 Month | In Progress
Follow Up Inspection |  | 55 | New Finding: Hot spots have been observed at some points. | Hot spots throughout the entire electrical system must be eliminated to ensure safety and prevent potential equipment failures or hazards and reduce downtime and repair costs. | In Progress | Nov 26 2025 |  | 1 Month | In Progress
Follow Up Inspection |  | 56 | New Finding: Panel body is not connected to earth. Earthing bar installed on insulator. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | In Progress | Nov 26 2025 |  | 1 Month | In Progress
Follow Up Inspection |  | 57 | New Finding: Wiring or extensions connecting equipment/ devices are laid on floors without protection, using flexible PVC. | Run the cable connections to machines/equipment through trenches covered with checkered plates or within rigid conduits/cable trays and supports to prevent external damage. | In Progress | Nov 26 2025 |  | 1 Month | In Progress
Follow Up Inspection |  | 58 | New Finding: Uncovered/perforated type cable tray used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | In Progress | Nov 26 2025 |  | 1 Month | In Progress
Follow Up Inspection |  | 59 | New Finding: Combustible/flammable materials are attached with BBT/cable channel/duct. | All flammable and combustible materials, including water bottles and other items, must be cleared from electrical cable channels, ducts, and BBTs. Separate storage arrangements for these materials should be implemented. | In Progress | Nov 26 2025 |  | 1 Month | In Progress