## Structural
Date
16-Sep-2025 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Gardenia Wears Ltd, 310/668, SITPARA, BORMI, SREEPUR, Gazipur
Date of Inspection |  | 2018-09-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Bolt missing and existence of gap in joints | Factory Engineer to survey the whole structure to identify locations of all missing bolts and install them. | There is no bolt missing of gap joint. And issue closed. | Nov 21 2018 | On 17-July-2019: Factory management has installed those missing bolts. During inspection bolts were not found missing in joints.. On 13-Jan-2021: Corrected from previous follow up inspection of Accord. During inspection bolts were not found missing in joints. On 02-Jan-2022: This issue was corrected from previous inspection. During inspection no bolts were found missing in joints. On 16-Nov-2023: This issue was corrected from previous inspection. On 23-May-2024: Corrected previously. During inspection, no bolts were found missing. | 6 Weeks | Corrected
Initial Inspection |  | 2 | Bolt missing and existence of gap in joints | Factory Engineer to survey the whole structure to locate the gap in joints and and take suitable measures. | There is no bolt missing of gap joint. And issue closed. | Nov 21 2018 | On 17-July-2019: Factory management has installed those missing bolts. Shim plate has been provided to reduce gap in joints On 13-Jan-2021: Corrected from previous follow up inspection of Accord. Gaps were not found in steel joints. Shim plate had been provided in steel plate joints On 02-Jan-2022: This issue was corrected from previous inspection. During inspection no connection gaps were observed. On 16-Nov-2023: This issue was corrected from previous inspection. On 23-May-2024: Corrected previously. However, during inspection total deck slab thickness was found 125 mm, and rib height was found 50 mm (without finishes). | 6 Weeks | Corrected
Initial Inspection |  | 3 | Corrosion in Steel member. | Apply suitable method to protect the steel members from corrison. | Every corrosion in steel member has removed. And issue closed.. | Nov 21 2018 | On 17-July-2019: Factory management has provided paint to remove corrosion from steel members. During inspection corrosion was not found. On 13-Jan-2021: Corrected from previous follow up inspection of Accord. Corrosion was not found in steel members. Factory management is required to keep monitoring regarding this issue. On 02-Jan-2022: This issue was corrected from previous inspection. During inspection no corrosion was observed on steel members. On 16-Nov-2023: This issue was corrected from previous inspection. Factory has applied anticorrosive paint and no corrosion was observed during inspection. On 23-May-2024: Corrected previously. During the inspection, no corrosion was found in steel members. | 6 Weeks | Corrected
Initial Inspection |  | 4 | Mismatch in rafter size. | Engage an Engineer to produce “as constructed” drawings which reflect the actual site dimensions with complete structural information. | Completed. EA report Approved by R.S.C on 3-Dec-2020. Retrofitting Job Done as per EA Report & Declared Timeline (Pictorial Evidence Attached). | Nov 21 2018 | On 17-July-2019: This issue is required to be covered in EA report. Factory management has submitted EA report to ACCORD on 17-July-2019 which is in under review. On 13-Jan-2021: As built drawings were prepared as a part of EA report. Factory management got EA acceptance from RSC on 03-December-2020. During inspection any major mismatches were not found. On 02-Jan-2022: This issue was corrected from previous inspection. During inspection no discrepancies was observed between existing condition & accepted drawings, On 16-Nov-2023: This issue was corrected from previous inspection. A set of as built drawings were produced as part of EA for Facility Building which was accepted by RSC on 03-Dec-2020. During inspection, as built drawings were available on site and found satisfactory. On 23-May-2024: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 5 | Missing bolts, Gap between rafter-column joints, improper Bracing connections, and lack of bracing details. | Factory Engineer to survey the whole structure to identify locations of all missing bolts and install them. | Every Missing bolts, Gap between rafter-column joints, improper Bracing connections, and lack of bracing are corrected. And issue closed. | Nov 21 2018 | On 17-July-2019: Factory management has installed those missing bolts. During inspection bolts were not found missing in joints. On 13-Jan-2021: Corrected from previous follow up inspection of Accord. During inspection bolts were found as per the accepted as-built drawing. On 02-Jan-2022: This issue was corrected from previous inspection. On 16-Nov-2023: This issue was corrected from previous inspection. During inspection no missing bolts were observed in Facility Building and Warehouse Building. On 23-May-2024: Corrected previously. During inspection, no bolts were found missing. | 6 Weeks | Corrected
Initial Inspection |  | 6 | Missing bolts, Gap between rafter-column joints, improper Bracing connections, and lack of bracing details. | Factory Engineer to survey the whole structure to locate the gap in joints and take suitable measures. | Every Missing bolts, Gap between rafter-column joints, improper Bracing connections, and lack of bracing are corrected. And issue closed. | Nov 21 2018 | On 17-July-2019: Factory management has installed those missing bolts. Shim plate has been provided to reduce gap in joints On 13-Jan-2021: Corrected from previous follow up inspection of Accord. Gaps were not found in steel joints. Shim plate had been provided in steel plate joints. On 02-Jan-2022: This issue was corrected from previous inspection. On 16-Nov-2023: This issue was corrected from previous inspection. During inspection no gap in connection was observed in Facility Building and Warehouse Building. On 23-May-2024: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 7 | Missing bolts, Gap between rafter-column joints, improper Bracing connections, and lack of bracing details. | Factory engineer to check the adequacy of bracing connections and update as- build grawings included bracing details. | Completed. EA report Approved by R.S.C on 3-Dec-2020. Retrofitting Job Done as per EA Report & Declared Timeline (Pictorial Evidence Attached). | Nov 21 2018 | On 17-July-2019: This issue is required to be covered in EA report. Factory management has submitted EA report to ACCORD on 17-July-2019 which is in under review. On 13-Jan-2021: As built drawings including bracing details were prepared as a part of EA report. Factory management got EA acceptance from RSC on 03-December-2020. During inspection any major mismatches were not found. On 02-Jan-2022: This issue was corrected from previous inspection. During inspection no discrepancies was observed between existing condition & accepted drawings, On 16-Nov-2023: This issue was corrected from previous inspection. As-built drawings were produced as part of EA. EA of the Facility Building and Warehouse Building got acceptance from RSC on 03-Dec-2020. On 23-May-2024: Corrected previously. | 6 Weeks | Corrected
Initial Inspection |  | 8 | Missing bolts, Gap between rafter-column joints, improper Bracing connections, and lack of bracing details. | Factory Engineer to take remedial actions where required. | Completed. factory management had installed those missing bracings and compression struts and send pictorial evidences over mail to RSC on 14-January-2021. Factory Management also asked for Special Inspection on 3rd February'2021 and kept required material test reports and QC certificates onsite. | Apr 10 2019 | On 17-July-2019: This issue is required to be covered in EA report. Factory management has submitted EA report to ACCORD on 17-July-2019 which is in under review. Factory management will go for remedial work after getting acceptance of EA from ACCORD (if recommended). On 13-Jan-2021: Factory management got EA acceptance from RSC on 03-December-2020. As per EA recommendation factory management had to complete all retrofitting works within 20-December-2020. During inspection some bracings and compression struts were not found installed as per accepted retrofitting drawing. Later factory management had installed those missing bracings and compression struts and send pictorial evidences over mail to RSC on 14-January-2021. So, it will be verified in next follow up inspection. Factory management is also required to keep material test reports and QC certificates onsite. On 02-Jan-2022: Factory management got EA acceptance from RSC on 03-December-2020. As per EA recommendation factory management had to complete all retrofitting works within 20-December-2020. During inspection some bracing & compression struts those were not installed in previous inspection has been found installed properly. Test report & QC certificate were also available at site. On 16-Nov-2023: This issue was corrected from previous inspection. As per accepted EA factory has completed remedial works. During inspection, retrofitting completion certificate was available on site. On 23-May-2024: Corrected previously. | 6 Months | Corrected
Follow Up Inspection |  | 9 | New findings 01:Non-engineered light weight shed (Jhut Godown) | Factory is required to replace the non-engineered Shed with engineered structure. | Already the facility has demolished the existing Non-engineered light wastage shed and made a Plan to Make the engineering Shed also Design has been completed. | May 16 2024 | On 16-Nov-2023: During inspection, light weight non-engineered Jhut godown was found beside the Utility Building on the factory premises. Building engineer is required to replace the non-engineered shed with a engineered structure. On 23-May-2024: The factory demolished the non-engineered lightweight shed (Jhut Godown). | (within 6 months) | Corrected

## Fire
Date
16-Sep-2025 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Gardenia Wears Ltd, 310/668, SITPARA, BORMI, SREEPUR, Gazipur
Date of Inspection |  | 2018-09-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Since the structure (2 storied) is steel-composite type and all the RCC panels are resting on the steel columns and girders. Hench, each floor of the building is not separated by a fire resistive rated construction barriers. | Provide fire-resistive rated construction barriers between floors following Section 4.4 and Table 4.4.1 of the Accord Standard or Table 3.3.1 and Table 4.1.1 from BNBC Part 4. Consult a qualified fire protection engineer to design the rated construction barriers. | The facility already covered all the steel columns with gypsum board. complete the works has been completed as per the standards and approval by the RSC. Also, the facility verified floor deck Slab thickness without Tilese 6 inches or 150mm. Work Done | Apr 10 2019 | On 21-Jun-2022: Based on the shared action plan, 1. Sprinkler systems have been installed according to the NFPA 13, NFPA 14, NFPA 20 and NFPA 25 standards with approved T&CVI.- Not verified on 4th FUiN. Point will be verify on Full T&CVI. 2. Building height up to the occupiable roof is limited to 11 meter from road level (Excluding lift machine room).- Verified and height has been found within the limit (9.5 meter). 3. The value of two times the sum of the width of the front road and the front open space is not less than 13.6 m - Verified and value has been found within the limit. 4. All vertical columns (exterior and interior) required to be protected with minimum 1 hour fire resistance rating.- Verified and found that installation has not been completed as per 3rd party listed design and guideline. Factory shall ensure that installation has been done as per UL design, manufacturers published guideline and by listed product. Factory shall keep all required samples and documents onsite for further verification. 5. Exit capacities are sufficient for existing occupants' load.-Verified and the capacity has been found within the limit.6. Shafts (other than exits) and elevator hoist ways if existed, shall be confirmed with 2 hours fire rated separation. Verified and found no shaft on the factory.7. More than 4.5 meter clearance (not below 4.5 meter) from other buildings/ occupancy groups/ assembly areas (except moderate fire risk storage and hazardous buildings i.e. containing chemical hazards) shall be ensured on west, north and east exposure of the said factory building.-Verified and clearance has been found more then 6.09 meter (East). 8. Minimum 1 hour fire resistance rated floor slab needs to be confirmed for this building.-Verified and RCC slab thickness has been found 7 inch (2.5 hour). On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Not Corrected. On-site design found in Box protection but calculation made with profile section. The slab details shown on-site has 5 inch thickness in valley and 3 inch in crest of the deck slab, which do not confirm 1 hr. rating. Additionally Sprinkler system has not been approved yet. On 04-Aug-25: The design philosophy need to be revised and include the Store Shed-1 & Store Shed-2. Gypsum board installation is not as per the design as Corner Beads (item 4) do not match the size and screws (item 6) are not spaced properly. | Within 6 months | In Progress
Initial Inspection |  | 2 | The fire pump room is not provided with adequate fire separation from compressor room. Location: Utility Shed. | Provide fire pump room with 2 hr. rated fire separation when not sprinkle red and 1 hr. rated fire separation when provided with automatic sprinklers in accordance with NFPA 20. Or, Physically separate the pump room from the protected building by a minimum of 50 ft. (15.3 m) in accordance with NFPA 20 | Fire rated Construction at Utility building For Fire Pump Separation is corrected. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected as per previous follow up. On 02/01/2022: Corrected. Separated. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 3 | Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas. Location: Packing store at SE side of ground floor. | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction. | Facility interface fire doors. And issue closed. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Fire rated door has been installed. Interfacing not completed. On 24.10.2019: Corrected. On 13/01/2021: Corrected as per previous follow up. On 02/01/2022: Refer to the issue number 19. On 21-Jun-2022: Refer to the issue number 19. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 4 | The exit stairs are not separated from [work areas, other spaces] on each floor by fire rated construction. SW exit stair discharge the occupant inside the building. Corrugated metal roofing observed. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire rated doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors.If fire rated doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system.Modify stair to discharge directly outside. Or Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). | Fire doors installed with proper interface. And issue closed. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Fire rated door has been installed. Interfacing not completed. On 24.10.2019: Corrected. On 13/01/2021: Corrected as per previous follow up. Note: Factory shall ensure that installed fire door with necessary accessories (door coordinator in double leaf, door closer, panic bar etc.) are working properly. On 02/01/2022: Corrected as per previous follow up. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 5 | Unsealed penetrations and openings are located in the fire rated floor/ceiling assemblies.( 1. Electrical Bus bar riser penetration at north west side of the building 2. Toilet plumbing line penetration at north and south side of the building) | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level.Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | Corrected. Factory asked Inspection on 8th November'2020. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: No action has been taken. On 24.10.2019: Work in progress. On 13/01/2021: Corrected. Sealed. On 02/01/2022: Corrected. Sealed. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 6 | Shutter gates are provided at [building exits, exit stairs, along egress routes, exit discharge]. Location: Bonded warehouse shed. | Replace all collapsible gates/ sliding doors/ rolling shutter doors along the means of egress with side-hinged, swinging egress doors.If locks are required for security reasons, utilize specialized door locking features complying with NFPA101. | At bonded ware house we installed two exits as emergency evacuation. | Nov 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Factory has removed non-compliant doors/gates from egress routes. On 02/01/2022: Corrected. Replaced. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 1 month | Corrected
Initial Inspection |  | 7 | Egress doors/gates with locking features not complying with NFPA101 are provided at [ building exits, exit stairs, along egress routes, exit discharge] | Remove locking features from all egress doors/gates.If locks are required for security reasons, utilize specialized door locking features complying with NFPA101. | All egress door/gates removing locking features. | Dec 10 2018 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Factory has removed non-compliant locking features from egress routes exit doors/gates. On 02/01/2022: Corrected. Removed. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Immediate | Corrected
Initial Inspection |  | 8 | Storage was located under the exit stair and egress path. | Remove storage from the exit stairs and egress path | All storages has been Removed from the exit stairs and egress path. | Nov 19 2018 | On 18/11/2018: During FUI visit, this issue will be verified. On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Removed. On 02/01/2022: Corrected. Removed. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Immediately | Corrected
Initial Inspection |  | 9 | An addressable fire alarm (Only alarm) system was found installed, and does not provide alarm and notification features consistent with acceptable standards. (Building-1, Dining shed, Utility shed and Bonded warehouse, wastage godown.) | Modifiy the system with a new listed addressable fire alarm and detection system in accordance with NFPA 72. Submit the proposed design to ACCORD for review. | The facility has completed the all work, now The facility is fully ready for the next verification. Work Done | Jul 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Installation completed. On 24.10.2019: Installation shall comply NFPA-72. After completing the T&C from contractor's side then factory shall apply for T&C to ACCORD. On 13/01/2021: Pre-T&C has been conducted along with follow-up inspection. The factory has installed sprinkler system in the main production building beside alarm system except smoke, heat, multi & etc. detectors. Sprinkler system shall be installed according to the NFPA 13 & 20. Please see details in Pre-T&C report. On 02/01/2022: Pre-T&C has been conducted along with follow-up inspection. The factory is required again Pre-T&C on site as per pre-T&C report after modification of work, documents, and drawings. Follow the Pre T&C report. On 21-Jun-2022: Installation has been completed and documents are under desk based review. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: The T&C found that the system is not approved. Another on site T&C required. See the detailed T&C report. On 04-Aug-25: T&CVI has been conducted and the system is not approved. Final Verification Inspection required. For details see Final Verification Inspection report. | Design within 10-feb-19, Install within 10-July-19 | Pending Verification
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the fire detection system is not inaccordance with NFPA 72. | Inspect, test and maintain the fire detection system, and keep written records on-site, in accordance with NFPA 72. | In accordance with NFPA 72 every documents update. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Maintaining. On 02/01/2022: Corrected as per previous follow up. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 11 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Facility provided sufficient emergency light on egress. And issue closed. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Not corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. On 02/01/2022: Corrected. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 12 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Keeping written record as per ACCORD standard. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Maintaining. On 02/01/2022: Corrected. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 13 | Manual on-off switch is provided for [emergency lighting / exit signage] units. | Remove manual on/off switches from [emergency lighting /exit signage] units to prevent them from being switched off. | No manual on/off switch with emergency/exit light. And issue closed. | Oct 15 2018 | On 18/11/2018: During FUI visit, this issue will be verified. On 11/04/2019: Not corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Removed. On 02/01/2022: Corrected. Removed. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 1 month | Corrected
Initial Inspection |  | 14 | The width of egress aisles is less than 36-inch. | Provide minimum aisle widths of 36-inch. All the aisles shall be free from any kind of obstruction. | Provided aisles widths of 36 inch. | Jan 10 2019 | On 18/11/2018: CAP has to be completed within the Final Timeline On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Provided. On 02/01/2022: Corrected. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 15 | Parapets or guards are provided in occupied roof which is less than 1067mm (42 inch | Provide parapets or guards with a minimum height of 1067mm (42 inch.). | Provided parapets or guards with a height of 45 inch. Issue solved and pending for verification. | Oct 20 2018 | On 18/11/2018: During FUI visit, this issue will be verified. On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected as per previous follow up. Parapets or guards shall be according to the Accord standard. On 02/01/2022: Corrected as per previous follow up. Parapets or guards shall be according to the Accord standard. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 3 months | Corrected
Initial Inspection |  | 16 | Exit sign not provided at exit. Location: Bonded warehouse | Provide exit signs above all exits to the exterior and all doors tothe exit stair. | Issue solved and pending for verification. | Oct 20 2018 | On 18/11/2018: During FUI visit, this issue will be verified. On 11/04/2019: Corrected. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Provided. On 02/01/2022: Corrected. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 1 month | Corrected
Initial Inspection |  | 17 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on-site, in accordance with NFPA 10. | Facility maintain fire extinguisher inspection record as per NFPA 10. And issue closed. | Oct 20 2018 | On 18/11/2018: During FUI visit, this issue will be verified. On 11/04/2019: In progress. On 24.10.2019: Corrected. On 13/01/2021: Corrected. Maintaining. On 02/01/2022: Corrected. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 18 | New Finding (1st follow-up): Storage was located in the dinning room | Remove all storage from dinning room | Already removed all storage from dinning room. And issue closed. | Apr 13 2019 | On 11/04/2019: New finding On 24.10.2019: Corrected. On 13/01/2021: Corrected. Removed. On 02/01/2022: Corrected as per previous follow up. Refer to the issue no 19. On 21-Jun-2022: Corrected. On Unannounced Special Escalation Inspection (11/10/2022): Not checked. On 16-Nov-2023: Corrected. On 04-Aug-25: Corrected | immediately | Corrected
Follow Up Inspection |  | 19 | New Finding (2nd follow-up): Areas used for in-process storage of combustible materials are open to the surrounding occupancy at ground floor. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Work done The facility already installed 2 hours rating UL listed new Fire on storeroom in ground floor & Also automatic Magnetic door holder has actived. | Dec 24 2019 | On 24.10.2019: New Finding On 13/01/2021: Partially corrected. During follow up inspection accessories storage rooms were not separated on ground and 1st floors. On 02/01/2022: Store rooms are not separated from work area on ground & 1st floor. Storage areas are not separated from dining area on ground floor in dining shed. On 21-Jun-2022: Not corrected yet. Fire Rated door has been found manually open condition during the inspection. Magnetic door holder has not been provided. On Unannounced Special Escalation Inspection (11/10/2022): Corrected. Factory has installed fire doors and magnetic door holders for dedicated storage room. Fire doors have been interfaced with FACP and found fully functional. On 16-Nov-2023: Corrected. Factory has kept the storage arrangements within the limits. On 04-Aug-25: Corrected | within 2 months | Corrected
Follow Up Inspection |  | 20 | New Finding (6th follow-up): Unsealed penetrations and openings are located on the fire-rated floor/ceiling assemblies. Location: -Electrical Cable riser (all floors). -PVC Sewage riser (all floors) -Wall penetration between dinning and storage | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling- 2hr) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the risers from each floor if required. Penetrations of fire resistive rated assemblies shall be protected with listed through penetration fire stop system tested in Accordance with ASTME814 in Accordance with RSC standard 4.7. | The facility has covered all Unsealed penetrations and openings of PVC Sewage Riser Pipe by RCC Slab. Work done | Feb 16 2024 | On 16-Nov-2023: New Finding. On 04-Aug-25: Still unsealed penetrations due to cable riser and PVC sewage risers are observed. Also in stair-03 on the ground floor PVC pipe riser from floor and penetrations are observed. | within 3 months | In Progress
Follow Up Inspection |  | 21 | New Finding (6th follow-up): Uneven path of travel and blockage in exit access. Location: Exit discharge from dinning. | Remove unnecessary items and level exit path to the public way. | The facility has removed the unnecessary items and leveled exit path of the public way beside the Dining Room's 2nd Exit point. Work done | Dec 16 2023 | On 16-Nov-2023: New Finding. On 04-Aug-25: Corrected. The factory level the exit path to the public way. | within 1 months | Corrected
Follow Up Inspection |  | 22 | New Finding (6th Follow-up): For Structural fire protection alternate solution, automatic sprinkler system has been installed in the factory. Drawing has been reviewed, However installation requires final approval. | Installation of sprinkler system shall be as per NFPA-13. Supported by a compliant fire pump installed as per NFPA-20. | The facility has completed all modification work for automatic sprinkler systems as per REC Standard. Work done | Dec 16 2023 | On 16-Nov-2023: New Finding. T&C has been conducted. Find attached T&C comment. On 04-Aug-25: Final Verification Inspection (FVI) has been conducted and the system is not approved. Another FVI required. For details see Final Verification Inspection report. | within 2 months | Pending Verification

## Electrical
Date
16-Sep-2025 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Gardenia Wears Ltd, 310/668, SITPARA, BORMI, SREEPUR, Gazipur
Date of Inspection |  | 2018-09-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/ less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord. Electrical SLD must be updated properly when electrical system is modified. |  | Dec 10 2018 | On 11/04/2019: SLD is not completed yet. Provide circuit identification by means of separate color coding, marking tape, tagging. The identification shall include sufficient detail to allow each circuit to be distinguished from all others. Circuit directory shall be available for each electrical panel/board On 24/10/2019: Not Corrected. SLD has been submitted to ACCORD. On 09/12/2019 (Special Inspection): Not Corrected. Factory submitted revised SLD to ACCORD. On 13/01/2021: SLD is not as built & SLD need modifications. Not Corrected. On 23-Jan-2022: Not Corrected. Work is going on. On 21/06/2022: Corrected. Factory has "Accepted" SLD from RSC on 29-Dec-2020, and SLD found as built. | Dec 10 2018 | Corrected
Initial Inspection |  | 2 | LPS earth electrodes are undersized. All metal parts are not properly bonded. Drawing needs to be modified. | Minimum earth electrode size shall be 12.7 mm for LPS. All open metal parts need to be properly bonded with LPS. As built LPS drawing is required with proper risk index for all structure. |  | Dec 10 2018 | On 11/04/2019: The air terminal shall be mounted on bases having a minimum contact area of 3 in.2(1940mm2), each secured to bare metal of the housing or mounted by drilling and tapping to the unit’s frame. All stick terminal device shall have two or more paths to ground. The distance from a strike termination device to an outside corner or the distance perpendicular to an outside edge shall not be greater than 2 ft. (0.6 m). On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Not Corrected. Drawing is not as built. On 13/01/2021: Both drawing & installation need modification. Not Corrected. On 23-Jan-2022: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 3 | Electric safety training program is not initiated/ conducted. | Electrical safety training and awareness program for the electrical personnel must be initiated. It is a periodic task which factory has to continue to improve the overall electrical safety situation for the staffs. |  | Oct 15 2018 | On 11/04/2019: Need to enrich safety training content. On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 4 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). |  | Nov 10 2018 | On 11/04/2019: Need to maintain a register for all program. On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 5 | Insulation resistance test of electrical power cables is not performed. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). |  | Nov 10 2018 | On 11/04/2019: Insulation test for all power cables is not performed. On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 6 | Thermography scanning report is unavailable. | Thermography survey must be done and recorded at least twice in a year. |  | Nov 10 2018 | On 11/04/2019: Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 7 | Transformer Oil Test (dielectric strength test) report is unavailable. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. |  | Nov 10 2018 | On 11/04/2019: Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 8 | Earth Pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be available to the Inspector when required. |  | Nov 10 2018 | On 11/04/2019: All pit resistance is not measured. On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 9 | No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all using records. |  | Nov 10 2018 | On 11/04/2019: Not Corrected On 24/10/2019: Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 10 | Generator terminal box’s bottom is left open. (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs. Gland shall be used, where required. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 11 | Only one earthing cable is connected with generator body. | At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 12 | Number of earth pits are inadequate for the factory. | Adequate number of earth pits must be ensured for the factory with proper earth lead and earth electrode size as mentioned in BNBC requirements. mixing all together shall be avoided. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 13 | Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Not Corrected. Batteries are placed on brick. On 09/12/2019 (Special Inspection): Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 14 | Distribution Board's top/ bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. |  | Dec 10 2018 | On 11/04/2019: Not Corrected On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 15 | Cable trench creates obstacles around the transformer which has trip hazard. Again the clearance space around the transformer is inadequate. | Workplace around each electrical installation shall be uniformly level. At least 1.07m (42 inch) clearance space is required around transformer. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 16 | Transformer Breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil mark on the cup. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 17 | Distribution Board's back cover is left open. | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. |  | Dec 10 2018 | On 11/04/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 18 | Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 19 | Interlocking is not available after opening panel door. | Mechanical interlocking system shall be fixed with breakers so that it is not possible to operate both breakers at same time even after opening the panel door. |  | Oct 12 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 20 | Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). |  | Nov 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 21 | Earth lead cable/ Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). |  | Oct 15 2018 | On 11/04/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 22 | Electrical distribution box/ panels are full of fluffs (lint/ dirt). | Each electrical distribution board/ panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. |  | Dec 15 2018 | On 11/04/2019: Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 23 | Utility building (Transformer, Generator and LT panel room) has improper ventilation. | Adequate ventilation must be maintained in sub-station room. Cross/ forced ventilation must be ensured. |  | Dec 10 2018 | On 11/04/2019: Need to ensure cross ventilation. On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 24 | Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, coloured heat shrink) shall be done on major power cables used in the system according to SLD. |  | Dec 10 2018 | On 11/04/2019: Not Corrected On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 25 | Cable connected to busbar/MCCB/MCB terminal without cable lug. | Each electrical circuit must be terminated at single busbar/ MCB/ MCCB terminal using cable proper sized cable lug (where applicable). |  | Dec 15 2018 | On 11/04/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 26 | Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. |  | Dec 10 2018 | On 11/04/2019: Not Corrected On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Not Corrected. On 13/01/2021: Found Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 27 | Multiple/Loop cables (came from different electrical consumers) terminated at MCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals and busbar shall be used for distribution. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 28 | Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables must be removed as soon as possible. |  | Dec 15 2018 | On 11/04/2019: Corrected. | Nov 10 2018 | Corrected
Initial Inspection |  | 29 | Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. |  | Dec 10 2018 | On 11/04/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 30 | Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacle (inside BBT riser room). | Total space in front of panel board cannot be less than 1 meter. All the panel door shall be open at least till 90degree without obstructing other doors to be opened. Working clearance must be maintained in front of each panel board. |  | Jan 10 2019 | On 11/04/2019: Corrected. | Jan 10 2019 | Corrected
Initial Inspection |  | 31 | Power cables entering or exiting from Distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). |  | Dec 10 2018 | On 11/04/2019: Not Corrected On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 32 | Power bus bars are installed congested; and power cables touch other phase bus bar/s. | Power bus bar must be installed with adequate clearance (not less than 2.5 inch for LV) between two bars. Cables must not touch opposite bus bars in any case. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 33 | Wooden support used for motor. | Replace wooden support and it is preferable to fix each rotation devices with its base. |  | Jan 10 2019 | On 11/04/2019: Corrected. | Jan 10 2019 | Corrected
Initial Inspection |  | 34 | Cables inside distribution board are disorganized. | Cables inside each distribution board shall be well organized to avoid misleading during any troubleshooting. Distribution board's form is appreciated. |  | Dec 10 2018 | On 11/04/2019: Not Corrected. On 24/10/2019: Corrected. | Dec 10 2018 | Corrected
Initial Inspection |  | 35 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. |  | Nov 10 2018 | On 11/04/2019: Corrected. | Nov 10 2018 | Corrected
Follow Up Inspection |  | 36 | New Finding: Cable trench is found wet or filled with water. | Cable trench must be kept always dry, and shall be covered by checkered plate. |  | May 20 2019 | On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Neutral point of generator does not have earthing connection. | Two separate earth connection & one separate and distinct Neutral connection must be provided over generator. |  | May 20 2019 | On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Leakage current collector of HT cable is not connected to earth. | Connect earth leakage current collector to earthing system by proper size earth cable. |  | May 20 2019 | On 24/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Cable insulation may be damaged by the edge of the trench cover. | Install cover properly on cable trench so that cable may not be damaged by the edge of the trench cover. |  | May 20 2019 | On 24/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s) | Cables passing through permanent wall/floor slab must be protected. Floor to floor openings shall be sealed by proper type materials (consult with fire expert). |  | May 20 2019 | On 24/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. |  | May 20 2019 | On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Not Corrected. Found at few area. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Single pole circuit breaker is used to protect line-to-line connected load. | Double pole/three pole circuit shall be used to protect line-to-line load as required. Individual single-pole circuit breaker can be used to protect line-to-line load if it has identified handle ties. |  | May 20 2019 | On 24/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Communication cables and power cable are in the same raceway. | Communications wires and cables shall be separated at least 50 mm (2 in.) from conductors of any electric light, power, Class 1, non-power-limited fire alarm, or medium-power network-powered broadband communications. |  | May 20 2019 | On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. Separate cable channel used for communication cables. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Cable tray is overloaded with excessive cables; eventually top cover has no effectiveness. | Proper sized cable tray must be installed; a perforated one is better and 20-25% space in cable tray/duct shall be kept free. |  | May 20 2019 | On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Boiler room has poor/inadequate ventilation | Boiler room must be well ventilated. Cross/forced ventilation must be ensured. For exhaust fan, the fan diameter must not be less than 18 inch. |  | May 20 2019 | On 24/10/2019: Not Corrected. Designed air flow is improper. On 09/12/2019 (Special Inspection): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: No/ Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. |  | May 20 2019 | On 24/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. |  | May 20 2019 | On 24/10/2019: Not Corrected. On 09/12/2019 (Special Inspection): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. |  | Nov 30 2019 | On 09/12/2019 (Special Inspection): Not Corrected. No progress observed. On 13/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Earth lead cable/ Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). |  | Jan 20 2020 | On 13/01/2021: Work's been started, but not finished yet. Not Corrected. On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. |  | Jan 20 2020 | On 13/01/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Panel door has no earth connection Power socket has no ECC connection Motor/Pumps are not earthed properly. | All metal panel doors shall have earth connection. ECC connection shall be provided to each power socket Ensure earthing connection for all motor/pumps coil and body. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Uninsulated electrical tools are used by maintenance personnel in the factory. | For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Panel has unwanted openings. | Openings shall be sealed properly. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/ duct) | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Equipment earth cable (for generator) size is inadequate. | Equipment earth connection for generator shall be drawn from at least two separate point of generator; and the cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Panel/ distribution board is not firmly fixed with the foundation. | Panel base must be securely fixed to the foundation. With appropriate fastening devices. |  | Feb 28 2021 | On 23-Jan-2022: Not Corrected. On 21/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Power cables inside cable trench are buried by sand/ soil/ concrete. | Power cables shall not be buried directly in any case. If it is not designed through sand/ concrete/ soil, removal of sand/ concrete /soil must be done. |  | Feb 28 2021 | On 23-Jan-2022: Not Corrected. On 21/06/2022: Not Corrected. Found at few locations (transformer LT cables and cables below LT panel). On 19/01/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Distribution boards have no clear identification markings. Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Electrical panel room has no ventilation | Electrical panel room must be well ventilated. |  | Feb 28 2021 | On 23-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Generator exhaust pipe is uninsulated. | Generator Exhaust pipe need to be covered by proper and adequate insulator. |  | Mar 3 2022 | On 21/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Inadequate working space around (or in front of) board/ panels and access to the board/ panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. |  | Mar 3 2022 | On 21/06/2022: Corrected. Panel boards are relocated. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Combustible material on touching/ attached with/ tied with the panel. | Need to remove combustibles which may catch fire. |  | Mar 3 2022 | On 21/06/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Periodicity of Transformer Oil Test (dielectric strength, moisture content and flash point) survey is not continued. | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year. If the operation of transformer is 24/7 in the facility twice in a year is a better practice. |  | Jul 30 2022 | On 19/01/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Wiring or extensions to connect equipment/ devices are laid on floors. | The cable connection to machines/equipment may be run under the checkered plates (existing) and in trenches or rigid conduits/cable trays and supports to protect from external damages. |  | Jul 30 2022 | On 19/01/2023: Corrected. | 1 Month | Corrected